MV/LV Substation BU***937 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =196 kW | --> | C16 ex DUNGLOE | Dungloe [T41,T42] | ARDNAGAPPARY |  | 54.9832 | -8.4407
MV/LV Substation ME***995 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =71 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =99 kW | --> | C18 ex DUNGLOE | Dungloe [T41,T42] | ARDNAGAPPARY |  | 54.9582 | -8.3638
MV/LV Substation LI***007X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3178 | -8.0741
MV/LV Substation ME***024X |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =907 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3082 | -8.1733
MV/LV Substation PL***028X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E11 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3105 | -8.2043
MV/LV Substation CL***035X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =18 kVA | --> | 0.048 | 0 | 0.01 | 0.044 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3089 | -8.1782
MV/LV Substation AM***041X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3114 | -8.1934
MV/LV Substation BA***042X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3157 | -8.2052
MV/LV Substation DI***047X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =548 kVA | --> | 0.598 | 0 | 0.035 | 0.5 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3045 | -8.1735
MV/LV Substation MA***061X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =188 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2871 | -7.9128
MV/LV Substation CR***066X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =346 kVA | --> | 0.38 | 0 | 0.01 | 0.38 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3051 | -8.1813
MV/LV Substation BE***070X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =181 kVA | --> | 0.19 | 0 | 0 | 0.193 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2919 | -7.8764
MV/LV Substation WA***073X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =492 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2539 | -8.2979
MV/LV Substation CL***079X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =377 kVA | --> | 0.38 | 0 | 0 | 0.383 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3073 | -8.171
MV/LV Substation MA***093X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E11 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3069 | -8.2066
MV/LV Substation SK***100X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =349 kVA | --> | 0.38 | 0 | 0.005 | 0.383 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3129 | -8.1719
MV/LV Substation MC***108X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3074 | -8.1338
MV/LV Substation CU***143X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2868 | -8.0458
MV/LV Substation RA***144X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2845 | -7.9888
MV/LV Substation LI***155X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.265 | -8.2096
MV/LV Substation BE***397 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =510 kVA | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.306 | -8.1745
MV/LV Substation MA***401 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.598 | 0 | 0.019 | 0.5 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3035 | -8.1743
MV/LV Substation SR***4013 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =65 kVA | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3712 | -8.2687
MV/LV Substation KI***4017 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3582 | -8.0376
MV/LV Substation HO***402 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =228 kVA | --> | 0.38 | 0 | 0 | 0.403 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3039 | -8.1665
MV/LV Substation DO***4028 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3002 | -8.1524
MV/LV Substation LO***405 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.19 | 0 | 0.03 | 0.183 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2884 | -7.9207
MV/LV Substation PU***427 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.19 | 0 | 0 | 0.195 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3026 | -8.1831
MV/LV Substation TR***428 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =173 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3032 | -8.1866
MV/LV Substation TU***432 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2896 | -7.8879
MV/LV Substation CR***435 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3569 | -8.0418
MV/LV Substation TH***436 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2999 | -8.1651
MV/LV Substation TO***445 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =28 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2901 | -7.8727
MV/LV Substation ST***452 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =91 kVA | --> | 0.095 | 0 | 0.006 | 0.092 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3021 | -8.1705
MV/LV Substation HO***454 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0.004 | 0.046 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3887 | -8.1126
MV/LV Substation BL***552 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =270 kVA | --> | 0.38 | 0 | 0.018 | 0.384 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3055 | -8.1705
MV/LV Substation FR***553 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 |  | --> | 0.598 | 0 | 0.163 | 0.5 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3068 | -8.1752
MV/LV Substation ST***572 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2938 | -8.0586
MV/LV Substation MC***575 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =170 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3028 | -8.1731
MV/LV Substation MO***578 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =74 kVA | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | E11 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3129 | -8.2103
MV/LV Substation CL***580 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =22 kVA | --> | 0.048 | 0 | 0.031 | 0.028 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3067 | -8.1839
MV/LV Substation GL***612 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =25 kVA | --> | 0.048 | 0 | 0 | 0.051 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2839 | -7.9834
MV/LV Substation KI***634 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =70 kVA | --> | 0.095 | 0 | 0.006 | 0.095 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3566 | -8.0394
MV/LV Substation UP***665 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2856 | -7.9441
MV/LV Substation BL***687 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.19 | 0 | 0.015 | 0.2 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2911 | -7.8778
MV/LV Substation SL***698 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =300 kVA | --> | 0.38 | 0 | 0.009 | 0.387 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.304 | -8.1795
MV/LV Substation KI***730 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2868 | -7.9
MV/LV Substation CO***731 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.095 | 0 | 0.015 | 0.092 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3024 | -8.1764
MV/LV Substation SK***779 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0.004 | 0.046 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3094 | -8.1737
MV/LV Substation ME***781 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =319 kVA | --> | 0.38 | 0 | 0 | 0.391 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3038 | -8.1687
MV/LV Substation RO***893 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3857 | -8.1122
MV/LV Substation OR***894 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.005 | 0.045 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3928 | -8.1199
MV/LV Substation EL***962 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3015 | -8.1927
MV/LV Substation WO***981 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2754 | -8.2002
MV/LV Substation WO***982 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2832 | -7.9771
MV/LV Substation MA***001 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.442 | 2.35 |  | --> | 0.598 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =615 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8509 | -8.9991
MV/LV Substation TH***002 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.35 |  | --> | 0.598 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =595 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8481 | -9.0025
MV/LV Substation TE***003 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.289 | 2.35 |  | --> | 0.38 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8482 | -8.9922
MV/LV Substation IR***007 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 2.35 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8519 | -8.9948
MV/LV Substation MA***012 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.092 | 2.35 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =197 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8493 | -9.0009
MV/LV Substation RI***019 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =184 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =192 kW | --> | C16 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1632 | -7.1376
MV/LV Substation CM***044 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.132 | 2.35 |  | --> | 0.19 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =162 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8548 | -8.9956
MV/LV Substation AI***063 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.005 | 2.35 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =107 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8535 | -8.9971
MV/LV Substation BA***079 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 2.35 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =98 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8283 | -9.0402
MV/LV Substation SW***080 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.35 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8553 | -8.9949
MV/LV Substation WA***081 |  | 10 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0 | 2.35 |  | --> | 0.028 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =35 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8673 | -8.9818
MV/LV Substation AL***105 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 2.35 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8458 | -9.0078
MV/LV Substation PA***119 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.318 | 2.35 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =391 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8577 | -8.9938
MV/LV Substation VO***194 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 2.35 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8437 | -9.0059
MV/LV Substation CO***210 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.378 | 2.35 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =383 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8474 | -9.0052
MV/LV Substation MO***222 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 2.35 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8451 | -9.0025
MV/LV Substation TH***262 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.35 |  | --> | 0.598 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =596 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8468 | -8.9982
MV/LV Substation AR***283 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.346 | 0.43 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =387 kW | --> | C13 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9345 | -8.949
MV/LV Substation FO***298 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.19 | 2.35 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =191 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8566 | -8.9969
MV/LV Substation RA***304 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.353 | 2.35 |  | --> | 0.38 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.851 | -8.9948
MV/LV Substation GI***311 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 2.35 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8603 | -9.0018
MV/LV Substation BU***337 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.368 | 2.35 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8594 | -8.9905
MV/LV Substation CE***338 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.35 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8486 | -8.982
MV/LV Substation KI***4007 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.35 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8477 | -9.0104
MV/LV Substation SE***4008 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.171 | 2.35 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =194 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8491 | -9.0058
MV/LV Substation SC***4013 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 2.35 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8456 | -9.0105
MV/LV Substation CA***4014 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.35 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8164 | -9.0529
MV/LV Substation RA***4040 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 2.35 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =50 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8504 | -9.0029
MV/LV Substation MA***003 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.337 | 1.57 |  | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =386 kW | --> | C13 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4761 | -8.2861
MV/LV Substation RA***004 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.16 | 1.57 |  | --> | 0.38 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =402 kW | --> | C13 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4782 | -8.2776
MV/LV Substation AT***004X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.28 | 1.57 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =396 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4801 | -8.277
MV/LV Substation AL***005 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.311 | 1.57 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =392 kW | --> | C13 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4755 | -8.2834
MV/LV Substation DA***006 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.159 | 1.57 |  | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =192 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4736 | -8.2884
MV/LV Substation FI***009X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4723 | -8.3188
MV/LV Substation OC***012X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.375 | 1.57 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =383 kW | --> | C13 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4768 | -8.2854
MV/LV Substation ER***014X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 1.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4913 | -8.24
MV/LV Substation GR***015 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.35 | 1.57 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =387 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4859 | -8.2761
MV/LV Substation FI***016 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.308 | 1.57 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =392 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4931 | -8.2383
MV/LV Substation LE***016X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.329 | 1.57 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =390 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4806 | -8.2752
MV/LV Substation DR***017X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.368 | 1.57 |  | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =382 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4819 | -8.2668
MV/LV Substation MC***018X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4436 | -8.3076
MV/LV Substation WE***025 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.298 | 1.57 |  | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =383 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4757 | -8.2981
MV/LV Substation SI***026X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.36 | 1.57 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =385 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4744 | -8.2986
MV/LV Substation SI***027 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.069 | 1.57 |  | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =195 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4824 | -8.2679
MV/LV Substation WA***030 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.334 | 1.57 |  | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =382 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4807 | -8.2787
MV/LV Substation ST***033 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.128 | 1.57 |  | --> | 0.19 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C13 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4756 | -8.2775
MV/LV Substation WI***034 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.064 | 1.57 |  | --> | 0.095 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4971 | -8.2088
MV/LV Substation MA***038 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.397 | 1.57 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =630 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4797 | -8.274
MV/LV Substation TO***040 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.298 | 1.57 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =642 kW | --> | C13 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4779 | -8.2805
MV/LV Substation DI***041 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.047 | 1.57 |  | --> | 0.095 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4761 | -8.2915
MV/LV Substation WH***043X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.295 | 1.57 |  | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =392 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4734 | -8.2786
MV/LV Substation MA***044 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.339 | 1.57 |  | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =382 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4756 | -8.3046
MV/LV Substation DR***050 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.143 | 1.57 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4806 | -8.2677
MV/LV Substation ME***061X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.142 | 1.57 |  | --> | 0.19 | 0 | 0.037 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4528 | -8.2877
MV/LV Substation KI***065X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.155 | 1.57 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =192 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.446 | -8.2816
MV/LV Substation MI***080X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.328 | 1.57 |  | --> | 0.38 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4435 | -8.2844
MV/LV Substation FI***085X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.385 | 1.57 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =382 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4832 | -8.2603
MV/LV Substation DU***093X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.195 | 1.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =191 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4657 | -8.3291
MV/LV Substation DO***105X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.371 | 1.57 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.481 | -8.2638
MV/LV Substation OA***131X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.57 |  | --> | 0.598 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =592 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4512 | -8.2885
MV/LV Substation OU***143X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4896 | -8.2505
MV/LV Substation BU***150X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 1.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4549 | -8.4201
MV/LV Substation ST***154X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.496 | 1.57 |  | --> | 0.598 | 0 | 0.038 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4863 | -8.2647
MV/LV Substation BO***158X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4743 | -8.3018
MV/LV Substation MO***171X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.3774 | -8.3918
MV/LV Substation BU***176X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.452 | 1.57 |  | --> | 0.598 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =606 kW | --> | C13 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4763 | -8.274
MV/LV Substation CA***179X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4557 | -8.3977
MV/LV Substation RO***180X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.341 | 1.57 |  | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4733 | -8.284
MV/LV Substation DA***181X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.365 | 1.57 |  | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =382 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4432 | -8.2884
MV/LV Substation AR***182X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4734 | -8.2631
MV/LV Substation TR***184X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.164 | 1.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =195 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4987 | -8.2226
MV/LV Substation ES***187X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 1.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | C13 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.473 | -8.2662
MV/LV Substation AT***189X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.57 |  | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =963 kW | --> | C13 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4791 | -8.2758
MV/LV Substation LA***201X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4399 | -8.3005
MV/LV Substation ME***203X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.196 | 1.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4471 | -8.2839
MV/LV Substation BU***206X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 1.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4548 | -8.4187
MV/LV Substation AU***212X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4601 | -8.3325
MV/LV Substation ED***213X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.57 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =615 kW | --> | C13 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4769 | -8.287
MV/LV Substation CA***372 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.143 | 1.57 |  | --> | 0.19 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4674 | -8.328
MV/LV Substation CA***376 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.168 | 1.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =194 kW | --> | C13 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4781 | -8.273
MV/LV Substation HO***4012 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4103 | -8.4087
MV/LV Substation WA***403 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.57 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.465 | -8.2818
MV/LV Substation AS***4030 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4522 | -8.2008
MV/LV Substation DR***4032 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4149 | -8.3805
MV/LV Substation DR***4034 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.175 | 1.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =193 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4799 | -8.2706
MV/LV Substation BU***4037 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1.57 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4717 | -8.2943
MV/LV Substation GO***4062 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 1.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4783 | -8.2611
MV/LV Substation WA***408 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.133 | 1.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =199 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4532 | -8.2103
MV/LV Substation BU***434 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4434 | -8.4239
MV/LV Substation MC***470 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.57 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4564 | -8.2763
MV/LV Substation KI***473 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.244 | 1.57 |  | --> | 0.38 | 0 | 0.037 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4465 | -8.2865
MV/LV Substation KI***476 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 1.57 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4451 | -8.2972
MV/LV Substation CR***480 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.147 | 1.57 |  | --> | 0.19 | 0 | 0.038 | 0 | 0 | Constrained, otherwise capacity available =169 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4764 | -8.3141
MV/LV Substation DR***481 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.142 | 1.57 |  | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =195 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4723 | -8.3211
MV/LV Substation TU***483 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.15 | 1.57 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =193 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4687 | -8.3297
MV/LV Substation CR***498 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 1.57 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4385 | -8.4351
MV/LV Substation BA***510 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.173 | 1.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =194 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4972 | -8.2138
MV/LV Substation RO***517 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 1.57 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C13 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4747 | -8.2841
MV/LV Substation FI***584 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 1.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4848 | -8.2576
MV/LV Substation FI***597 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4987 | -8.2268
MV/LV Substation N ***716 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 1.57 |  | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4017 | -8.4063
MV/LV Substation ES***759 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.02 | 1.57 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4752 | -8.3108
MV/LV Substation MU***827 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 1.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4589 | -8.2594
MV/LV Substation PU***946 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4704 | -8.3305
MV/LV Substation CO***992 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4318 | -8.326
MV/LV Substation GU***998 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.455 | -8.2824
MV/LV Substation TH***002 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.06 | 0.06 | Constrained, otherwise capacity available =214 kVA | --> | 0.38 | 0 | 0.04 | 0.375 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0538 | -8.7303
MV/LV Substation AL***003X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0449 | -8.7603
MV/LV Substation BA***004 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.06 | 0.06 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0.01 | 0.088 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0393 | -8.8152
MV/LV Substation CH***005 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =128 kVA | --> | 0.19 | 0 | 0.01 | 0.192 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.049 | -8.7325
MV/LV Substation TE***006 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.06 | 0.06 | Constrained, otherwise capacity available =513 kVA | --> | 0.598 | 0 | 0.01 | 0.5 | 0 | Constrained, otherwise capacity available =607 kW | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0513 | -8.732
MV/LV Substation BA***008 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.06 | 0.06 | Constrained, otherwise capacity available =976 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 | Constrained, otherwise capacity available =953 kW | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0524 | -8.7376
MV/LV Substation B/***010 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.06 | 0.06 | Constrained, otherwise capacity available =71 kVA | --> | 0.095 | 0 | 0 | 0.099 | 0 |  | --> | C18 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0511 | -8.7168
MV/LV Substation TE***011 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =67 kVA | --> | 0.19 | 0 | 0.01 | 0.2 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0557 | -8.7258
MV/LV Substation CA***011X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0636 | -8.7247
MV/LV Substation TO***013 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.06 | 0.06 | Constrained, otherwise capacity available =471 kVA | --> | 0.598 | 0 | 0.036 | 0.5 | 0 | Constrained, otherwise capacity available =593 kW | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0537 | -8.7382
MV/LV Substation MU***013X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.06 |  | --> | 0.048 | 0 | 0.005 | 0.044 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.1097 | -8.7459
MV/LV Substation IN***014 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.06 | 0.06 | Constrained, otherwise capacity available =281 kVA | --> | 0.38 | 0 | 0.063 | 0.349 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0512 | -8.7383
MV/LV Substation MO***015 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =136 kVA | --> | 0.19 | 0 | 0 | 0.199 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.052 | -8.7296
MV/LV Substation AC***018X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.429 | 0.43 | Constrained, otherwise capacity available =543 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =610 kW | --> | C14 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 54.0374 | -8.8943
MV/LV Substation MU***033X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.06 | 0.06 | Constrained, otherwise capacity available =477 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 | Constrained, otherwise capacity available =619 kW | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0538 | -8.7325
MV/LV Substation RH***034X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0367 | -8.7721
MV/LV Substation PA***040X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0.017 | 0.186 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0583 | -8.7255
MV/LV Substation KN***041X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.1051 | -8.6848
MV/LV Substation LE***046X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =179 kVA | --> | 0.19 | 0 | 0 | 0.193 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0501 | -8.7261
MV/LV Substation HI***048X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.06 | 0.06 | Constrained, otherwise capacity available =342 kVA | --> | 0.38 | 0 | 0 | 0.388 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0488 | -8.7351
MV/LV Substation CA***056 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.016 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.052 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0643 | -8.7092
MV/LV Substation NE***062X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.06 | 0.06 | Constrained, otherwise capacity available =369 kVA | --> | 0.38 | 0 | 0 | 0.384 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.054 | -8.7598
MV/LV Substation AC***064 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C14 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 54.038 | -8.8935
MV/LV Substation MO***069X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0333 | -8.7914
MV/LV Substation ON***081X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.06 | 0.06 | Constrained, otherwise capacity available =444 kVA | --> | 0.598 | 0 | 0.003 | 0.5 | 0 | Constrained, otherwise capacity available =621 kW | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0547 | -8.7278
MV/LV Substation FU***085 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.06 | 0.06 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0389 | -8.7557
MV/LV Substation NO***094X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0127 | -8.809
MV/LV Substation BR***105 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =181 kVA | --> | 0.19 | 0 | 0.009 | 0.186 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0979 | -8.7777
MV/LV Substation FI***117 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.055 | -8.776
MV/LV Substation FA***117X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =164 kVA | --> | 0.19 | 0 | 0.011 | 0.187 | 0 |  | --> | C18 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0517 | -8.7126
MV/LV Substation TH***129X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =162 kVA | --> | 0.19 | 0 | 0 | 0.195 | 0 |  | --> | C18 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0537 | -8.7116
MV/LV Substation RA***137X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =146 kVA | --> | 0.19 | 0 | 0.009 | 0.191 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0513 | -8.7431
MV/LV Substation OH***141X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0652 | -8.7622
MV/LV Substation SP***147X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.06 | 0.06 | Constrained, otherwise capacity available =548 kVA | --> | 0.598 | 0 | 0.006 | 0.5 | 0 | Constrained, otherwise capacity available =605 kW | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0566 | -8.7229
MV/LV Substation MA***172X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0646 | -8.7816
MV/LV Substation MA***174X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =195 kVA | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0555 | -8.7325
MV/LV Substation MU***177 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.044 | 0.06 |  | --> | 0.095 | 0 | 0 | 0.102 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0677 | -8.7097
MV/LV Substation CN***183X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =194 kVA | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0529 | -8.7438
MV/LV Substation CA***184X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.06 |  | --> | 0.048 | 0 | 0.02 | 0.034 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0357 | -8.7259
MV/LV Substation FA***206X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =195 kVA | --> | 0.19 | 0 | 0.002 | 0.189 | 0 |  | --> | C18 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0526 | -8.709
MV/LV Substation QU***221X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C18 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0551 | -8.6439
MV/LV Substation MU***250 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.06 | 0.06 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C18 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0436 | -8.6554
MV/LV Substation RO***364 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.055 | 0.06 |  | --> | 0.095 | 0 | 0.027 | 0.081 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.052 | -8.7222
MV/LV Substation CA***4005 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0512 | -8.846
MV/LV Substation CH***4027 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 0.06 |  | --> | 0.048 | 0 | 0.006 | 0.044 | 0 |  | --> | C18 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0464 | -8.6843
MV/LV Substation CO***4028 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.06 | 0.06 | Constrained, otherwise capacity available =568 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 | Constrained, otherwise capacity available =603 kW | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0546 | -8.7264
MV/LV Substation CU***4038 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.06 | 0.06 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.099 | -8.7781
MV/LV Substation BR***4055 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C18 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.044 | -8.6476
MV/LV Substation IR***4074 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.06 | 0.06 | Constrained, otherwise capacity available =369 kVA | --> | 0.38 | 0 | 0 | 0.384 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0547 | -8.7436
MV/LV Substation MI***4078 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0619 | -8.7676
MV/LV Substation GA***4083 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0584 | -8.7229
MV/LV Substation RA***413 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =151 kVA | --> | 0.19 | 0 | 0 | 0.196 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0521 | -8.7479
MV/LV Substation GA***428 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.06 |  | --> | 0.048 | 0 | 0.006 | 0.044 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0391 | -8.8357
MV/LV Substation TO***429 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 0.06 |  | --> | 0.048 | 0 | 0.004 | 0.046 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0395 | -8.843
MV/LV Substation PI***699 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.06 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.1007 | -8.7473
MV/LV Substation WO***713 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.034 | 0.06 |  | --> | 0.095 | 0 | 0 | 0.104 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.1284 | -8.7371
MV/LV Substation GO***899 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 0.06 |  | --> | 0.048 | 0 | 0.006 | 0.044 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0747 | -8.9114
MV/LV Substation DE***015 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5529 | -9.4716
MV/LV Substation BA***023 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =99 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4856 | -9.5674
MV/LV Substation AH***041 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5067 | -9.6542
MV/LV Substation BA***086 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4913 | -9.6723
MV/LV Substation BR***115 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5316 | -9.6543
MV/LV Substation AS***122 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5534 | -9.5581
MV/LV Substation SA***133 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.382 | 3.25 |  | --> | 0.38 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5039 | -9.6717
MV/LV Substation KC***151 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.186 | 3.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =192 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4913 | -9.6704
MV/LV Substation KC***152 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.379 | 3.25 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =383 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4996 | -9.6717
MV/LV Substation AH***155 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 3.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C14 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.5087 | -9.3772
MV/LV Substation BA***159 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4881 | -9.6759
MV/LV Substation BA***160 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4954 | -9.6535
MV/LV Substation TU***162 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5407 | -9.6102
MV/LV Substation LE***168 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 3.75 |  | --> | 0.095 | 0 | 0.045 | 0 | 0 | Constrained, otherwise capacity available =63 kW | --> | C14 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.5126 | -9.3934
MV/LV Substation EA***182 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.176 | 3.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =193 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5079 | -9.6661
MV/LV Substation TE***187 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 3.25 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4577 | -9.5124
MV/LV Substation HE***188 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4572 | -9.5207
MV/LV Substation LO***4001 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 3.25 |  | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4964 | -9.5795
MV/LV Substation O ***4040 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5563 | -9.58
MV/LV Substation TR***4044 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =50 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5473 | -9.4727
MV/LV Substation HO***4048 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5488 | -9.5056
MV/LV Substation AS***4049 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.194 | 3.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =191 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5477 | -9.4815
MV/LV Substation TO***4052 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =50 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4575 | -9.5132
MV/LV Substation O ***4053 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5608 | -9.4641
MV/LV Substation HE***4061 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 3.25 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5535 | -9.5233
MV/LV Substation GO***4068 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.19 | 3.25 |  | --> | 0.19 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5 | -9.678
MV/LV Substation LO***4081 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5527 | -9.5398
MV/LV Substation MU***4082 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5553 | -9.5274
MV/LV Substation CO***4086 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5062 | -9.5156
MV/LV Substation BA***4105 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 3.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5269 | -9.4886
MV/LV Substation DR***4108 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 3.25 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4875 | -9.481
MV/LV Substation KI***416 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.198 | 3.25 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5565 | -9.5803
MV/LV Substation MA***500 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.07 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =99 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5435 | -9.4775
MV/LV Substation BR***501 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.116 | 3.25 |  | --> | 0.19 | 0 | 0.04 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5459 | -9.477
MV/LV Substation GU***528 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 3.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C14 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.5302 | -9.4056
MV/LV Substation WA***602 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.468 | -9.5357
MV/LV Substation LI***613 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4904 | -9.5869
MV/LV Substation BA***658 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4877 | -9.6157
MV/LV Substation GO***667 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5008 | -9.6384
MV/LV Substation GO***673 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.183 | 3.25 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5058 | -9.6504
MV/LV Substation LI***693 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.058 | 3.25 |  | --> | 0.095 | 0 | 0.044 | 0 | 0 | Constrained, otherwise capacity available =68 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4875 | -9.5775
MV/LV Substation GO***694 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.367 | 3.25 |  | --> | 0.38 | 0 | 0.1 | 0 | 0 | Constrained, otherwise capacity available =310 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4952 | -9.6739
MV/LV Substation GO***695 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5026 | -9.6509
MV/LV Substation GR***696 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.154 | 3.25 |  | --> | 0.19 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =173 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5065 | -9.6731
MV/LV Substation SA***697 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.29 | 3.25 |  | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =388 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5102 | -9.676
MV/LV Substation CA***698 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.353 | 3.25 |  | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =382 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5118 | -9.6747
MV/LV Substation AH***699 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.042 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =102 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5069 | -9.6589
MV/LV Substation LI***700 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.334 | 3.25 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =382 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5104 | -9.666
MV/LV Substation CH***701 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.233 | 3.25 |  | --> | 0.38 | 0 | 0.034 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5134 | -9.671
MV/LV Substation DO***702 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.25 |  | --> | 0.598 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =601 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5185 | -9.674
MV/LV Substation DU***703 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.329 | 3.25 |  | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =387 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5196 | -9.6715
MV/LV Substation G ***705 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.161 | 3.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =195 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4997 | -9.6725
MV/LV Substation B/***712 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.25 |  | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =606 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5117 | -9.6712
MV/LV Substation LI***713 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 3.25 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.505 | -9.6469
MV/LV Substation AM***716 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.414 | 3.25 |  | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =620 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5109 | -9.6739
MV/LV Substation QU***742 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.167 | 3.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =194 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5471 | -9.4747
MV/LV Substation RU***778 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5521 | -9.482
MV/LV Substation NE***788 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 3.25 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5078 | -9.6721
MV/LV Substation NE***810 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.186 | 3.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =192 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5074 | -9.6702
MV/LV Substation VI***833 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.37 | 3.25 |  | --> | 0.38 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5072 | -9.6758
MV/LV Substation GL***838 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.383 | 3.25 |  | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5078 | -9.6694
MV/LV Substation BA***875 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.166 | 3.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =195 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5038 | -9.5775
MV/LV Substation CH***884 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.182 | 3.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =192 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5165 | -9.6691
MV/LV Substation FL***885 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.25 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =607 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5125 | -9.672
MV/LV Substation CL***893 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.25 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =604 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5155 | -9.6739
MV/LV Substation KN***894 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4946 | -9.5166
MV/LV Substation DI***896 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4623 | -9.5201
MV/LV Substation LE***897 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.38 | 3.25 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =383 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5096 | -9.6748
MV/LV Substation GO***902 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5015 | -9.6477
MV/LV Substation CU***904 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.175 | 3.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =193 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4532 | -9.5087
MV/LV Substation PA***908 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.298 | 3.25 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =386 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5029 | -9.6707
MV/LV Substation DO***912 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 3.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5232 | -9.6708
MV/LV Substation TH***918 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.147 | 3.25 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5147 | -9.6701
MV/LV Substation BB***926 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4954 | -9.6569
MV/LV Substation CU***930 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4511 | -9.5126
MV/LV Substation TH***932 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4968 | -9.6581
MV/LV Substation DI***934 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4608 | -9.5174
MV/LV Substation MA***001 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =368 kVA | --> | 0.38 | 0 | 0.015 | 0.373 | 0 |  | --> | C16 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2845 | -6.3816
MV/LV Substation BA***002 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.011 | 0.04 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2383 | -6.3982
MV/LV Substation AI***002X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =327 kVA | --> | 0.38 | 0 | 0 | 0.39 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2923 | -6.364
MV/LV Substation RO***003 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =364 kVA | --> | 0.38 | 0 | 0 | 0.385 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2891 | -6.4018
MV/LV Substation AI***003X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =542 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2931 | -6.361
MV/LV Substation ES***004 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =340 kVA | --> | 0.38 | 0 | 0 | 0.388 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2965 | -6.3581
MV/LV Substation FI***004X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =878 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2946 | -6.3607
MV/LV Substation CO***004Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =121 kVA | --> | 0.19 | 0 | 0 | 0.198 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.305 | -6.4956
MV/LV Substation NE***005Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =68 kVA | --> | 0.095 | 0 | 0.006 | 0.095 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2987 | -6.5215
MV/LV Substation LI***006 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =380 kVA | --> | 0.38 | 0 | 0 | 0.383 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2809 | -6.4705
MV/LV Substation BA***006X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =292 kVA | --> | 0.38 | 0 | 0.054 | 0.354 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.29 | -6.3533
MV/LV Substation KI***007 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0 | 0.391 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2923 | -6.4134
MV/LV Substation BA***007X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =246 kVA | --> | 0.38 | 0 | 0.043 | 0.369 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2894 | -6.3497
MV/LV Substation MO***008 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =272 kVA | --> | 0.38 | 0 | 0.029 | 0.376 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2851 | -6.3581
MV/LV Substation SA***009 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =801 kVA | --> | 0.95 | 0 | 0.003 | 0.5 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2776 | -6.4459
MV/LV Substation HU***010 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =270 kVA | --> | 0.38 | 0 | 0.008 | 0.391 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2701 | -6.3334
MV/LV Substation SI***011 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =319 kVA | --> | 0.38 | 0 | 0.024 | 0.373 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2948 | -6.3483
MV/LV Substation BE***012 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =283 kVA | --> | 0.38 | 0 | 0.017 | 0.383 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.271 | -6.3375
MV/LV Substation RA***012Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C29 ex GRANGE CASTLE | Grange Castle [T101,T102] | INCHICORE 220KV |  | 53.291 | -6.4811
MV/LV Substation BR***013X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =442 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2879 | -6.3514
MV/LV Substation CO***013Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =609 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3134 | -6.5109
MV/LV Substation DE***014 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.392 | 13.91 |  | --> | 0.598 | 0 | 0.003 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2712 | -6.3736
MV/LV Substation DE***015 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0.004 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2691 | -6.3736
MV/LV Substation BE***015X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.19 | 0 | 0 | 0.206 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2972 | -6.3539
MV/LV Substation DE***016 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0.078 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2703 | -6.3752
MV/LV Substation DE***017 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0.185 | 0.477 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2711 | -6.3775
MV/LV Substation CU***018 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.345 | 13.91 |  | --> | 0.38 | 0 | 0 | 0.387 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2723 | -6.377
MV/LV Substation BE***019 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =460 kVA | --> | 0.598 | 0 | 0.006 | 0.5 | 0 |  | --> | C19 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2777 | -6.4163
MV/LV Substation CR***019X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =314 kVA | --> | 0.38 | 0 | 0.025 | 0.373 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3118 | -6.3535
MV/LV Substation BE***020 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =514 kVA | --> | 0.598 | 0 | 0.004 | 0.5 | 0 |  | --> | C19 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2778 | -6.4144
MV/LV Substation BE***021 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =542 kVA | --> | 0.598 | 0 | 0.002 | 0.5 | 0 |  | --> | C19 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2764 | -6.413
MV/LV Substation CL***021Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3202 | -6.4682
MV/LV Substation BE***022 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =572 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2759 | -6.4117
MV/LV Substation CR***023X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =312 kVA | --> | 0.38 | 0 | 0 | 0.392 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3127 | -6.3552
MV/LV Substation GA***024X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.38 | 0 | 0 | 0.412 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3147 | -6.3534
MV/LV Substation PE***024Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =289 kVA | --> | 0.38 | 0 | 0 | 0.395 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.319 | -6.4794
MV/LV Substation BA***025X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.289 | 13.91 |  | --> | 0.38 | 0 | 0 | 0.395 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2819 | -6.3993
MV/LV Substation BA***027X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =366 kVA | --> | 0.598 | 0 | 0.039 | 0.5 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3242 | -6.4111
MV/LV Substation LO***029Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0.005 | 0.046 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3185 | -6.5002
MV/LV Substation WA***031X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =330 kVA | --> | 0.38 | 0 | 0.018 | 0.376 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3078 | -6.3656
MV/LV Substation PE***031Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =169 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3153 | -6.4812
MV/LV Substation SL***033X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2742 | -6.4458
MV/LV Substation CO***034 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0.005 | 0.192 | 0 |  | --> | C14 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2803 | -6.4319
MV/LV Substation CO***035Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0.016 | 0.086 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3063 | -6.4979
MV/LV Substation DO***036 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =913 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2898 | -6.3647
MV/LV Substation KI***036X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =326 kVA | --> | 0.38 | 0 | 0 | 0.39 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2774 | -6.3798
MV/LV Substation WE***036Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.006 | 0.044 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3042 | -6.4801
MV/LV Substation ME***037X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =267 kVA | --> | 0.38 | 0 | 0.013 | 0.388 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3276 | -6.42
MV/LV Substation WH***038 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2796 | -6.3747
MV/LV Substation DE***038X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =259 kVA | --> | 0.38 | 0 | 0.003 | 0.397 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3281 | -6.4222
MV/LV Substation NE***038Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =172 kVA | --> | 0.19 | 0 | 0.005 | 0.19 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3017 | -6.4982
MV/LV Substation WH***039 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.353 | 13.91 |  | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2788 | -6.3754
MV/LV Substation BR***039X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =932 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2977 | -6.3614
MV/LV Substation FO***040X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =287 kVA | --> | 0.38 | 0 | 0.026 | 0.376 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3085 | -6.3635
MV/LV Substation AY***040Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =136 kVA | --> | 0.19 | 0 | 0.01 | 0.191 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3 | -6.4881
MV/LV Substation VI***041X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =119 kVA | --> | 0.19 | 0 | 0.027 | 0.181 | 0 |  | --> | C16 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2881 | -6.3798
MV/LV Substation CO***041Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =135 kVA | --> | 0.19 | 0 | 0 | 0.199 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3007 | -6.4817
MV/LV Substation ST***042X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =271 kVA | --> | 0.38 | 0 | 0.024 | 0.38 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.317 | -6.4061
MV/LV Substation TA***043 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =421 kVA | --> | 0.598 | 0 | 0.048 | 0.5 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3046 | -6.3575
MV/LV Substation MO***044 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =540 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2769 | -6.3792
MV/LV Substation ST***044X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =143 kVA | --> | 0.19 | 0 | 0.025 | 0.179 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3163 | -6.4004
MV/LV Substation AY***044Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =136 kVA | --> | 0.19 | 0 | 0 | 0.199 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2993 | -6.4911
MV/LV Substation KI***045X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.46 | 13.91 |  | --> | 0.598 | 0 | 0.045 | 0.5 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2812 | -6.3925
MV/LV Substation FE***046 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =360 kVA | --> | 0.38 | 0 | 0 | 0.385 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2922 | -6.3964
MV/LV Substation CU***046X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =242 kVA | --> | 0.38 | 0 | 0.005 | 0.397 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2759 | -6.3776
MV/LV Substation WH***047 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.347 | 13.91 |  | --> | 0.38 | 0 | 0 | 0.387 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2779 | -6.377
MV/LV Substation CU***047X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =299 kVA | --> | 0.38 | 0 | 0 | 0.394 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2756 | -6.375
MV/LV Substation CO***048X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.173 | 13.91 |  | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2939 | -6.384
MV/LV Substation LY***048Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.301 | -6.546
MV/LV Substation BE***049 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =398 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2699 | -6.3353
MV/LV Substation LY***049Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =336 kVA | --> | 0.38 | 0 | 0 | 0.389 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2992 | -6.5367
MV/LV Substation MA***051X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =283 kVA | --> | 0.38 | 0 | 0 | 0.396 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.298 | -6.3684
MV/LV Substation AS***052X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =907 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2808 | -6.3822
MV/LV Substation MA***053 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =333 kVA | --> | 0.38 | 0 | 0.059 | 0.345 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2849 | -6.4114
MV/LV Substation MA***054 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =560 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2853 | -6.4144
MV/LV Substation SM***054X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =275 kVA | --> | 0.38 | 0 | 0.006 | 0.392 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3302 | -6.3454
MV/LV Substation MA***055 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =363 kVA | --> | 0.598 | 0 | 0.007 | 0.5 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.284 | -6.4171
MV/LV Substation KI***056 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.398 | 13.91 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2706 | -6.3723
MV/LV Substation IR***056X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =460 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3271 | -6.3463
MV/LV Substation BA***056Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0.011 | 0.042 | 0 |  | --> | C29 ex GRANGE CASTLE | Grange Castle [T101,T102] | INCHICORE 220KV |  | 53.2924 | -6.4891
MV/LV Substation MA***057 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.323 | 13.91 |  | --> | 0.38 | 0 | 0.004 | 0.387 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2708 | -6.3712
MV/LV Substation DI***058 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =847 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2909 | -6.4204
MV/LV Substation CL***058X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =753 kVA | --> | 0.95 | 0 | 0.005 | 0.5 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3203 | -6.3935
MV/LV Substation RA***058Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | C29 ex GRANGE CASTLE | Grange Castle [T101,T102] | INCHICORE 220KV |  | 53.2888 | -6.4933
MV/LV Substation DI***059 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =458 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2898 | -6.4196
MV/LV Substation PR***059X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =323 kVA | --> | 0.38 | 0 | 0.014 | 0.38 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3179 | -6.3925
MV/LV Substation KI***060 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2722 | -6.3727
MV/LV Substation MO***060X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =213 kVA | --> | 0.38 | 0 | 0.005 | 0.401 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3207 | -6.3959
MV/LV Substation HO***061 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =457 kVA | --> | 0.598 | 0 | 0.015 | 0.5 | 0 |  | --> | C19 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2837 | -6.3506
MV/LV Substation SA***062 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2667 | -6.3663
MV/LV Substation MI***062X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =188 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3221 | -6.3978
MV/LV Substation CL***063 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =499 kVA | --> | 0.598 | 0 | 0.017 | 0.5 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3077 | -6.3667
MV/LV Substation ST***064X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =289 kVA | --> | 0.38 | 0 | 0.031 | 0.372 | 0 |  | --> | C17 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.329 | -6.4009
MV/LV Substation CO***064Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0.015 | 0.039 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3085 | -6.5123
MV/LV Substation M.***065X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =585 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3275 | -6.3982
MV/LV Substation HU***066 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =458 kVA | --> | 0.598 | 0 | 0.018 | 0.5 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2698 | -6.3292
MV/LV Substation HU***067 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =390 kVA | --> | 0.38 | 0 | 0 | 0.381 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.269 | -6.3308
MV/LV Substation NA***068X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3177 | -6.429
MV/LV Substation SL***069 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2721 | -6.4479
MV/LV Substation KI***069X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3152 | -6.4312
MV/LV Substation TY***071 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =194 kVA | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3005 | -6.3432
MV/LV Substation DR***072 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =333 kVA | --> | 0.38 | 0 | 0 | 0.389 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2898 | -6.3934
MV/LV Substation FA***073 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =951 kVA | --> | 0.95 | 0 | 0.06 | 0.5 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3075 | -6.3527
MV/LV Substation GR***074 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =299 kVA | --> | 0.38 | 0 | 0 | 0.394 | 0 |  | --> | C13 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2826 | -6.411
MV/LV Substation ST***074X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =396 kVA | --> | 0.598 | 0 | 0.051 | 0.5 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3166 | -6.3955
MV/LV Substation BO***076 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =480 kVA | --> | 0.598 | 0 | 0.003 | 0.5 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.278 | -6.4448
MV/LV Substation GA***077 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =602 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2785 | -6.4466
MV/LV Substation BO***077X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.095 | 0 | 0.017 | 0.089 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3128 | -6.3979
MV/LV Substation NE***079X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =413 kVA | --> | 0.598 | 0 | 0.035 | 0.5 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3139 | -6.3897
MV/LV Substation KI***081 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.139 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2786 | -6.3749
MV/LV Substation HE***082 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =850 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2841 | -6.4381
MV/LV Substation ST***083Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.302 | -6.4858
MV/LV Substation CL***084 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =939 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.294 | -6.4427
MV/LV Substation KI***085X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3024 | -6.4167
MV/LV Substation HO***088 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =470 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2957 | -6.4295
MV/LV Substation CO***088X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.19 | 0 | 0 | 0.196 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3117 | -6.4172
MV/LV Substation HU***089 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =556 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2705 | -6.3299
MV/LV Substation TA***090 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =175 kVA | --> | 0.19 | 0 | 0.005 | 0.19 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2762 | -6.44
MV/LV Substation KI***090X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =120 kVA | --> | 0.19 | 0 | 0.036 | 0.174 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.2963 | -6.4227
MV/LV Substation OR***091 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =542 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2872 | -6.4317
MV/LV Substation SW***092 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =302 kVA | --> | 0.38 | 0 | 0 | 0.393 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2838 | -6.44
MV/LV Substation PE***092Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.006 | 0.044 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3189 | -6.4738
MV/LV Substation BA***094X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =87 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.2994 | -6.4328
MV/LV Substation SC***095 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C22 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.293 | -6.3446
MV/LV Substation NE***095X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =15 kVA | --> | 0.048 | 0 | 0.024 | 0.034 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.308 | -6.3921
MV/LV Substation OL***096 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =354 kVA | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2721 | -6.3497
MV/LV Substation BL***097 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =513 kVA | --> | 0.598 | 0 | 0.007 | 0.5 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2777 | -6.4768
MV/LV Substation CA***097X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =296 kVA | --> | 0.38 | 0 | 0.02 | 0.379 | 0 |  | --> | C15 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3233 | -6.3892
MV/LV Substation KI***097Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =83 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C29 ex GRANGE CASTLE | Grange Castle [T101,T102] | INCHICORE 220KV |  | 53.3122 | -6.4643
MV/LV Substation GR***098 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =178 kVA | --> | 0.38 | 0 | 0.023 | 0.392 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2777 | -6.4784
MV/LV Substation CA***098X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =383 kVA | --> | 0.598 | 0 | 0.035 | 0.5 | 0 |  | --> | C15 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3216 | -6.3907
MV/LV Substation PE***098Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3162 | -6.4837
MV/LV Substation MO***099X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =517 kVA | --> | 0.598 | 0 | 0.024 | 0.5 | 0 |  | --> | C15 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3223 | -6.3867
MV/LV Substation NE***099Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.19 | 0 | 0 | 0.196 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2964 | -6.513
MV/LV Substation BA***100 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =876 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2944 | -6.4421
MV/LV Substation MO***100X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =554 kVA | --> | 0.598 | 0 | 0.024 | 0.5 | 0 |  | --> | C15 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3214 | -6.3844
MV/LV Substation BE***101 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =496 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2775 | -6.4188
MV/LV Substation MO***101X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =542 kVA | --> | 0.598 | 0 | 0.023 | 0.5 | 0 |  | --> | C15 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3242 | -6.3867
MV/LV Substation CA***102X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =279 kVA | --> | 0.38 | 0 | 0.04 | 0.367 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.326 | -6.3842
MV/LV Substation CO***103 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =586 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2874 | -6.3634
MV/LV Substation MA***103X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =327 kVA | --> | 0.38 | 0 | 0.032 | 0.366 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3279 | -6.387
MV/LV Substation SI***105 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2761 | -6.4518
MV/LV Substation MI***107 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =417 kVA | --> | 0.598 | 0 | 0.189 | 0.487 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2801 | -6.45
MV/LV Substation MI***108 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =345 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.279 | -6.414
MV/LV Substation FO***109 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2831 | -6.393
MV/LV Substation DA***109X |  | 10 kV | _ | LV | 100 kVA :Kiosk Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.095 | 0 | 0.015 | 0.09 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3169 | -6.377
MV/LV Substation NE***110 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.268 | -6.536
MV/LV Substation HE***110X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =828 kVA | --> | 0.95 | 0 | 0.19 | 0.5 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3142 | -6.3777
MV/LV Substation S.***111X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =529 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3179 | -6.381
MV/LV Substation RI***112 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2949 | -6.3764
MV/LV Substation MC***112X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =139 kVA | --> | 0.19 | 0 | 0 | 0.198 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3158 | -6.3823
MV/LV Substation WO***116 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =264 kVA | --> | 0.38 | 0 | 0.044 | 0.366 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2834 | -6.3378
MV/LV Substation TO***116X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =260 kVA | --> | 0.598 | 0 | 0.27 | 0.434 | 0 |  | --> | C22 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3272 | -6.3591
MV/LV Substation WO***117 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =241 kVA | --> | 0.38 | 0 | 0.041 | 0.371 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2812 | -6.3345
MV/LV Substation MA***117X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0 | 0.39 | 0 |  | --> | C22 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3301 | -6.3583
MV/LV Substation WO***118X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =509 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3288 | -6.3543
MV/LV Substation NE***118Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2955 | -6.5137
MV/LV Substation AN***119 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =833 kVA | --> | 0.95 | 0 | 0.09 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.312 | -6.3593
MV/LV Substation MC***119X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =477 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3299 | -6.3536
MV/LV Substation AT***119Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =58 kVA | --> | 0.095 | 0 | 0 | 0.101 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2941 | -6.5123
MV/LV Substation AS***120X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =513 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3307 | -6.3514
MV/LV Substation LO***121 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2869 | -6.3763
MV/LV Substation G.***121X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =574 kVA | --> | 0.598 | 0 | 0.006 | 0.5 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3302 | -6.3503
MV/LV Substation HO***122 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.483 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.287 | -6.3757
MV/LV Substation RO***122X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =358 kVA | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3286 | -6.3437
MV/LV Substation AL***123 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.478 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2871 | -6.3754
MV/LV Substation CA***123X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =314 kVA | --> | 0.95 | 0 | 0.145 | 0.5 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.326 | -6.3499
MV/LV Substation CA***123Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 |  | --> | 0.048 | 0 | 0 | 0.054 | 0 |  | --> | C29 ex GRANGE CASTLE | Grange Castle [T101,T102] | INCHICORE 220KV |  | 53.3125 | -6.4574
MV/LV Substation SW***124 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.495 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2864 | -6.3752
MV/LV Substation TA***125 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.423 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2858 | -6.376
MV/LV Substation AV***125X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =475 kVA | --> | 0.598 | 0 | 0.036 | 0.5 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3246 | -6.3471
MV/LV Substation MI***125Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3199 | -6.4614
MV/LV Substation SY***126 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =394 kVA | --> | 0.38 | 0 | 0.015 | 0.37 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3069 | -6.3686
MV/LV Substation KO***126X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =129 kVA | --> | 0.19 | 0 | 0.011 | 0.191 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3225 | -6.3481
MV/LV Substation WH***127 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2792 | -6.3782
MV/LV Substation BL***127X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =70 kVA | --> | 0.095 | 0 | 0.009 | 0.092 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.322 | -6.3471
MV/LV Substation WH***128 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2804 | -6.3764
MV/LV Substation PA***128X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =832 kVA | --> | 0.95 | 0 | 0.01 | 0.5 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.322 | -6.3457
MV/LV Substation SA***129 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2703 | -6.3898
MV/LV Substation RO***129X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =246 kVA | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3204 | -6.3478
MV/LV Substation GR***129Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =287 kVA | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =384 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.2945 | -6.4776
MV/LV Substation TH***130 |  | 10 kV | _ | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =925 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2933 | -6.3747
MV/LV Substation MU***130X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =505 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3198 | -6.3462
MV/LV Substation MJ***131 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =560 kVA | --> | 0.598 | 0 | 0.11 | 0.5 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2923 | -6.4434
MV/LV Substation J.***131X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =517 kVA | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | C20 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3279 | -6.3519
MV/LV Substation LI***132 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =248 kVA | --> | 0.38 | 0 | 0.011 | 0.392 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2854 | -6.4178
MV/LV Substation CU***132X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =392 kVA | --> | 0.38 | 0 | 0 | 0.381 | 0 |  | --> | C20 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3278 | -6.3502
MV/LV Substation BE***133 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =567 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2757 | -6.4154
MV/LV Substation MI***134 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =485 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2804 | -6.4522
MV/LV Substation DA***137 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =322 kVA | --> | 0.38 | 0 | 0.078 | 0.333 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2717 | -6.3278
MV/LV Substation DA***138 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =582 kVA | --> | 0.598 | 0 | 0.042 | 0.5 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2715 | -6.3252
MV/LV Substation NE***139 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =937 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2881 | -6.3581
MV/LV Substation BA***140X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =230 kVA | --> | 0.38 | 0 | 0 | 0.403 | 0 |  | --> | C14 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3207 | -6.3582
MV/LV Substation AL***141 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2888 | -6.3741
MV/LV Substation FO***141X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =177 kVA | --> | 0.19 | 0 | 0.005 | 0.189 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3196 | -6.3554
MV/LV Substation HO***141Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =330 kVA | --> | 0.38 | 0 | 0 | 0.389 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3184 | -6.3719
MV/LV Substation AL***142 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2885 | -6.3752
MV/LV Substation SY***142X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =377 kVA | --> | 0.38 | 0 | 0 | 0.383 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3171 | -6.349
MV/LV Substation NE***142Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3089 | -6.4027
MV/LV Substation CI***143 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =624 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2819 | -6.4221
MV/LV Substation RO***143X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =331 kVA | --> | 0.38 | 0 | 0 | 0.389 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3171 | -6.3467
MV/LV Substation BA***143Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =173 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3199 | -6.4281
MV/LV Substation CO***144 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2748 | -6.4136
MV/LV Substation JO***144Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =676 kVA | --> | 0.95 | 0 | 0.063 | 0.5 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3154 | -6.3848
MV/LV Substation CI***145Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =312 kVA | --> | 0.38 | 0 | 0 | 0.392 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.329 | -6.3461
MV/LV Substation CI***146 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =927 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2819 | -6.4222
MV/LV Substation PA***146X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =370 kVA | --> | 0.38 | 0 | 0 | 0.384 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3179 | -6.3414
MV/LV Substation NE***146Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =327 kVA | --> | 0.38 | 0 | 0 | 0.39 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3138 | -6.3917
MV/LV Substation CA***147 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =522 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C14 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2841 | -6.43
MV/LV Substation RE***147X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =731 kVA | --> | 0.95 | 0 | 0.04 | 0.5 | 0 |  | --> | C14 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3187 | -6.3626
MV/LV Substation AR***148 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.397 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2828 | -6.3764
MV/LV Substation IN***148X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =288 kVA | --> | 0.38 | 0 | 0.006 | 0.39 | 0 |  | --> | C19 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3283 | -6.3476
MV/LV Substation SA***149 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.278 | -6.4507
MV/LV Substation AL***150 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2885 | -6.3753
MV/LV Substation CO***152X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =55 kVA | --> | 0.095 | 0 | 0 | 0.101 | 0 |  | --> | C17 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.331 | -6.3443
MV/LV Substation AU***154X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | C20 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3259 | -6.3511
MV/LV Substation AL***155 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2887 | -6.3741
MV/LV Substation CI***156 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =628 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.282 | -6.4221
MV/LV Substation PR***157 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =684 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2879 | -6.3567
MV/LV Substation KI***158X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =87 kVA | --> | 0.19 | 0 | 0.005 | 0.201 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2915 | -6.3994
MV/LV Substation P+***160X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =266 kVA | --> | 0.38 | 0 | 0.008 | 0.378 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3218 | -6.4085
MV/LV Substation MA***161 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0 | 0.391 | 0 |  | --> | C13 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2807 | -6.414
MV/LV Substation BR***163 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2879 | -6.3739
MV/LV Substation PR***164 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2878 | -6.3567
MV/LV Substation ST***165 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2829 | -6.3761
MV/LV Substation LA***166 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =299 kVA | --> | 0.38 | 0 | 0 | 0.394 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2919 | -6.4247
MV/LV Substation KI***167 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =278 kVA | --> | 0.38 | 0 | 0 | 0.396 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2946 | -6.4172
MV/LV Substation AY***167X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =498 kVA | --> | 0.598 | 0 | 0.002 | 0.5 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2761 | -6.3664
MV/LV Substation CA***168 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =601 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3112 | -6.348
MV/LV Substation CH***168X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =134 kVA | --> | 0.19 | 0 | 0.015 | 0.188 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3215 | -6.4039
MV/LV Substation SL***169 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =867 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2799 | -6.4454
MV/LV Substation S.***169X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =541 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3155 | -6.3749
MV/LV Substation PA***170 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2871 | -6.3895
MV/LV Substation TY***170X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.005 | 0.392 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2984 | -6.3515
MV/LV Substation FO***171 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =464 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2832 | -6.4252
MV/LV Substation TY***171X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =321 kVA | --> | 0.38 | 0 | 0.013 | 0.381 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2988 | -6.3496
MV/LV Substation TE***172 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =371 kVA | --> | 0.38 | 0 | 0 | 0.384 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.281 | -6.4676
MV/LV Substation TY***172X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =323 kVA | --> | 0.38 | 0 | 0.004 | 0.387 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3004 | -6.3503
MV/LV Substation DU***173Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =308 kVA | --> | 0.38 | 0 | 0.02 | 0.378 | 0 |  | --> | C17 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3265 | -6.4029
MV/LV Substation CU***174 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2748 | -6.3761
MV/LV Substation AS***178Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =464 kVA | --> | 0.598 | 0 | 0.036 | 0.5 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.327 | -6.4084
MV/LV Substation FO***180 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =556 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2832 | -6.4252
MV/LV Substation AI***182 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =510 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2947 | -6.3585
MV/LV Substation WH***182X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0.007 | 0.043 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3059 | -6.3755
MV/LV Substation KI***182Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2681 | -6.379
MV/LV Substation JU***183 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =856 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.294 | -6.3562
MV/LV Substation TA***184 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2874 | -6.3764
MV/LV Substation LY***184Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3001 | -6.5268
MV/LV Substation TA***185 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2875 | -6.3766
MV/LV Substation TA***186 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.25 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2876 | -6.3769
MV/LV Substation DO***186X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =128 kVA | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2752 | -6.3903
MV/LV Substation TA***187 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2877 | -6.3771
MV/LV Substation DO***187X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =136 kVA | --> | 0.19 | 0 | 0.008 | 0.193 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2742 | -6.3887
MV/LV Substation BR***187Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =152 kVA | --> | 0.19 | 0 | 0.009 | 0.19 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.2975 | -6.4206
MV/LV Substation TA***188 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2882 | -6.3776
MV/LV Substation DO***188X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =314 kVA | --> | 0.38 | 0 | 0 | 0.392 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2748 | -6.3926
MV/LV Substation CO***188Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3186 | -6.43
MV/LV Substation TA***189 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2886 | -6.3778
MV/LV Substation YE***189X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =286 kVA | --> | 0.38 | 0 | 0.015 | 0.384 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3264 | -6.3813
MV/LV Substation TA***190 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2889 | -6.3769
MV/LV Substation TA***191 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2889 | -6.3767
MV/LV Substation FL***191Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =521 kVA | --> | 0.598 | 0 | 0.031 | 0.5 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3202 | -6.3894
MV/LV Substation TA***192 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2888 | -6.3758
MV/LV Substation CO***192X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =186 kVA | --> | 0.19 | 0 | 0.005 | 0.188 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2845 | -6.4624
MV/LV Substation SL***193 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =555 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2798 | -6.4454
MV/LV Substation ME***194 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2828 | -6.3763
MV/LV Substation MA***195 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2878 | -6.3567
MV/LV Substation GL***195X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =124 kVA | --> | 0.19 | 0 | 0.03 | 0.178 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2766 | -6.35
MV/LV Substation TA***196 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2878 | -6.375
MV/LV Substation GL***196X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.117 | 13.91 |  | --> | 0.19 | 0 | 0 | 0.201 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2853 | -6.4018
MV/LV Substation GL***197X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.232 | 13.91 |  | --> | 0.38 | 0 | 0.005 | 0.398 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2852 | -6.4
MV/LV Substation VO***198 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2686 | -6.3936
MV/LV Substation CI***199 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =378 kVA | --> | 0.38 | 0 | 0 | 0.383 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2895 | -6.4169
MV/LV Substation AR***200 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.365 | 13.91 |  | --> | 0.38 | 0 | 0 | 0.385 | 0 |  | --> | C18 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.288 | -6.3734
MV/LV Substation FL***200Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =505 kVA | --> | 0.598 | 0 | 0.021 | 0.5 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3186 | -6.3833
MV/LV Substation GL***202 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =357 kVA | --> | 0.38 | 0 | 0.015 | 0.375 | 0 |  | --> | C15 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.289 | -6.3381
MV/LV Substation KI***203 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =341 kVA | --> | 0.38 | 0 | 0 | 0.388 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2779 | -6.4054
MV/LV Substation SO***203X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =352 kVA | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2968 | -6.3567
MV/LV Substation CL***206X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =466 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2798 | -6.4015
MV/LV Substation BA***209 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =16 kVA | --> | 0.048 | 0 | 0 | 0.052 | 0 |  | --> | C14 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.316 | -6.3609
MV/LV Substation CA***210X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =461 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2956 | -6.3427
MV/LV Substation FA***211 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =297 kVA | --> | 0.38 | 0 | 0.013 | 0.384 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2782 | -6.4421
MV/LV Substation CU***211X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =255 kVA | --> | 0.38 | 0 | 0 | 0.399 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2738 | -6.3751
MV/LV Substation BA***212 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =585 kVA | --> | 0.598 | 0 | 0.006 | 0.5 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3075 | -6.3506
MV/LV Substation CU***213X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =266 kVA | --> | 0.38 | 0 | 0 | 0.398 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2734 | -6.3777
MV/LV Substation BO***213Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =303 kVA | --> | 0.38 | 0 | 0 | 0.393 | 0 |  | --> | C20 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3264 | -6.3518
MV/LV Substation SA***214 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =267 kVA | --> | 0.38 | 0 | 0.011 | 0.39 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2798 | -6.446
MV/LV Substation CH***214X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =273 kVA | --> | 0.38 | 0 | 0.024 | 0.379 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3199 | -6.4076
MV/LV Substation SA***215 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =489 kVA | --> | 0.598 | 0 | 0.013 | 0.5 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2815 | -6.4516
MV/LV Substation LY***215Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.19 | 0 | 0 | 0.204 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3 | -6.555
MV/LV Substation SA***216 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2837 | -6.4544
MV/LV Substation CL***216X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =460 kVA | --> | 0.598 | 0 | 0.002 | 0.5 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2793 | -6.3969
MV/LV Substation LY***216Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =190 kVA | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | C20 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2996 | -6.5573
MV/LV Substation BR***219 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2915 | -6.4421
MV/LV Substation BU***219Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2696 | -6.522
MV/LV Substation KI***220Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.281 | -6.4803
MV/LV Substation ST***222 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =356 kVA | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C22 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2951 | -6.3448
MV/LV Substation BE***223 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =291 kVA | --> | 0.38 | 0 | 0.048 | 0.359 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.282 | -6.4612
MV/LV Substation DE***223X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =106 kVA | --> | 0.19 | 0 | 0.019 | 0.188 | 0 |  | --> | C19 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2762 | -6.4105
MV/LV Substation FI***224 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =511 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2842 | -6.4568
MV/LV Substation DO***224X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =279 kVA | --> | 0.38 | 0 | 0 | 0.396 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2738 | -6.3846
MV/LV Substation CO***225 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =206 kVA | --> | 0.38 | 0 | 0.004 | 0.403 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2813 | -6.4657
MV/LV Substation DO***225X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =262 kVA | --> | 0.38 | 0 | 0.035 | 0.372 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2741 | -6.3817
MV/LV Substation OR***226 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =564 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2885 | -6.4277
MV/LV Substation DO***226X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =144 kVA | --> | 0.19 | 0 | 0 | 0.198 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2748 | -6.3829
MV/LV Substation NE***227 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =145 kVA | --> | 0.19 | 0 | 0 | 0.197 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2838 | -6.4743
MV/LV Substation JO***227X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =499 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3086 | -6.3488
MV/LV Substation RA***228 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.38 | 0 | 0 | 0.411 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2817 | -6.4669
MV/LV Substation KI***229 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =481 kVA | --> | 0.598 | 0 | 0.03 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2954 | -6.4209
MV/LV Substation KI***229X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =229 kVA | --> | 0.38 | 0 | 0.021 | 0.387 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2923 | -6.3925
MV/LV Substation CA***230Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.267 | -6.5296
MV/LV Substation RA***232 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =336 kVA | --> | 0.38 | 0 | 0.034 | 0.364 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.278 | -6.4808
MV/LV Substation MO***233 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =428 kVA | --> | 0.598 | 0 | 0.03 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2939 | -6.3702
MV/LV Substation TO***235 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =92 kVA | --> | 0.19 | 0 | 0.015 | 0.193 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2782 | -6.4893
MV/LV Substation GA***235X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =87 kVA | --> | 0.095 | 0 | 0.011 | 0.089 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2924 | -6.4186
MV/LV Substation CH***236X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =252 kVA | --> | 0.38 | 0 | 0.02 | 0.385 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.318 | -6.4123
MV/LV Substation ST***237X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =82 kVA | --> | 0.19 | 0 | 0.019 | 0.191 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3149 | -6.4045
MV/LV Substation KI***238 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =289 kVA | --> | 0.38 | 0 | 0 | 0.395 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2818 | -6.3447
MV/LV Substation WI***238X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =277 kVA | --> | 0.38 | 0 | 0.038 | 0.368 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3124 | -6.4012
MV/LV Substation KI***239 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =671 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2936 | -6.4262
MV/LV Substation OA***239X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =179 kVA | --> | 0.38 | 0 | 0.059 | 0.365 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3134 | -6.4032
MV/LV Substation CR***240 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.272 | -6.4784
MV/LV Substation AR***242X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =274 kVA | --> | 0.38 | 0 | 0 | 0.397 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2968 | -6.3495
MV/LV Substation RA***243X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =294 kVA | --> | 0.598 | 0 | 0.003 | 0.5 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2818 | -6.4714
MV/LV Substation CH***247X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =238 kVA | --> | 0.38 | 0 | 0.032 | 0.378 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3193 | -6.4129
MV/LV Substation EM***248Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2705 | -6.4301
MV/LV Substation WO***249X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0.01 | 0.191 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3212 | -6.3793
MV/LV Substation WO***250X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =227 kVA | --> | 0.38 | 0 | 0.033 | 0.378 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3213 | -6.3777
MV/LV Substation NE***251 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0.005 | 0.046 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2538 | -6.4865
MV/LV Substation MO***251X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =205 kVA | --> | 0.38 | 0 | 0.076 | 0.35 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3222 | -6.3767
MV/LV Substation LY***251Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2956 | -6.551
MV/LV Substation MO***252X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0.018 | 0.184 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3244 | -6.3771
MV/LV Substation SL***253 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =68 kVA | --> | 0.095 | 0 | 0 | 0.099 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2461 | -6.4774
MV/LV Substation WH***253Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2784 | -6.3803
MV/LV Substation KI***254X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =279 kVA | --> | 0.38 | 0 | 0.005 | 0.392 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2772 | -6.4067
MV/LV Substation NE***255 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2605 | -6.4944
MV/LV Substation KI***255X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =266 kVA | --> | 0.38 | 0 | 0 | 0.398 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2776 | -6.402
MV/LV Substation RE***255Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.321 | -6.3693
MV/LV Substation OL***256X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =150 kVA | --> | 0.19 | 0 | 0.005 | 0.193 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3202 | -6.4147
MV/LV Substation SU***256Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2859 | -6.3739
MV/LV Substation OL***257X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =297 kVA | --> | 0.38 | 0 | 0.005 | 0.39 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3197 | -6.4186
MV/LV Substation PI***258X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =142 kVA | --> | 0.38 | 0 | 0.071 | 0.361 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3005 | -6.3716
MV/LV Substation TA***259Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2859 | -6.3758
MV/LV Substation SL***260 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =177 kVA | --> | 0.19 | 0 | 0 | 0.193 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2558 | -6.4725
MV/LV Substation LO***260Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2869 | -6.3762
MV/LV Substation NE***262Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2549 | -6.4859
MV/LV Substation AV***265X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.02 | 0.034 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2872 | -6.3392
MV/LV Substation CO***266 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =21 kVA | --> | 0.048 | 0 | 0 | 0.051 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2774 | -6.501
MV/LV Substation CO***267 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =15 kVA | --> | 0.048 | 0 | 0.015 | 0.041 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2801 | -6.5032
MV/LV Substation KI***268X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =160 kVA | --> | 0.19 | 0 | 0.007 | 0.19 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2761 | -6.3965
MV/LV Substation TA***268Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =409 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2876 | -6.3547
MV/LV Substation WH***269X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =367 kVA | --> | 0.38 | 0 | 0 | 0.384 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2803 | -6.3838
MV/LV Substation TL***269Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =239 kVA | --> | 0.95 | 0 | 0.126 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2863 | -6.4316
MV/LV Substation KI***272 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =789 kVA | --> | 0.95 | 0 | 0.05 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2947 | -6.4263
MV/LV Substation BR***281 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =384 kVA | --> | 0.598 | 0 | 0.222 | 0.467 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.278 | -6.4846
MV/LV Substation BU***287 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =472 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2714 | -6.5192
MV/LV Substation CA***290 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2682 | -6.5297
MV/LV Substation RO***291X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =238 kVA | --> | 0.38 | 0 | 0.017 | 0.389 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2868 | -6.4016
MV/LV Substation QU***292 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2685 | -6.5327
MV/LV Substation QU***293 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2636 | -6.5339
MV/LV Substation RI***293X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =225 kVA | --> | 0.38 | 0 | 0.044 | 0.371 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3266 | -6.3903
MV/LV Substation SU***294X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.277 | 13.91 |  | --> | 0.38 | 0 | 0.039 | 0.368 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2819 | -6.4062
MV/LV Substation SY***295X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =175 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3043 | -6.3661
MV/LV Substation GO***296 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =116 kVA | --> | 0.19 | 0 | 0 | 0.201 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2526 | -6.5373
MV/LV Substation FA***297 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2575 | -6.5275
MV/LV Substation PO***299 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.095 | 0 | 0.006 | 0.091 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2467 | -6.5472
MV/LV Substation PD***307 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2468 | -6.5337
MV/LV Substation PD***308 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =297 kVA | --> | 0.38 | 0 | 0 | 0.394 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2444 | -6.5363
MV/LV Substation RA***309 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =70 kVA | --> | 0.095 | 0 | 0.015 | 0.088 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2777 | -6.4651
MV/LV Substation TA***310 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =216 kVA | --> | 0.38 | 0 | 0.049 | 0.368 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3027 | -6.3617
MV/LV Substation TH***311 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2746 | -6.4409
MV/LV Substation SL***322 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0.005 | 0.094 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2668 | -6.4359
MV/LV Substation RO***323 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =163 kVA | --> | 0.19 | 0 | 0.016 | 0.183 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2683 | -6.4342
MV/LV Substation CR***325 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.257 | -6.4447
MV/LV Substation BE***330X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.267 | 13.91 |  | --> | 0.38 | 0 | 0.059 | 0.354 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2993 | -6.3799
MV/LV Substation HI***331 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =72 kVA | --> | 0.095 | 0 | 0.005 | 0.095 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2491 | -6.4387
MV/LV Substation AL***331X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =246 kVA | --> | 0.38 | 0 | 0.032 | 0.377 | 0 |  | --> | C15 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2893 | -6.3831
MV/LV Substation AL***332X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =435 kVA | --> | 0.598 | 0 | 0.023 | 0.5 | 0 |  | --> | C16 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2864 | -6.3804
MV/LV Substation MA***333X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =336 kVA | --> | 0.598 | 0 | 0.026 | 0.5 | 0 |  | --> | C16 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2871 | -6.3832
MV/LV Substation RA***334 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2406 | -6.447
MV/LV Substation KI***334X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0.014 | 0.186 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2754 | -6.4068
MV/LV Substation BR***335 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.095 | 0 | 0.01 | 0.096 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2367 | -6.454
MV/LV Substation RO***336X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =295 kVA | --> | 0.38 | 0 | 0 | 0.394 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2882 | -6.4003
MV/LV Substation RO***337X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =307 kVA | --> | 0.38 | 0 | 0 | 0.392 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2889 | -6.4032
MV/LV Substation AG***344 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =18 kVA | --> | 0.048 | 0 | 0.006 | 0.047 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.233 | -6.4318
MV/LV Substation AG***356 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2315 | -6.4208
MV/LV Substation RA***381 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =574 kVA | --> | 0.598 | 0 | 0.024 | 0.5 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2831 | -6.3874
MV/LV Substation RA***382 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =344 kVA | --> | 0.38 | 0 | 0.028 | 0.367 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2841 | -6.3879
MV/LV Substation RA***383 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =343 kVA | --> | 0.38 | 0 | 0.013 | 0.378 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2837 | -6.3897
MV/LV Substation RA***385 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =237 kVA | --> | 0.38 | 0 | 0.014 | 0.391 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2852 | -6.3898
MV/LV Substation RA***386 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =331 kVA | --> | 0.38 | 0 | 0.014 | 0.379 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2852 | -6.3881
MV/LV Substation AS***387 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =308 kVA | --> | 0.38 | 0 | 0.008 | 0.386 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2883 | -6.3865
MV/LV Substation BI***389 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0.017 | 0.5 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2907 | -6.3842
MV/LV Substation BI***390 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0.011 | 0.5 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2913 | -6.3842
MV/LV Substation KI***390X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =232 kVA | --> | 0.38 | 0 | 0.01 | 0.395 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.327 | -6.4272
MV/LV Substation KI***391X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =340 kVA | --> | 0.38 | 0 | 0.005 | 0.384 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.327 | -6.4299
MV/LV Substation P.***393X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.446 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2952 | -6.3852
MV/LV Substation BR***394X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2499 | -6.5415
MV/LV Substation OA***395X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =120 kVA | --> | 0.19 | 0 | 0.01 | 0.193 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3253 | -6.3933
MV/LV Substation B.***396X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.293 | -6.4192
MV/LV Substation PR***398X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =135 kVA | --> | 0.19 | 0 | 0 | 0.199 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2952 | -6.3736
MV/LV Substation CE***399X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =589 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3183 | -6.3432
MV/LV Substation KI***400 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =70 kVA | --> | 0.095 | 0 | 0 | 0.099 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2745 | -6.4031
MV/LV Substation NE***4004 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =768 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2869 | -6.3594
MV/LV Substation KI***4007 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2702 | -6.4029
MV/LV Substation SP***4009 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =227 kVA | --> | 0.38 | 0 | 0 | 0.403 | 0 |  | --> | C16 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2873 | -6.3781
MV/LV Substation DE***400X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =252 kVA | --> | 0.38 | 0 | 0.017 | 0.387 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3233 | -6.4255
MV/LV Substation AT***4010 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2482 | -6.5329
MV/LV Substation KC***4012 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =172 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3101 | -6.3588
MV/LV Substation SP***4018 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2917 | -6.327
MV/LV Substation EL***4020 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =344 kVA | --> | 0.38 | 0 | 0.045 | 0.354 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2717 | -6.3839
MV/LV Substation MA***4024 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2729 | -6.4468
MV/LV Substation JO***403 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =66 kVA | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2741 | -6.4113
MV/LV Substation CO***4032 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 13.91 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C11 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2933 | -6.3779
MV/LV Substation BR***4034 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =397 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2958 | -6.362
MV/LV Substation WE***4037 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3102 | -6.3578
MV/LV Substation JO***4040 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.273 | -6.4141
MV/LV Substation OL***4041 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2534 | -6.5365
MV/LV Substation PP***4043 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.275 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2944 | -6.3839
MV/LV Substation RI***4046 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =335 kVA | --> | 0.38 | 0 | 0 | 0.389 | 0 |  | --> | C14 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2814 | -6.3754
MV/LV Substation DE***4050 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =379 kVA | --> | 0.38 | 0 | 0 | 0.383 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2826 | -6.4193
MV/LV Substation AI***4056 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =377 kVA | --> | 0.38 | 0 | 0 | 0.383 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2941 | -6.3636
MV/LV Substation LO***4059 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3181 | -6.5125
MV/LV Substation EM***406 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2739 | -6.4256
MV/LV Substation KN***4060 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2603 | -6.4809
MV/LV Substation WA***4062 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =491 kVA | --> | 0.598 | 0 | 0.05 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2949 | -6.4257
MV/LV Substation WI***4063 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =491 kVA | --> | 0.598 | 0 | 0.024 | 0.5 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2802 | -6.4777
MV/LV Substation FO***4064 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =385 kVA | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2922 | -6.3753
MV/LV Substation JO***4065 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =273 kVA | --> | 0.38 | 0 | 0.029 | 0.375 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2794 | -6.479
MV/LV Substation M5***4066 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =170 kVA | --> | 0.38 | 0 | 0 | 0.41 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3086 | -6.3533
MV/LV Substation EL***4067 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =277 kVA | --> | 0.38 | 0 | 0.202 | 0.247 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2715 | -6.3806
MV/LV Substation AR***4068 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =509 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2789 | -6.3818
MV/LV Substation JO***407 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2719 | -6.415
MV/LV Substation JA***4070 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C14 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2935 | -6.367
MV/LV Substation LA***4071 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =882 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2921 | -6.4231
MV/LV Substation DO***4073 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 |  | --> | 0.38 | 0 | 0.257 | 0.241 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2682 | -6.3446
MV/LV Substation AB***4074 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =577 kVA | --> | 0.598 | 0 | 0.124 | 0.5 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2709 | -6.3262
MV/LV Substation PO***4077 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2961 | -6.3664
MV/LV Substation WE***4078 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =775 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2963 | -6.373
MV/LV Substation TA***4083 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0 | 0.389 | 0 |  | --> | C15 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2952 | -6.3379
MV/LV Substation BR***4084 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =768 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2974 | -6.3577
MV/LV Substation GR***4085 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0.01 | 0.382 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2948 | -6.3504
MV/LV Substation CI***4088 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =171 kVA | --> | 0.38 | 0 | 0.092 | 0.342 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2878 | -6.4213
MV/LV Substation CI***4089 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =202 kVA | --> | 0.38 | 0 | 0.115 | 0.321 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2876 | -6.4183
MV/LV Substation RA***408X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =310 kVA | --> | 0.38 | 0 | 0.009 | 0.386 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2793 | -6.4067
MV/LV Substation TY***4090 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =334 kVA | --> | 0.38 | 0 | 0 | 0.389 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2984 | -6.3456
MV/LV Substation CH***4092 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =560 kVA | --> | 0.598 | 0 | 0.098 | 0.5 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2896 | -6.4053
MV/LV Substation DR***4093 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2793 | -6.4505
MV/LV Substation KI***4094 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =582 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3063 | -6.3724
MV/LV Substation BA***4095 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =228 kVA | --> | 0.38 | 0 | 0.056 | 0.361 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2682 | -6.3336
MV/LV Substation CL***4096 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =346 kVA | --> | 0.38 | 0 | 0 | 0.387 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3179 | -6.3924
MV/LV Substation TE***4098 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =397 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3034 | -6.3502
MV/LV Substation WO***409X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =250 kVA | --> | 0.38 | 0 | 0.024 | 0.382 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.325 | -6.3791
MV/LV Substation RA***4101 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =393 kVA | --> | 0.38 | 0 | 0.02 | 0.366 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2754 | -6.4856
MV/LV Substation LI***4102 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.3015 | -6.3779
MV/LV Substation ML***4103 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =458 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2963 | -6.4424
MV/LV Substation MO***4104 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =895 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2947 | -6.4448
MV/LV Substation DO***4107 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2701 | -6.3428
MV/LV Substation BR***410X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =131 kVA | --> | 0.19 | 0 | 0.013 | 0.19 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2863 | -6.4137
MV/LV Substation CU***4110 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =621 kVA | --> | 0.598 | 0 | 0.021 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2876 | -6.4289
MV/LV Substation SA***4112 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2766 | -6.4477
MV/LV Substation KE***4113 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.299 | -6.4263
MV/LV Substation BE***4114 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3028 | -6.3885
MV/LV Substation CU***4115 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =353 kVA | --> | 0.38 | 0 | 0.078 | 0.329 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3252 | -6.4169
MV/LV Substation DO***4116 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2694 | -6.3471
MV/LV Substation DO***4117 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2688 | -6.3466
MV/LV Substation AT***4118 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2925 | -6.5244
MV/LV Substation AR***4119 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2956 | -6.4232
MV/LV Substation CH***411X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0.014 | 0.188 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3198 | -6.4123
MV/LV Substation JO***4123 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2685 | -6.4337
MV/LV Substation LE***4126 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0.08 | 0.326 | 0 |  | --> | C15 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3208 | -6.3886
MV/LV Substation WA***4127 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =131 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2976 | -6.3627
MV/LV Substation CO***4129 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =560 kVA | --> | 0.598 | 0 | 0.208 | 0.454 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3175 | -6.4169
MV/LV Substation BL***4130 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2769 | -6.4748
MV/LV Substation ED***4131 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2872 | -6.4259
MV/LV Substation KI***4132 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =398 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2679 | -6.3773
MV/LV Substation BA***4136 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =380 kVA | --> | 0.38 | 0 | 0 | 0.383 | 0 |  | --> | C15 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2897 | -6.3418
MV/LV Substation PA***4137 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2884 | -6.433
MV/LV Substation PA***4138 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.287 | -6.4346
MV/LV Substation PA***4139 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2857 | -6.4339
MV/LV Substation MA***414 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =551 kVA | --> | 0.598 | 0 | 0.015 | 0.5 | 0 |  | --> | C16 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2844 | -6.3848
MV/LV Substation TH***4141 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2838 | -6.4193
MV/LV Substation TH***4142 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2835 | -6.4209
MV/LV Substation GM***4144 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =24 kVA | --> | 0.048 | 0 | 0 | 0.051 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3153 | -6.3742
MV/LV Substation TH***4146 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2849 | -6.4273
MV/LV Substation CI***4147 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =995 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2849 | -6.4277
MV/LV Substation TH***4148 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2885 | -6.419
MV/LV Substation TH***4149 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2892 | -6.4183
MV/LV Substation RA***414X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =122 kVA | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C19 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3005 | -6.3417
MV/LV Substation MA***415 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =352 kVA | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C16 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2854 | -6.385
MV/LV Substation OL***4153 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3102 | -6.3631
MV/LV Substation NA***4154 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =560 kVA | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.322 | -6.4093
MV/LV Substation MO***4158 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2806 | -6.5022
MV/LV Substation MA***4159 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C15 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2906 | -6.3817
MV/LV Substation PI***415X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =91 kVA | --> | 0.19 | 0 | 0.012 | 0.195 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3137 | -6.4062
MV/LV Substation G ***4161 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3086 | -6.3519
MV/LV Substation WO***4163 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0.013 | 0.5 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2895 | -6.385
MV/LV Substation RO***4166 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =361 kVA | --> | 0.38 | 0 | 0 | 0.385 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3174 | -6.3463
MV/LV Substation ML***4168 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2943 | -6.4482
MV/LV Substation ML***4169 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2927 | -6.4505
MV/LV Substation AL***416X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =51 kVA | --> | 0.19 | 0 | 0 | 0.209 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2721 | -6.3558
MV/LV Substation ML***4170 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =131 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2888 | -6.4557
MV/LV Substation BE***4172 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2693 | -6.3656
MV/LV Substation SA***4173 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =364 kVA | --> | 0.38 | 0 | 0 | 0.385 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3224 | -6.3975
MV/LV Substation PA***4174 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2867 | -6.4374
MV/LV Substation TA***4175 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2891 | -6.4388
MV/LV Substation SI***4176 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2883 | -6.437
MV/LV Substation WE***4178 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.282 | -6.372
MV/LV Substation BA***4179 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2797 | -6.4199
MV/LV Substation AL***417X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =254 kVA | --> | 0.38 | 0 | 0.015 | 0.388 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2724 | -6.3519
MV/LV Substation MB***4180 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2941 | -6.3843
MV/LV Substation SA***4182 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =377 kVA | --> | 0.38 | 0 | 0 | 0.383 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3201 | -6.3931
MV/LV Substation CA***4183 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2757 | -6.3945
MV/LV Substation OS***4184 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =990 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2808 | -6.4188
MV/LV Substation PE***4185 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2821 | -6.4187
MV/LV Substation RO***4188 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2651 | -6.4867
MV/LV Substation AL***418X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0.005 | 0.387 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2744 | -6.3542
MV/LV Substation SO***4191 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2938 | -6.4116
MV/LV Substation S.***4192 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2932 | -6.4104
MV/LV Substation C ***4193 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2751 | -6.5113
MV/LV Substation OL***4195 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2686 | -6.3308
MV/LV Substation BB***4196 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2938 | -6.4314
MV/LV Substation IN***4199 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C16 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2915 | -6.3729
MV/LV Substation BO***420 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =90 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2721 | -6.3582
MV/LV Substation CO***4200 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.294 | -6.3841
MV/LV Substation SP***4201 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3085 | -6.3494
MV/LV Substation GE***4202 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =622 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2675 | -6.3392
MV/LV Substation AP***4203 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2785 | -6.489
MV/LV Substation BO***4205 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =879 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3165 | -6.3967
MV/LV Substation FI***4206 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2768 | -6.349
MV/LV Substation GL***4207 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.293 | -6.3672
MV/LV Substation FI***4208 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2671 | -6.4859
MV/LV Substation BL***4213 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2844 | -6.4261
MV/LV Substation TR***4214 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =984 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2845 | -6.4236
MV/LV Substation ML***4216 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =473 kVA | --> | 0.598 | 0 | 0.06 | 0.5 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2887 | -6.4562
MV/LV Substation BR***4217 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2806 | -6.3589
MV/LV Substation BL***4219 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2844 | -6.4261
MV/LV Substation ST***422 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.19 | 0 | 0.016 | 0.192 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2698 | -6.3567
MV/LV Substation RO***4220 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2943 | -6.4202
MV/LV Substation CA***4222 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =626 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2819 | -6.4248
MV/LV Substation CA***4223 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =883 kVA | --> | 0.95 | 0 | 0.004 | 0.5 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2837 | -6.4235
MV/LV Substation AI***4225 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2929 | -6.357
MV/LV Substation AI***4226 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2929 | -6.3569
MV/LV Substation CA***4228 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =626 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2819 | -6.4225
MV/LV Substation CA***4229 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =994 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2819 | -6.4224
MV/LV Substation KI***423 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =90 kVA | --> | 0.19 | 0 | 0.015 | 0.193 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2682 | -6.3644
MV/LV Substation CO***4230 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.295 | -6.3727
MV/LV Substation CA***4231 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =628 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3284 | -6.4096
MV/LV Substation BS***4232 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C16 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2911 | -6.3751
MV/LV Substation TH***4235 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =442 kVA | --> | 0.598 | 0 | 0.14 | 0.5 | 0 |  | --> | C22 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2899 | -6.4164
MV/LV Substation TH***4236 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.291 | -6.4113
MV/LV Substation FO***4238 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2905 | -6.4144
MV/LV Substation CA***4240 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3118 | -6.3522
MV/LV Substation CA***4241 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3132 | -6.3538
MV/LV Substation RA***4242 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =399 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2761 | -6.487
MV/LV Substation IN***4243 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =614 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2911 | -6.3745
MV/LV Substation NE***4246 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =362 kVA | --> | 0.38 | 0 | 0 | 0.385 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3124 | -6.3747
MV/LV Substation AI***4247 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.293 | -6.3564
MV/LV Substation CI***4248 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2871 | -6.4246
MV/LV Substation NE***425 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2659 | -6.3827
MV/LV Substation AI***4251 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.293 | -6.3674
MV/LV Substation OI***4252 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2929 | -6.368
MV/LV Substation EX***4256 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =848 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3282 | -6.348
MV/LV Substation MA***4260 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =587 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2806 | -6.4162
MV/LV Substation SW***4264 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =571 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2855 | -6.4527
MV/LV Substation SW***4265 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2838 | -6.4513
MV/LV Substation SW***4267 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =617 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2848 | -6.4538
MV/LV Substation NV***4269 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.2994 | -6.4329
MV/LV Substation CA***4272 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C19 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3308 | -6.3483
MV/LV Substation BC***4275 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2682 | -6.3398
MV/LV Substation CI***4276 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2837 | -6.4353
MV/LV Substation SA***4290 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =375 kVA | --> | 0.38 | 0 | 0 | 0.383 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2837 | -6.4546
MV/LV Substation HO***4293 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2763 | -6.4785
MV/LV Substation MO***433X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =124 kVA | --> | 0.19 | 0 | 0.01 | 0.193 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3214 | -6.373
MV/LV Substation AL***434X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.299 | -6.3732
MV/LV Substation TO***436X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =131 kVA | --> | 0.19 | 0 | 0.018 | 0.186 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3213 | -6.3951
MV/LV Substation DE***437X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =179 kVA | --> | 0.19 | 0 | 0.01 | 0.186 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3237 | -6.42
MV/LV Substation TH***439X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2679 | -6.3828
MV/LV Substation BR***441X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =221 kVA | --> | 0.38 | 0 | 0.009 | 0.397 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2872 | -6.4077
MV/LV Substation BR***442X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =146 kVA | --> | 0.19 | 0 | 0.005 | 0.194 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2892 | -6.4066
MV/LV Substation KI***444X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =132 kVA | --> | 0.19 | 0 | 0 | 0.199 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.276 | -6.4064
MV/LV Substation RE***445X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2921 | -6.3696
MV/LV Substation HA***449X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =276 kVA | --> | 0.38 | 0 | 0.023 | 0.38 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3116 | -6.404
MV/LV Substation BE***451X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.243 | 13.91 |  | --> | 0.38 | 0 | 0.063 | 0.354 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2998 | -6.3812
MV/LV Substation WO***452X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =228 kVA | --> | 0.38 | 0 | 0.029 | 0.381 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3235 | -6.3829
MV/LV Substation BA***456X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =213 kVA | --> | 0.38 | 0 | 0.083 | 0.343 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2737 | -6.3487
MV/LV Substation PA***457X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =73 kVA | --> | 0.19 | 0 | 0.048 | 0.171 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3027 | -6.3522
MV/LV Substation GL***458X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =108 kVA | --> | 0.19 | 0 | 0.015 | 0.191 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2728 | -6.366
MV/LV Substation RE***459X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0.02 | 0.178 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2629 | -6.48
MV/LV Substation KE***460X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.215 | 13.91 |  | --> | 0.38 | 0 | 0 | 0.404 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2971 | -6.3787
MV/LV Substation WO***461X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =273 kVA | --> | 0.38 | 0 | 0 | 0.397 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3235 | -6.3799
MV/LV Substation MC***463X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =469 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3301 | -6.3513
MV/LV Substation PR***466X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =240 kVA | --> | 0.38 | 0 | 0 | 0.401 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2965 | -6.3731
MV/LV Substation OL***469 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =142 kVA | --> | 0.19 | 0 | 0.007 | 0.193 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2764 | -6.3568
MV/LV Substation RO***470X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2924 | -6.44
MV/LV Substation OR***472X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =203 kVA | --> | 0.38 | 0 | 0.045 | 0.373 | 0 |  | --> | C15 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3228 | -6.3927
MV/LV Substation EL***473 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =113 kVA | --> | 0.19 | 0 | 0.007 | 0.196 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2711 | -6.3488
MV/LV Substation OL***474 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =307 kVA | --> | 0.38 | 0 | 0.058 | 0.35 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2711 | -6.345
MV/LV Substation BE***475X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.139 | 13.91 |  | --> | 0.19 | 0 | 0 | 0.198 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2986 | -6.3862
MV/LV Substation BE***476X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0 | 0.193 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2591 | -6.4966
MV/LV Substation CO***481X |  | 10 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0 | 0 | Constrained, otherwise capacity available =28 kVA | --> | 0.031 | 0 | 0 | 0.032 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2744 | -6.416
MV/LV Substation CA***482 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =561 kVA | --> | 0.598 | 0 | 0.015 | 0.5 | 0 |  | --> | C15 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2924 | -6.338
MV/LV Substation CA***483 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =330 kVA | --> | 0.38 | 0 | 0.008 | 0.384 | 0 |  | --> | C15 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2924 | -6.341
MV/LV Substation BA***484 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =220 kVA | --> | 0.38 | 0 | 0.018 | 0.39 | 0 |  | --> | C15 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2911 | -6.3398
MV/LV Substation MC***484X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =322 kVA | --> | 0.38 | 0 | 0 | 0.39 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3277 | -6.3445
MV/LV Substation WA***485X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =378 kVA | --> | 0.38 | 0 | 0 | 0.383 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2958 | -6.3554
MV/LV Substation MO***488X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =194 kVA | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.303 | -6.4286
MV/LV Substation KI***490X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =180 kVA | --> | 0.19 | 0 | 0 | 0.193 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2492 | -6.5322
MV/LV Substation MI***492X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0.023 | 0.181 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2895 | -6.3874
MV/LV Substation MC***497X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =388 kVA | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3294 | -6.3542
MV/LV Substation RO***499X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =57 kVA | --> | 0.095 | 0 | 0.005 | 0.097 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3017 | -6.4348
MV/LV Substation WE***500X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =762 kVA | --> | 0.95 | 0 | 0.136 | 0.5 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3224 | -6.3694
MV/LV Substation RO***502X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3005 | -6.4165
MV/LV Substation MO***506X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =467 kVA | --> | 0.598 | 0 | 0.065 | 0.5 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3153 | -6.3635
MV/LV Substation AL***508X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =376 kVA | --> | 0.38 | 0 | 0.01 | 0.376 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.313 | -6.3599
MV/LV Substation BU***509X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =159 kVA | --> | 0.19 | 0 | 0 | 0.196 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3106 | -6.4037
MV/LV Substation CH***510X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =280 kVA | --> | 0.38 | 0 | 0.025 | 0.378 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3193 | -6.4098
MV/LV Substation LO***513X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =355 kVA | --> | 0.38 | 0 | 0.005 | 0.382 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3237 | -6.3457
MV/LV Substation CL***515X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =356 kVA | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C14 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3223 | -6.3555
MV/LV Substation WE***516X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =388 kVA | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3222 | -6.3686
MV/LV Substation ST***517X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.003 | 0.394 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3154 | -6.4072
MV/LV Substation HA***522X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =304 kVA | --> | 0.38 | 0 | 0 | 0.393 | 0 |  | --> | C20 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3258 | -6.3541
MV/LV Substation WE***523X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.598 | 0 | 0.055 | 0.5 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3223 | -6.4192
MV/LV Substation KI***524X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =437 kVA | --> | 0.598 | 0 | 0.014 | 0.5 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.329 | -6.427
MV/LV Substation HA***527X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0.075 | 0.336 | 0 |  | --> | C20 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3241 | -6.3562
MV/LV Substation TH***528X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =303 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3245 | -6.3956
MV/LV Substation PE***530X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3207 | -6.4721
MV/LV Substation BU***531X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =244 kVA | --> | 0.38 | 0 | 0.026 | 0.382 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3101 | -6.4061
MV/LV Substation B/***533X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =343 kVA | --> | 0.38 | 0 | 0 | 0.388 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3252 | -6.3607
MV/LV Substation WA***534X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =378 kVA | --> | 0.38 | 0 | 0 | 0.383 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3247 | -6.3705
MV/LV Substation TI***535X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =385 kVA | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | C14 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3185 | -6.3598
MV/LV Substation RO***538X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =347 kVA | --> | 0.38 | 0 | 0 | 0.387 | 0 |  | --> | C14 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3212 | -6.3542
MV/LV Substation CL***539X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =187 kVA | --> | 0.38 | 0 | 0 | 0.408 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3182 | -6.3663
MV/LV Substation BE***540X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =820 kVA | --> | 0.95 | 0 | 0.01 | 0.5 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3139 | -6.3934
MV/LV Substation OL***542X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =162 kVA | --> | 0.19 | 0 | 0.02 | 0.18 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3272 | -6.3452
MV/LV Substation CA***543X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.19 | 0 | 0 | 0.195 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3059 | -6.4173
MV/LV Substation RE***544X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.598 | 0 | 0.036 | 0.5 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3185 | -6.3636
MV/LV Substation KY***546X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =521 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3294 | -6.3433
MV/LV Substation TA***549X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.19 | 0 | 0 | 0.21 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3191 | -6.3552
MV/LV Substation MO***550X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =207 kVA | --> | 0.38 | 0 | 0.088 | 0.34 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3191 | -6.3766
MV/LV Substation I ***553X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =462 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2825 | -6.3828
MV/LV Substation AR***555X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =504 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3252 | -6.3718
MV/LV Substation ME***556X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =273 kVA | --> | 0.38 | 0 | 0 | 0.397 | 0 |  | --> | C14 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3167 | -6.3543
MV/LV Substation HO***560 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =550 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3287 | -6.3562
MV/LV Substation MA***561X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =151 kVA | --> | 0.19 | 0 | 0.004 | 0.194 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2978 | -6.3641
MV/LV Substation SP***562X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =732 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2868 | -6.3609
MV/LV Substation LI***563X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =171 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3069 | -6.3581
MV/LV Substation PU***564 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =590 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2922 | -6.3761
MV/LV Substation DO***565X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =547 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3116 | -6.357
MV/LV Substation MI***566 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =334 kVA | --> | 0.38 | 0 | 0 | 0.389 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2931 | -6.3653
MV/LV Substation F.***568 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =60 kVA | --> | 0.095 | 0 | 0.05 | 0.063 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3202 | -6.3501
MV/LV Substation EL***569 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =201 kVA | --> | 0.38 | 0 | 0.061 | 0.361 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.303 | -6.3548
MV/LV Substation TY***570 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =527 kVA | --> | 0.598 | 0 | 0.024 | 0.5 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2771 | -6.3463
MV/LV Substation MA***571X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2362 | -6.453
MV/LV Substation KI***572 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =523 kVA | --> | 0.598 | 0 | 0.058 | 0.5 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.277 | -6.3431
MV/LV Substation CA***573 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.38 | 0 | 0.076 | 0.356 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2782 | -6.3401
MV/LV Substation SA***573X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =56 kVA | --> | 0.095 | 0 | 0 | 0.101 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2774 | -6.4489
MV/LV Substation GL***574 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =436 kVA | --> | 0.598 | 0 | 0.106 | 0.5 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.28 | -6.3295
MV/LV Substation LO***577 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =20 kVA | --> | 0.19 | 0 | 0 | 0.213 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.28 | -6.3812
MV/LV Substation A.***578X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 |  | --> | 0.38 | 0 | 0.036 | 0.412 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3104 | -6.3579
MV/LV Substation CA***580X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =324 kVA | --> | 0.38 | 0 | 0.012 | 0.381 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2795 | -6.3264
MV/LV Substation DO***581X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =115 kVA | --> | 0.19 | 0 | 0.017 | 0.189 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2787 | -6.3482
MV/LV Substation JO***588X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =177 kVA | --> | 0.19 | 0 | 0 | 0.193 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2784 | -6.4095
MV/LV Substation LL***592 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =538 kVA | --> | 0.598 | 0 | 0.02 | 0.5 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2904 | -6.3871
MV/LV Substation BR***594X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2743 | -6.4849
MV/LV Substation OL***596 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =502 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2763 | -6.3535
MV/LV Substation CA***597X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =134 kVA | --> | 0.19 | 0 | 0.018 | 0.185 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2829 | -6.3273
MV/LV Substation DU***599X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =166 kVA | --> | 0.19 | 0 | 0.04 | 0.165 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2509 | -6.4969
MV/LV Substation SU***603X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =502 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2869 | -6.3705
MV/LV Substation SU***604X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2858 | -6.3707
MV/LV Substation BR***605 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.2996 | -6.4226
MV/LV Substation SU***605X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.272 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2861 | -6.3726
MV/LV Substation PE***606 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =290 kVA | --> | 0.38 | 0 | 0.006 | 0.39 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2777 | -6.4704
MV/LV Substation SU***606X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.474 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2867 | -6.3734
MV/LV Substation GR***609X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =289 kVA | --> | 0.38 | 0 | 0.033 | 0.37 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.275 | -6.3324
MV/LV Substation RE***610 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =246 kVA | --> | 0.38 | 0 | 0.031 | 0.378 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2988 | -6.3638
MV/LV Substation LE***612 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =357 kVA | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3233 | -6.4121
MV/LV Substation LE***613 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =336 kVA | --> | 0.38 | 0 | 0.004 | 0.386 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3224 | -6.4124
MV/LV Substation MU***613X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =153 kVA | --> | 0.19 | 0 | 0.005 | 0.192 | 0 |  | --> | C15 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.287 | -6.3454
MV/LV Substation LE***614 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =324 kVA | --> | 0.38 | 0 | 0.007 | 0.385 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3234 | -6.4158
MV/LV Substation LE***615 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.19 | 0 | 0.004 | 0.193 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.322 | -6.4159
MV/LV Substation TV***619X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3096 | -6.3552
MV/LV Substation OA***623 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =114 kVA | --> | 0.19 | 0 | 0.015 | 0.19 | 0 |  | --> | C17 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3281 | -6.4045
MV/LV Substation MI***623X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =450 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3085 | -6.3574
MV/LV Substation LI***626 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =105 kVA | --> | 0.19 | 0 | 0.04 | 0.173 | 0 |  | --> | C14 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3165 | -6.3607
MV/LV Substation RA***627X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =392 kVA | --> | 0.38 | 0 | 0 | 0.381 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2768 | -6.4719
MV/LV Substation PA***629 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =121 kVA | --> | 0.19 | 0 | 0.023 | 0.183 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2988 | -6.3677
MV/LV Substation GR***629X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =242 kVA | --> | 0.38 | 0 | 0.03 | 0.379 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2938 | -6.3475
MV/LV Substation UN***630X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =392 kVA | --> | 0.38 | 0 | 0.004 | 0.378 | 0 |  | --> | C12 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2914 | -6.3692
MV/LV Substation SL***631X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2542 | -6.4833
MV/LV Substation CA***632X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =24 kVA | --> | 0.048 | 0 | 0 | 0.051 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2656 | -6.5441
MV/LV Substation HO***637 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =387 kVA | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2967 | -6.375
MV/LV Substation CO***637X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2869 | -6.4602
MV/LV Substation KE***640X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.276 | -6.4955
MV/LV Substation TR***641X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2759 | -6.4953
MV/LV Substation FA***642X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2741 | -6.5116
MV/LV Substation BR***644X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =314 kVA | --> | 0.38 | 0 | 0 | 0.392 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2906 | -6.3345
MV/LV Substation GL***645X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =336 kVA | --> | 0.38 | 0 | 0.009 | 0.382 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2777 | -6.33
MV/LV Substation MC***650X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =413 kVA | --> | 0.598 | 0 | 0.02 | 0.5 | 0 |  | --> | C11 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2877 | -6.3678
MV/LV Substation BA***652X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =366 kVA | --> | 0.38 | 0 | 0 | 0.385 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2917 | -6.3348
MV/LV Substation AB***653X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =162 kVA | --> | 0.19 | 0 | 0 | 0.195 | 0 |  | --> | C12 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2899 | -6.3688
MV/LV Substation MI***655X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =356 kVA | --> | 0.598 | 0 | 0.048 | 0.5 | 0 |  | --> | C19 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2834 | -6.3558
MV/LV Substation QU***659X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =386 kVA | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2792 | -6.3804
MV/LV Substation KI***667 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =172 kVA | --> | 0.19 | 0 | 0.004 | 0.191 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.301 | -6.3582
MV/LV Substation KI***672 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =254 kVA | --> | 0.38 | 0 | 0.025 | 0.381 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2799 | -6.343
MV/LV Substation KI***687X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =264 kVA | --> | 0.38 | 0 | 0 | 0.398 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2905 | -6.4005
MV/LV Substation CI***691X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =739 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2889 | -6.3738
MV/LV Substation DO***692X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =131 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2877 | -6.3663
MV/LV Substation CE***693X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2678 | -6.3594
MV/LV Substation GL***696X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.271 | -6.3608
MV/LV Substation CO***700X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =274 kVA | --> | 0.38 | 0 | 0.037 | 0.369 | 0 |  | --> | C19 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2765 | -6.4203
MV/LV Substation MI***701X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =452 kVA | --> | 0.598 | 0 | 0.052 | 0.5 | 0 |  | --> | C15 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2821 | -6.3518
MV/LV Substation VI***708X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =285 kVA | --> | 0.38 | 0 | 0.01 | 0.388 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2865 | -6.363
MV/LV Substation PL***709X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2861 | -6.368
MV/LV Substation SO***712X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =173 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C20 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2868 | -6.3697
MV/LV Substation SA***714X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =236 kVA | --> | 0.38 | 0 | 0.049 | 0.366 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2892 | -6.4272
MV/LV Substation BE***717X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =203 kVA | --> | 0.38 | 0 | 0 | 0.406 | 0 |  | --> | C12 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2892 | -6.3716
MV/LV Substation WE***722X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =425 kVA | --> | 0.598 | 0 | 0.021 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3134 | -6.3479
MV/LV Substation WO***723X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =226 kVA | --> | 0.38 | 0 | 0.04 | 0.373 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2755 | -6.3341
MV/LV Substation SU***726X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =20 kVA | --> | 0.19 | 0 | 0.013 | 0.204 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2802 | -6.4083
MV/LV Substation BE***727X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.22 | 13.91 |  | --> | 0.38 | 0 | 0.037 | 0.376 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2932 | -6.3889
MV/LV Substation OL***730X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2489 | -6.5313
MV/LV Substation AL***734X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =474 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2845 | -6.378
MV/LV Substation CO***737X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =60 kVA | --> | 0.38 | 0 | 0.046 | 0.39 | 0 |  | --> | C17 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2766 | -6.4245
MV/LV Substation BA***738X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =361 kVA | --> | 0.38 | 0 | 0.04 | 0.356 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3105 | -6.3471
MV/LV Substation EL***741X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =91 kVA | --> | 0.19 | 0 | 0.02 | 0.19 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2669 | -6.3672
MV/LV Substation DA***742X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =309 kVA | --> | 0.38 | 0 | 0.047 | 0.357 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2732 | -6.3365
MV/LV Substation EL***744X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =128 kVA | --> | 0.19 | 0 | 0.012 | 0.191 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2712 | -6.3513
MV/LV Substation CL***745X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.258 | 13.91 |  | --> | 0.38 | 0 | 0 | 0.399 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2954 | -6.3797
MV/LV Substation UP***746X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =521 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2882 | -6.3649
MV/LV Substation BR***747X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =281 kVA | --> | 0.38 | 0 | 0 | 0.396 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2888 | -6.4082
MV/LV Substation PA***751X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =416 kVA | --> | 0.598 | 0 | 0.075 | 0.5 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3018 | -6.3672
MV/LV Substation KI***756X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =257 kVA | --> | 0.38 | 0 | 0.04 | 0.369 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3036 | -6.3744
MV/LV Substation IR***757X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =530 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2974 | -6.356
MV/LV Substation TE***758X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =399 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3077 | -6.3508
MV/LV Substation SA***759X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =492 kVA | --> | 0.598 | 0 | 0.006 | 0.5 | 0 |  | --> | C18 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2885 | -6.4318
MV/LV Substation BL***760X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =111 kVA | --> | 0.19 | 0 | 0.005 | 0.198 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2781 | -6.399
MV/LV Substation SU***765X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.076 | 13.91 |  | --> | 0.19 | 0 | 0.028 | 0.186 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2822 | -6.4092
MV/LV Substation WO***767X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =156 kVA | --> | 0.19 | 0 | 0.027 | 0.176 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2748 | -6.338
MV/LV Substation ES***768X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0.01 | 0.09 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2455 | -6.4761
MV/LV Substation TU***769X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =192 kVA | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2914 | -6.4268
MV/LV Substation VI***771X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =563 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2899 | -6.4242
MV/LV Substation OL***772X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =207 kVA | --> | 0.38 | 0 | 0.038 | 0.377 | 0 |  | --> | C16 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2806 | -6.3582
MV/LV Substation LA***774X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 |  | --> | 0.38 | 0 | 0.219 | 0.293 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2792 | -6.4212
MV/LV Substation WE***777X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =334 kVA | --> | 0.38 | 0 | 0 | 0.389 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3143 | -6.349
MV/LV Substation TY***778X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =107 kVA | --> | 0.19 | 0 | 0.002 | 0.201 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3074 | -6.3726
MV/LV Substation AV***779X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =472 kVA | --> | 0.598 | 0 | 0.016 | 0.5 | 0 |  | --> | C19 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2853 | -6.3493
MV/LV Substation TY***780X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =436 kVA | --> | 0.598 | 0 | 0.068 | 0.5 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.279 | -6.3661
MV/LV Substation BA***781X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =233 kVA | --> | 0.38 | 0 | 0.035 | 0.376 | 0 |  | --> | C15 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2794 | -6.3538
MV/LV Substation LI***782X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =397 kVA | --> | 0.598 | 0 | 0.037 | 0.5 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2789 | -6.3696
MV/LV Substation BL***785X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =494 kVA | --> | 0.598 | 0 | 0.096 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3103 | -6.3509
MV/LV Substation DO***786X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =582 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.289 | -6.4304
MV/LV Substation AV***787X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =268 kVA | --> | 0.38 | 0 | 0.017 | 0.385 | 0 |  | --> | C15 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2859 | -6.3433
MV/LV Substation SU***788X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =260 kVA | --> | 0.38 | 0 | 0.033 | 0.374 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2811 | -6.3648
MV/LV Substation ST***790X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =531 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2882 | -6.3645
MV/LV Substation TH***792X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =14 kVA | --> | 0.048 | 0 | 0 | 0.052 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.273 | -6.3604
MV/LV Substation SU***793X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =342 kVA | --> | 0.38 | 0 | 0 | 0.388 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2842 | -6.4088
MV/LV Substation BR***794X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =346 kVA | --> | 0.38 | 0 | 0.015 | 0.376 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2976 | -6.3632
MV/LV Substation DU***795X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2753 | -6.357
MV/LV Substation WE***796X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =483 kVA | --> | 0.598 | 0 | 0.002 | 0.5 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.29 | -6.4385
MV/LV Substation CI***797X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =302 kVA | --> | 0.38 | 0 | 0 | 0.393 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.293 | -6.426
MV/LV Substation OA***799X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =113 kVA | --> | 0.38 | 0 | 0.077 | 0.36 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2726 | -6.3386
MV/LV Substation WO***800X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =244 kVA | --> | 0.38 | 0 | 0.049 | 0.364 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2741 | -6.3264
MV/LV Substation WA***801X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =467 kVA | --> | 0.598 | 0 | 0.055 | 0.5 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2796 | -6.3618
MV/LV Substation DU***802X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =253 kVA | --> | 0.38 | 0 | 0.049 | 0.363 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2819 | -6.3692
MV/LV Substation BR***804X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =133 kVA | --> | 0.19 | 0 | 0.002 | 0.197 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2885 | -6.4108
MV/LV Substation EL***806X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0.016 | 0.379 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2687 | -6.3677
MV/LV Substation VE***808X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =281 kVA | --> | 0.38 | 0 | 0.025 | 0.377 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.279 | -6.424
MV/LV Substation FE***810X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =278 kVA | --> | 0.38 | 0 | 0.017 | 0.384 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.273 | -6.3456
MV/LV Substation CR***811 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =412 kVA | --> | 0.598 | 0 | 0.028 | 0.5 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3258 | -6.3661
MV/LV Substation KI***811X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =311 kVA | --> | 0.38 | 0 | 0 | 0.392 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2896 | -6.332
MV/LV Substation EI***812X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =518 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2922 | -6.4312
MV/LV Substation AS***814X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =197 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2774 | -6.3275
MV/LV Substation VE***815X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =290 kVA | --> | 0.38 | 0 | 0.027 | 0.375 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2806 | -6.4242
MV/LV Substation CA***816X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =442 kVA | --> | 0.598 | 0 | 0.028 | 0.5 | 0 |  | --> | C22 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2912 | -6.3445
MV/LV Substation GL***817X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.279 | 13.91 |  | --> | 0.38 | 0 | 0.005 | 0.392 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2848 | -6.4039
MV/LV Substation CI***819X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =12 kVA | --> | 0.19 | 0 | 0 | 0.214 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2963 | -6.4174
MV/LV Substation HA***822X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =122 kVA | --> | 0.19 | 0 | 0.021 | 0.185 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2752 | -6.3978
MV/LV Substation WO***824X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =250 kVA | --> | 0.38 | 0 | 0.036 | 0.373 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2739 | -6.3232
MV/LV Substation WO***825X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =203 kVA | --> | 0.38 | 0 | 0.011 | 0.398 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2759 | -6.3298
MV/LV Substation ES***827X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =351 kVA | --> | 0.38 | 0 | 0 | 0.387 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3104 | -6.3594
MV/LV Substation CI***828X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =339 kVA | --> | 0.38 | 0 | 0 | 0.388 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2848 | -6.4414
MV/LV Substation NE***829X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =586 kVA | --> | 0.598 | 0 | 0.02 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.293 | -6.4225
MV/LV Substation KI***831 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =251 kVA | --> | 0.38 | 0 | 0.005 | 0.396 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2804 | -6.3863
MV/LV Substation KI***832 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =497 kVA | --> | 0.598 | 0 | 0.014 | 0.5 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2789 | -6.3884
MV/LV Substation MO***832X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =132 kVA | --> | 0.19 | 0 | 0.011 | 0.191 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3201 | -6.3735
MV/LV Substation KI***833X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =105 kVA | --> | 0.19 | 0 | 0.008 | 0.197 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3182 | -6.417
MV/LV Substation CI***834X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 |  | --> | 0.38 | 0 | 0.184 | 0.32 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2879 | -6.4264
MV/LV Substation FO***835X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =376 kVA | --> | 0.38 | 0 | 0.07 | 0.331 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2973 | -6.3508
MV/LV Substation AN***838X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2785 | -6.4012
MV/LV Substation BA***839X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =323 kVA | --> | 0.38 | 0 | 0 | 0.39 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2932 | -6.4431
MV/LV Substation BA***840X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =223 kVA | --> | 0.598 | 0 | 0.138 | 0.5 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2959 | -6.4414
MV/LV Substation SU***841X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =197 kVA | --> | 0.38 | 0 | 0.019 | 0.393 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2844 | -6.4108
MV/LV Substation RA***842X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2392 | -6.4477
MV/LV Substation BE***843X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =276 kVA | --> | 0.38 | 0 | 0.03 | 0.374 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2911 | -6.3278
MV/LV Substation NE***844X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =183 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3098 | -6.3773
MV/LV Substation GL***845X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =324 kVA | --> | 0.38 | 0 | 0.008 | 0.384 | 0 |  | --> | C15 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2889 | -6.3408
MV/LV Substation GL***846X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =256 kVA | --> | 0.38 | 0 | 0.008 | 0.393 | 0 |  | --> | C22 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2886 | -6.3468
MV/LV Substation AS***847X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =11 kVA | --> | 0.19 | 0 | 0 | 0.214 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2929 | -6.3559
MV/LV Substation PO***848X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =187 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2451 | -6.5495
MV/LV Substation CO***849X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =616 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2922 | -6.421
MV/LV Substation EL***850X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =295 kVA | --> | 0.38 | 0 | 0.01 | 0.387 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2679 | -6.3712
MV/LV Substation DA***851X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.19 | 0 | 0.025 | 0.185 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2726 | -6.3351
MV/LV Substation DA***852 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =294 kVA | --> | 0.38 | 0 | 0.036 | 0.368 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2746 | -6.3613
MV/LV Substation PI***853 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =375 kVA | --> | 0.38 | 0 | 0.004 | 0.38 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2746 | -6.3655
MV/LV Substation WO***853X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =137 kVA | --> | 0.19 | 0 | 0.01 | 0.191 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2739 | -6.3217
MV/LV Substation HO***854X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2642 | -6.3954
MV/LV Substation LI***855 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =291 kVA | --> | 0.38 | 0 | 0.013 | 0.385 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3276 | -6.414
MV/LV Substation LI***856 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =319 kVA | --> | 0.38 | 0 | 0.005 | 0.387 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3273 | -6.4158
MV/LV Substation ST***856X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =352 kVA | --> | 0.38 | 0 | 0 | 0.387 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2768 | -6.4016
MV/LV Substation MC***857 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =321 kVA | --> | 0.38 | 0 | 0 | 0.391 | 0 |  | --> | C14 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3155 | -6.3542
MV/LV Substation CO***857X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =215 kVA | --> | 0.38 | 0 | 0 | 0.404 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.296 | -6.4134
MV/LV Substation LO***858 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =273 kVA | --> | 0.38 | 0 | 0 | 0.397 | 0 |  | --> | C14 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2819 | -6.3771
MV/LV Substation DI***859X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =839 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2893 | -6.4243
MV/LV Substation CA***860X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =553 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.312 | -6.3471
MV/LV Substation OL***863 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =156 kVA | --> | 0.19 | 0 | 0 | 0.196 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2476 | -6.5334
MV/LV Substation KI***864 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =234 kVA | --> | 0.38 | 0 | 0.082 | 0.341 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3039 | -6.3696
MV/LV Substation CA***865 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =243 kVA | --> | 0.38 | 0 | 0.059 | 0.357 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2792 | -6.3351
MV/LV Substation M ***866X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2908 | -6.4371
MV/LV Substation ST***867 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =486 kVA | --> | 0.598 | 0 | 0.008 | 0.5 | 0 |  | --> | C22 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2972 | -6.3431
MV/LV Substation OL***867X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =287 kVA | --> | 0.38 | 0 | 0 | 0.395 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.274 | -6.3458
MV/LV Substation SP***868X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =224 kVA | --> | 0.38 | 0 | 0 | 0.391 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2943 | -6.4145
MV/LV Substation RO***869X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.298 | -6.3589
MV/LV Substation CO***870X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2858 | -6.4602
MV/LV Substation FI***871 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =410 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2807 | -6.341
MV/LV Substation BI***872 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C28 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3265 | -6.3935
MV/LV Substation TY***874 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =320 kVA | --> | 0.38 | 0 | 0 | 0.391 | 0 |  | --> | C22 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2955 | -6.3465
MV/LV Substation TY***875 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =106 kVA | --> | 0.19 | 0 | 0.01 | 0.195 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2975 | -6.3474
MV/LV Substation KI***876 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =599 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2995 | -6.3608
MV/LV Substation WO***876X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =284 kVA | --> | 0.38 | 0 | 0.044 | 0.363 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2756 | -6.3254
MV/LV Substation SA***878X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =370 kVA | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.282 | -6.4413
MV/LV Substation CA***879X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =593 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3121 | -6.3461
MV/LV Substation RO***880X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =387 kVA | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2936 | -6.4303
MV/LV Substation AR***881X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.38 | 0 | 0.038 | 0.378 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2874 | -6.4172
MV/LV Substation LI***882 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =151 kVA | --> | 0.19 | 0 | 0.002 | 0.195 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3263 | -6.416
MV/LV Substation AR***882X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =334 kVA | --> | 0.38 | 0 | 0 | 0.389 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2881 | -6.4151
MV/LV Substation CA***883X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =354 kVA | --> | 0.38 | 0 | 0.004 | 0.383 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2728 | -6.3695
MV/LV Substation DE***884X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.025 | 0.377 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2773 | -6.4095
MV/LV Substation NE***885X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =196 kVA | --> | 0.19 | 0 | 0.005 | 0.187 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2847 | -6.4714
MV/LV Substation SO***886X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2318 | -6.4495
MV/LV Substation FO***887X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.19 | 0 | 0.024 | 0.186 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2798 | -6.4706
MV/LV Substation KI***889 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =273 kVA | --> | 0.38 | 0 | 0.034 | 0.372 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2749 | -6.3595
MV/LV Substation SA***889X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =391 kVA | --> | 0.38 | 0 | 0 | 0.381 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2944 | -6.423
MV/LV Substation AM***891X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =280 kVA | --> | 0.38 | 0 | 0.049 | 0.36 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2925 | -6.4208
MV/LV Substation WH***892 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.145 | 13.91 |  | --> | 0.19 | 0 | 0.008 | 0.191 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2847 | -6.3914
MV/LV Substation BI***893 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =212 kVA | --> | 0.38 | 0 | 0.039 | 0.376 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2996 | -6.356
MV/LV Substation AL***894 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.442 | 13.91 |  | --> | 0.598 | 0 | 0.044 | 0.5 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2969 | -6.3855
MV/LV Substation ST***898 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =124 kVA | --> | 0.19 | 0 | 0.025 | 0.182 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3183 | -6.4001
MV/LV Substation CH***900X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =246 kVA | --> | 0.38 | 0 | 0.046 | 0.366 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2803 | -6.4748
MV/LV Substation KN***901 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =466 kVA | --> | 0.598 | 0 | 0.022 | 0.5 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2765 | -6.39
MV/LV Substation BR***902 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =383 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2955 | -6.3648
MV/LV Substation BR***902X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =315 kVA | --> | 0.38 | 0 | 0.021 | 0.376 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.279 | -6.4823
MV/LV Substation EL***903X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =259 kVA | --> | 0.38 | 0 | 0.03 | 0.377 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2671 | -6.3721
MV/LV Substation PA***904 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =64 kVA | --> | 0.19 | 0 | 0.036 | 0.181 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.278 | -6.3595
MV/LV Substation KI***904X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =373 kVA | --> | 0.38 | 0 | 0 | 0.384 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2767 | -6.3758
MV/LV Substation TR***905 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =131 kVA | --> | 0.19 | 0 | 0.021 | 0.184 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3008 | -6.3613
MV/LV Substation NI***905X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =488 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.293 | -6.3643
MV/LV Substation RO***906 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =12 kVA | --> | 0.095 | 0 | 0 | 0.106 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.2987 | -6.3959
MV/LV Substation AS***906X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =336 kVA | --> | 0.38 | 0 | 0 | 0.389 | 0 |  | --> | C13 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2813 | -6.4109
MV/LV Substation WE***907 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =271 kVA | --> | 0.38 | 0 | 0 | 0.397 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3242 | -6.3628
MV/LV Substation RA***907X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2423 | -6.5572
MV/LV Substation WE***908 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =260 kVA | --> | 0.38 | 0 | 0 | 0.399 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3232 | -6.3642
MV/LV Substation TH***908X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =197 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C16 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2853 | -6.3643
MV/LV Substation HE***909 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =236 kVA | --> | 0.38 | 0 | 0.018 | 0.388 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2758 | -6.3692
MV/LV Substation AL***909X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =344 kVA | --> | 0.38 | 0 | 0 | 0.388 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2962 | -6.3612
MV/LV Substation BA***910X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =382 kVA | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2781 | -6.379
MV/LV Substation ST***912 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.144 | 13.91 |  | --> | 0.19 | 0 | 0 | 0.198 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2916 | -6.3878
MV/LV Substation DI***912X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =865 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2887 | -6.4216
MV/LV Substation FI***913X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =366 kVA | --> | 0.38 | 0 | 0 | 0.385 | 0 |  | --> | C13 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2821 | -6.4103
MV/LV Substation FO***914 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =285 kVA | --> | 0.38 | 0 | 0.073 | 0.341 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3071 | -6.3618
MV/LV Substation DU***914X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =581 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2905 | -6.4221
MV/LV Substation BE***916 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0 | 0.196 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2984 | -6.3713
MV/LV Substation NE***918X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =191 kVA | --> | 0.19 | 0 | 0.03 | 0.169 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.253 | -6.5398
MV/LV Substation WE***919 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =518 kVA | --> | 0.598 | 0 | 0.05 | 0.5 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3221 | -6.3663
MV/LV Substation DI***920X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =555 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2888 | -6.4207
MV/LV Substation MI***921 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =441 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2846 | -6.3544
MV/LV Substation SO***922X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =179 kVA | --> | 0.19 | 0 | 0 | 0.193 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2282 | -6.4492
MV/LV Substation EU***923 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =414 kVA | --> | 0.598 | 0 | 0.025 | 0.5 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2947 | -6.3535
MV/LV Substation CO***923X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =164 kVA | --> | 0.19 | 0 | 0 | 0.195 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3008 | -6.3487
MV/LV Substation BR***924 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0.05 | 0.354 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2955 | -6.36
MV/LV Substation GL***926X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.367 | 13.91 |  | --> | 0.38 | 0 | 0 | 0.384 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2836 | -6.4015
MV/LV Substation ST***927 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =248 kVA | --> | 0.38 | 0 | 0.036 | 0.374 | 0 |  | --> | C16 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2828 | -6.3625
MV/LV Substation BR***927X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =696 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.29 | -6.3741
MV/LV Substation AS***928 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =241 kVA | --> | 0.38 | 0 | 0.036 | 0.374 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3084 | -6.3695
MV/LV Substation SH***928X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 13.91 |  | --> | 0.38 | 0 | 0.057 | 0.389 | 0 |  | --> | C11 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2827 | -6.3742
MV/LV Substation ST***929 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =268 kVA | --> | 0.38 | 0 | 0.02 | 0.383 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3172 | -6.4012
MV/LV Substation PA***929X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =281 kVA | --> | 0.38 | 0 | 0.02 | 0.381 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2744 | -6.3408
MV/LV Substation PE***930X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =355 kVA | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C13 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2816 | -6.4135
MV/LV Substation WH***931X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =320 kVA | --> | 0.38 | 0 | 0 | 0.391 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3082 | -6.3546
MV/LV Substation OL***932 |  | 10 kV | _ | LV | 100 kVA :Building Structure | 0.1 | --> | 0.1 | 0.053 | 13.91 |  | --> | 0.095 | 0 | 0 | 0.101 | 0 |  | --> | C11 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2832 | -6.3718
MV/LV Substation CA***932X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =241 kVA | --> | 0.38 | 0 | 0 | 0.401 | 0 |  | --> | C20 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3125 | -6.3441
MV/LV Substation MO***933 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =321 kVA | --> | 0.598 | 0 | 0.015 | 0.5 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3136 | -6.3626
MV/LV Substation WO***933X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =59 kVA | --> | 0.19 | 0 | 0.055 | 0.168 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2737 | -6.3297
MV/LV Substation DR***934 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =268 kVA | --> | 0.38 | 0 | 0 | 0.398 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2892 | -6.3965
MV/LV Substation DR***935 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =121 kVA | --> | 0.19 | 0 | 0.008 | 0.194 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.289 | -6.3942
MV/LV Substation DI***935X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =869 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2901 | -6.4213
MV/LV Substation DR***936 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =144 kVA | --> | 0.19 | 0 | 0 | 0.197 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2911 | -6.3966
MV/LV Substation KI***937 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =145 kVA | --> | 0.19 | 0 | 0 | 0.197 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2921 | -6.3948
MV/LV Substation CA***937X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =308 kVA | --> | 0.38 | 0 | 0.009 | 0.386 | 0 |  | --> | C14 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2826 | -6.4293
MV/LV Substation HE***938 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =150 kVA | --> | 0.19 | 0 | 0.006 | 0.192 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2811 | -6.383
MV/LV Substation HE***939 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.19 | 0 | 0.022 | 0.187 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2762 | -6.3691
MV/LV Substation BO***939X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =390 kVA | --> | 0.38 | 0 | 0 | 0.381 | 0 |  | --> | C15 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2861 | -6.3426
MV/LV Substation SY***940 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =281 kVA | --> | 0.38 | 0 | 0.03 | 0.374 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3055 | -6.3645
MV/LV Substation SE***940X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =327 kVA | --> | 0.38 | 0 | 0 | 0.39 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2953 | -6.3523
MV/LV Substation HA***941X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =307 kVA | --> | 0.38 | 0 | 0 | 0.392 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2755 | -6.3959
MV/LV Substation D.***942 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =480 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3246 | -6.359
MV/LV Substation QU***942X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2333 | -6.4242
MV/LV Substation WE***943 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.08 | 0.337 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3233 | -6.3659
MV/LV Substation TU***943X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =838 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2883 | -6.3694
MV/LV Substation WE***944 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =73 kVA | --> | 0.38 | 0 | 0 | 0.422 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3216 | -6.3619
MV/LV Substation CU***944X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0.006 | 0.384 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2723 | -6.3744
MV/LV Substation AS***945 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =178 kVA | --> | 0.38 | 0 | 0 | 0.409 | 0 |  | --> | C28 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3275 | -6.3927
MV/LV Substation BR***946X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =322 kVA | --> | 0.38 | 0 | 0.028 | 0.37 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.28 | -6.4813
MV/LV Substation FA***947X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =426 kVA | --> | 0.598 | 0 | 0.04 | 0.5 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3073 | -6.3501
MV/LV Substation KN***948 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0.005 | 0.387 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2776 | -6.3926
MV/LV Substation BA***948X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =987 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3059 | -6.352
MV/LV Substation OH***949X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =537 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2926 | -6.442
MV/LV Substation CA***950 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =207 kVA | --> | 0.38 | 0 | 0.002 | 0.404 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2929 | -6.3672
MV/LV Substation EL***950X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0 | 0.388 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2687 | -6.3692
MV/LV Substation CA***951 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =306 kVA | --> | 0.38 | 0 | 0.024 | 0.375 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2737 | -6.3692
MV/LV Substation CO***951X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =363 kVA | --> | 0.38 | 0 | 0.012 | 0.376 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2806 | -6.4406
MV/LV Substation RU***952X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.493 | 13.91 |  | --> | 0.598 | 0 | 0.002 | 0.5 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2824 | -6.4042
MV/LV Substation CL***953 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =51 kVA | --> | 0.19 | 0 | 0.018 | 0.196 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.324 | -6.4034
MV/LV Substation RU***953X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.287 | 13.91 |  | --> | 0.38 | 0 | 0.011 | 0.387 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.283 | -6.4066
MV/LV Substation DU***954 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =102 kVA | --> | 0.19 | 0 | 0.031 | 0.18 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3094 | -6.3699
MV/LV Substation RU***954X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.302 | 13.91 |  | --> | 0.38 | 0 | 0.019 | 0.379 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2848 | -6.406
MV/LV Substation DU***955 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =239 kVA | --> | 0.38 | 0 | 0.031 | 0.378 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3101 | -6.3664
MV/LV Substation MO***955X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0 | 0.388 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2779 | -6.401
MV/LV Substation DR***956 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.285 | 13.91 |  | --> | 0.38 | 0 | 0 | 0.395 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2817 | -6.3957
MV/LV Substation JO***957 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =329 kVA | --> | 0.38 | 0 | 0 | 0.39 | 0 |  | --> | C14 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3191 | -6.36
MV/LV Substation ST***958X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =172 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C16 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2828 | -6.3604
MV/LV Substation HU***960X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =392 kVA | --> | 0.598 | 0 | 0.036 | 0.5 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2715 | -6.3311
MV/LV Substation HU***961X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0 | 0.196 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2719 | -6.3336
MV/LV Substation HU***962X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =374 kVA | --> | 0.38 | 0 | 0 | 0.384 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2704 | -6.3322
MV/LV Substation CO***963X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =738 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2979 | -6.3737
MV/LV Substation CI***964X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =736 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2859 | -6.4506
MV/LV Substation ES***965X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2894 | -6.3357
MV/LV Substation CA***966X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =173 kVA | --> | 0.38 | 0 | 0.066 | 0.361 | 0 |  | --> | C14 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2822 | -6.4312
MV/LV Substation CA***967X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =772 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.284 | -6.4256
MV/LV Substation TO***968X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =186 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2462 | -6.5392
MV/LV Substation CA***969X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =397 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C14 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2818 | -6.4273
MV/LV Substation ES***970X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =444 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2886 | -6.3585
MV/LV Substation GR***971X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =928 kVA | --> | 0.95 | 0 | 0.004 | 0.5 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2885 | -6.3574
MV/LV Substation MA***972X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =389 kVA | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | C13 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2809 | -6.4135
MV/LV Substation P.***973 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C11 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2915 | -6.3681
MV/LV Substation TA***974 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =247 kVA | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.288 | -6.363
MV/LV Substation MA***974X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.25 | 13.91 |  | --> | 0.598 | 0 | 0.018 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2718 | -6.3692
MV/LV Substation MA***975X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2707 | -6.3689
MV/LV Substation WA***976 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =291 kVA | --> | 0.38 | 0 | 0.017 | 0.382 | 0 |  | --> | C16 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2829 | -6.3646
MV/LV Substation BE***976X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =472 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2931 | -6.373
MV/LV Substation CO***977X |  | 10 kV | _ | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =824 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2851 | -6.3761
MV/LV Substation BA***978X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =548 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3057 | -6.3493
MV/LV Substation KI***979X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.346 | 13.91 |  | --> | 0.38 | 0 | 0 | 0.387 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2693 | -6.3707
MV/LV Substation GL***981 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =356 kVA | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2959 | -6.3713
MV/LV Substation AI***981X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =491 kVA | --> | 0.598 | 0 | 0.085 | 0.5 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2953 | -6.3587
MV/LV Substation JO***982 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =879 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2966 | -6.3728
MV/LV Substation KI***982X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =381 kVA | --> | 0.38 | 0 | 0 | 0.383 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2788 | -6.3438
MV/LV Substation IM***983 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =141 kVA | --> | 0.19 | 0 | 0.05 | 0.161 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2927 | -6.3736
MV/LV Substation GR***983X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =496 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2931 | -6.3549
MV/LV Substation WE***984X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =273 kVA | --> | 0.38 | 0 | 0 | 0.397 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.291 | -6.3573
MV/LV Substation D.***985 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =346 kVA | --> | 0.38 | 0 | 0 | 0.387 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2955 | -6.3754
MV/LV Substation CO***986 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.495 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2954 | -6.3789
MV/LV Substation CO***986X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2477 | -6.5275
MV/LV Substation PR***987 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =490 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2947 | -6.3775
MV/LV Substation GA***988X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =359 kVA | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2833 | -6.4407
MV/LV Substation ST***989X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =358 kVA | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2798 | -6.4683
MV/LV Substation TR***991 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.344 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2985 | -6.3754
MV/LV Substation CA***992X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0.008 | 0.383 | 0 |  | --> | C14 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2827 | -6.4268
MV/LV Substation GA***995 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =79 kVA | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3063 | -6.3811
MV/LV Substation CA***995X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =554 kVA | --> | 0.598 | 0 | 0.006 | 0.5 | 0 |  | --> | C20 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3134 | -6.3422
MV/LV Substation BR***997 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =310 kVA | --> | 0.38 | 0 | 0 | 0.392 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2947 | -6.3636
MV/LV Substation TH***998X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =191 kVA | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3232 | -6.352
MV/LV Substation AU***006X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.398 | 0.45 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C14 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2664 | -9.5611
MV/LV Substation TR***012 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.152 | 0.45 |  | --> | 0.19 | 0 | 0 | 0.196 | 0 |  | --> | C14 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.263 | -9.5653
MV/LV Substation IN***012X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.013 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.052 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0606 | -9.521
MV/LV Substation IN***016X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.45 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0903 | -9.5795
MV/LV Substation CO***022X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 0.45 |  | --> | 0.095 | 0 | 0.01 | 0.088 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0937 | -9.5847
MV/LV Substation NE***023X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1002 | -9.5771
MV/LV Substation FA***024X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.191 | 0.45 |  | --> | 0.19 | 0 | 0.07 | 0.139 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0882 | -9.5828
MV/LV Substation CA***025 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.36 | 0.45 |  | --> | 0.38 | 0 | 0.005 | 0.382 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2646 | -9.6012
MV/LV Substation GE***025X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 0.45 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0877 | -9.5828
MV/LV Substation NE***034X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0893 | -9.5929
MV/LV Substation CR***035 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3168 | -9.8308
MV/LV Substation SR***037 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.271 | -9.5834
MV/LV Substation RO***047 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 1.47 |  | --> | 0.095 | 0 | 0.005 | 0.093 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3698 | -9.6265
MV/LV Substation CR***047X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.174 | 0.45 |  | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0653 | -9.5412
MV/LV Substation N.***049 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 0.45 |  | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2612 | -9.6102
MV/LV Substation KI***054 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 0.45 |  | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1034 | -9.6559
MV/LV Substation OS***057X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.07 | 0.45 |  | --> | 0.095 | 0 | 0.013 | 0.089 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0632 | -9.5236
MV/LV Substation BA***059X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 0.45 |  | --> | 0.048 | 0 | 0.006 | 0.046 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.067 | -9.5279
MV/LV Substation KI***060 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1052 | -9.6642
MV/LV Substation BA***061X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.45 |  | --> | 0.048 | 0 | 0.002 | 0.047 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0668 | -9.5321
MV/LV Substation TI***064X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.001 | 0.45 |  | --> | 0.048 | 0 | 0.004 | 0.051 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0627 | -9.5305
MV/LV Substation IN***066X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 0.45 |  | --> | 0.048 | 0 | 0.014 | 0.039 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0604 | -9.5277
MV/LV Substation KI***069 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.45 |  | --> | 0.19 | 0 | 0.003 | 0.188 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1174 | -9.6831
MV/LV Substation WA***070 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 0.45 |  | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1146 | -9.6894
MV/LV Substation DU***072 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.149 | 0.45 |  | --> | 0.19 | 0 | 0 | 0.197 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.118 | -9.6752
MV/LV Substation KI***073 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 0.45 |  | --> | 0.048 | 0 | 0.009 | 0.042 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1188 | -9.6728
MV/LV Substation KI***076 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.151 | 0.45 |  | --> | 0.19 | 0 | 0.023 | 0.18 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1217 | -9.67
MV/LV Substation VO***077 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.162 | 0.45 |  | --> | 0.19 | 0 | 0.029 | 0.174 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1256 | -9.672
MV/LV Substation IN***077X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 0.45 |  | --> | 0.048 | 0 | 0.016 | 0.037 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.063 | -9.512
MV/LV Substation BA***081 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.073 | 0.45 |  | --> | 0.095 | 0 | 0.002 | 0.097 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1249 | -9.663
MV/LV Substation PI***084 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.45 |  | --> | 0.048 | 0 | 0.005 | 0.044 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1228 | -9.6664
MV/LV Substation PI***085 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.054 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1205 | -9.6676
MV/LV Substation PO***086 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.164 | 0.45 |  | --> | 0.19 | 0 | 0 | 0.195 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1201 | -9.6699
MV/LV Substation HA***088X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 0.45 |  | --> | 0.048 | 0 | 0.013 | 0.04 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.087 | -9.5879
MV/LV Substation OG***092 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1282 | -9.6882
MV/LV Substation CU***094X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.177 | 0.45 |  | --> | 0.19 | 0 | 0.005 | 0.19 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.265 | -9.6078
MV/LV Substation SI***098X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.47 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3576 | -9.7037
MV/LV Substation KI***108 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1335 | -9.7535
MV/LV Substation KI***110 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 0.45 |  | --> | 0.095 | 0 | 0.01 | 0.089 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1305 | -9.7568
MV/LV Substation MA***111X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 0.45 |  | --> | 0.095 | 0 | 0.02 | 0.081 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1345 | -9.6962
MV/LV Substation SR***116 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.45 |  | --> | 0.048 | 0 | 0.008 | 0.042 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1442 | -9.7779
MV/LV Substation LY***116X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3228 | -9.8251
MV/LV Substation OD***127X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.155 | 0.45 |  | --> | 0.19 | 0 | 0.004 | 0.193 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2613 | -9.6047
MV/LV Substation UD***128X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.372 | 1.47 |  | --> | 0.38 | 0 | 0.006 | 0.379 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3213 | -9.8106
MV/LV Substation CO***146X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0646 | -9.5161
MV/LV Substation EA***147X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.45 |  | --> | 0.048 | 0 | 0.005 | 0.044 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0996 | -9.6546
MV/LV Substation SC***170X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.387 | 0.45 |  | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2621 | -9.5986
MV/LV Substation EL***201 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.446 | 0.45 | Constrained, otherwise capacity available =517 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2902 | -9.5508
MV/LV Substation DE***202 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3907 | -9.6673
MV/LV Substation PR***206 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.386 | 0.45 |  | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | C14 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2653 | -9.5658
MV/LV Substation RE***208X |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.183 | 0.45 |  | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1276 | -9.6868
MV/LV Substation AR***226 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.008 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.053 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2895 | -9.5545
MV/LV Substation L ***228X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.191 | 1.47 |  | --> | 0.19 | 0 | 0.03 | 0.169 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.2429 | -9.7307
MV/LV Substation AD***235 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.388 | 0.45 |  | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2899 | -9.5515
MV/LV Substation FL***235X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3536 | -9.7045
MV/LV Substation CA***246X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.169 | 1.47 |  | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3248 | -9.8396
MV/LV Substation CA***249X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.077 | 1.47 |  | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3245 | -9.8174
MV/LV Substation FO***254X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.47 |  | --> | 0.048 | 0 | 0.006 | 0.043 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.2453 | -9.7232
MV/LV Substation GL***282X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.4215 | -9.4017
MV/LV Substation I ***302X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 0.45 |  | --> | 0.095 | 0 | 0.005 | 0.092 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0863 | -9.5829
MV/LV Substation CA***314 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 0.45 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2581 | -9.6027
MV/LV Substation LE***322 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.76 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C19 ex RECESS | Recess [T41] | SCREEB |  | 53.369 | -9.8622
MV/LV Substation PH***325 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 2.76 |  | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | C19 ex RECESS | Recess [T41] | SCREEB |  | 53.3267 | -9.9044
MV/LV Substation BR***325X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.376 | 1.47 |  | --> | 0.38 | 0 | 0 | 0.383 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3249 | -9.8377
MV/LV Substation BH***327X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.446 | 0.45 | Constrained, otherwise capacity available =620 kVA | --> | 0.598 | 0 | 0.002 | 0.5 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2627 | -9.5986
MV/LV Substation OC***336X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2881 | -9.5658
MV/LV Substation GA***350X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 1.47 |  | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.2422 | -9.7351
MV/LV Substation SC***362 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.37 | 1.47 |  | --> | 0.38 | 0 | 0 | 0.384 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3842 | -9.5552
MV/LV Substation DE***363 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.47 |  | --> | 0.048 | 0 | 0.005 | 0.044 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3893 | -9.5527
MV/LV Substation LE***368X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 1.47 |  | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.2788 | -9.6592
MV/LV Substation AR***377X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 1.47 |  | --> | 0.048 | 0 | 0.006 | 0.045 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3059 | -9.7744
MV/LV Substation KI***378 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.019 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.052 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3225 | -9.7364
MV/LV Substation NA***391X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.183 | 0.45 |  | --> | 0.19 | 0 | 0.005 | 0.189 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2654 | -9.6019
MV/LV Substation SL***393X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.197 | 0.45 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2647 | -9.6055
MV/LV Substation CA***399 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.446 | 0.45 | Constrained, otherwise capacity available =620 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2636 | -9.6024
MV/LV Substation GL***401 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3814 | -9.5845
MV/LV Substation CR***4016 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1449 | -9.7874
MV/LV Substation DR***4017 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.2367 | -9.6677
MV/LV Substation SR***402X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.366 | 0.45 |  | --> | 0.38 | 0 | 0.025 | 0.366 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2627 | -9.6001
MV/LV Substation CN***404 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.064 | 1.47 |  | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.4086 | -9.5453
MV/LV Substation CO***4048 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3333 | -9.7258
MV/LV Substation CR***406 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.163 | 1.47 |  | --> | 0.19 | 0 | 0.049 | 0.159 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.4581 | -9.5386
MV/LV Substation PE***4062 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3888 | -9.6186
MV/LV Substation RO***4093 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.195 | 0.45 |  | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | C14 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2685 | -9.5592
MV/LV Substation UD***4131 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 0.45 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C12 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2909 | -9.5511
MV/LV Substation SR***416X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.446 | 0.45 | Constrained, otherwise capacity available =608 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.262 | -9.6031
MV/LV Substation CU***430 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.185 | 0.45 |  | --> | 0.19 | 0 | 0.006 | 0.188 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2622 | -9.612
MV/LV Substation GA***447 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1.47 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3602 | -9.6235
MV/LV Substation GO***461 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.129 | 1.47 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3879 | -9.6127
MV/LV Substation AR***482 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.255 | 1.47 |  | --> | 0.38 | 0 | 0 | 0.399 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3221 | -9.7345
MV/LV Substation CL***501 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.47 |  | --> | 0.048 | 0 | 0.005 | 0.045 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3233 | -9.8178
MV/LV Substation MO***504 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 1.47 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.312 | -9.8314
MV/LV Substation OS***513 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3265 | -9.8392
MV/LV Substation MO***536 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 2.76 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C19 ex RECESS | Recess [T41] | SCREEB |  | 53.3164 | -9.8664
MV/LV Substation CA***556 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.45 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2793 | -9.5333
MV/LV Substation CO***557 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.173 | 0.45 |  | --> | 0.19 | 0 | 0.01 | 0.186 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2884 | -9.5502
MV/LV Substation CA***560 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.051 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3238 | -9.8374
MV/LV Substation CA***561 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3233 | -9.8287
MV/LV Substation CA***568 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.07 | 0.45 |  | --> | 0.095 | 0 | 0 | 0.099 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.289 | -9.552
MV/LV Substation GA***575 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 0.45 |  | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2724 | -9.5835
MV/LV Substation OB***580 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.147 | 0.45 |  | --> | 0.19 | 0 | 0 | 0.197 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2654 | -9.5936
MV/LV Substation CE***582 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.276 | 0.45 |  | --> | 0.38 | 0 | 0.003 | 0.394 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2632 | -9.599
MV/LV Substation OS***592 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.169 | 0.45 |  | --> | 0.19 | 0 | 0.006 | 0.19 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2652 | -9.6036
MV/LV Substation GA***603 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.446 | 0.45 | Constrained, otherwise capacity available =576 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2596 | -9.6041
MV/LV Substation MO***613 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.45 |  | --> | 0.048 | 0 | 0.005 | 0.045 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2596 | -9.6221
MV/LV Substation CL***614 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.2923 | -9.5603
MV/LV Substation BE***628 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 1.47 |  | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3146 | -9.616
MV/LV Substation AN***631 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3106 | -9.6282
MV/LV Substation LE***636 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.141 | 1.47 |  | --> | 0.19 | 0 | 0 | 0.198 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.2894 | -9.6557
MV/LV Substation LE***637 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.051 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.2893 | -9.665
MV/LV Substation CO***675 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3228 | -9.8133
MV/LV Substation SE***692 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.299 | 1.47 |  | --> | 0.38 | 0 | 0 | 0.394 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3291 | -9.7333
MV/LV Substation ST***694 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2589 | -9.6065
MV/LV Substation MU***695 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.362 | 0.45 |  | --> | 0.38 | 0 | 0 | 0.385 | 0 |  | --> | C12 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2921 | -9.551
MV/LV Substation TI***701 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.298 | 1.47 |  | --> | 0.38 | 0 | 0 | 0.394 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.2747 | -9.6618
MV/LV Substation TI***708 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 1.47 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.2666 | -9.6656
MV/LV Substation CI***863 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.47 |  | --> | 0.048 | 0 | 0.006 | 0.044 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3197 | -9.7348
MV/LV Substation KI***868 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.175 | 1.47 |  | --> | 0.19 | 0 | 0 | 0.193 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3257 | -9.7675
MV/LV Substation BA***914 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.45 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C14 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2567 | -9.5336
MV/LV Substation AR***934 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.446 | 0.45 | Constrained, otherwise capacity available =576 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2916 | -9.5518
MV/LV Substation B ***935 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.183 | 1.47 |  | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.2476 | -9.7384
MV/LV Substation DR***936 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 1.47 |  | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.2441 | -9.6738
MV/LV Substation EA***952 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 0.45 |  | --> | 0.048 | 0 | 0.03 | 0.028 | 0 |  | --> | C14 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2725 | -9.5396
MV/LV Substation LE***953 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.172 | 0.45 |  | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C14 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2739 | -9.5428
MV/LV Substation RO***955 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 0.45 |  | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C14 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2712 | -9.5467
MV/LV Substation EI***957 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.393 | 0.45 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2677 | -9.5562
MV/LV Substation IC***960 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.352 | 0.45 |  | --> | 0.38 | 0 | 0 | 0.387 | 0 |  | --> | C14 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2674 | -9.5625
MV/LV Substation LE***978 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.47 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3094 | -9.634
MV/LV Substation I.***981 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.191 | 1.47 |  | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3493 | -9.6225
MV/LV Substation CO***991 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 1.47 |  | --> | 0.048 | 0 | 0.005 | 0.045 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3473 | -9.6193
MV/LV Substation MA***002 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =203 kVA | --> | 0.38 | 0 | 0.018 | 0.393 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7644 | -8.7664
MV/LV Substation KN***003 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0 | 0.198 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7645 | -8.7634
MV/LV Substation ST***004 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.19 | 0 | 0.015 | 0.193 | 0 |  | --> | C16 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7609 | -8.759
MV/LV Substation CO***005 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =251 kVA | --> | 0.38 | 0 | 0.003 | 0.398 | 0 |  | --> | C16 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7612 | -8.7643
MV/LV Substation CL***006 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =143 kVA | --> | 0.19 | 0 | 0.045 | 0.164 | 0 |  | --> | C16 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7606 | -8.7682
MV/LV Substation CL***007 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =404 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7628 | -8.766
MV/LV Substation HA***008 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.19 | 0 | 0.014 | 0.193 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7643 | -8.7729
MV/LV Substation KN***009 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7643 | -8.7927
MV/LV Substation BL***011 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =195 kVA | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7678 | -8.7788
MV/LV Substation MI***013 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =61 kVA | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7601 | -8.7706
MV/LV Substation HA***017 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =74 kVA | --> | 0.095 | 0 | 0 | 0.099 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7631 | -8.7721
MV/LV Substation AG***061X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.19 | 0 | 0.005 | 0.191 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.827 | -8.8193
MV/LV Substation CA***071X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.8131 | -8.8013
MV/LV Substation EN***086X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =54 kVA | --> | 0.095 | 0 | 0 | 0.101 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.797 | -8.7693
MV/LV Substation TO***088X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.8099 | -8.7681
MV/LV Substation CL***131X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.6797 | -8.7438
MV/LV Substation WA***148X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0.006 | 0.094 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7662 | -8.7671
MV/LV Substation SE***152X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =67 kVA | --> | 0.095 | 0 | 0 | 0.099 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7575 | -8.7648
MV/LV Substation CA***169X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =167 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.8143 | -8.8029
MV/LV Substation CO***171X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7598 | -8.719
MV/LV Substation BR***181X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =360 kVA | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C16 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7611 | -8.7665
MV/LV Substation BA***188X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7429 | -8.6334
MV/LV Substation CA***192X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7581 | -8.7346
MV/LV Substation CO***214X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7201 | -8.7676
MV/LV Substation BA***221X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7439 | -8.6318
MV/LV Substation CH***252X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7621 | -8.7558
MV/LV Substation BA***260X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =19 kVA | --> | 0.048 | 0 | 0.005 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7448 | -8.6291
MV/LV Substation FA***261X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7465 | -8.6266
MV/LV Substation BE***266X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7567 | -8.8506
MV/LV Substation BE***267X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.767 | -8.8506
MV/LV Substation WE***270X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7502 | -8.7714
MV/LV Substation BA***277X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7411 | -8.633
MV/LV Substation HA***278X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.759 | -8.7823
MV/LV Substation CO***289X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.8015 | -8.7709
MV/LV Substation EN***293X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =13 kVA | --> | 0.048 | 0 | 0 | 0.052 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7614 | -8.7698
MV/LV Substation GA***295X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.8042 | -8.8077
MV/LV Substation HA***304X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0.011 | 0.188 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7622 | -8.7787
MV/LV Substation FA***325X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =20 kVA | --> | 0.048 | 0 | 0 | 0.051 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7596 | -8.7726
MV/LV Substation LI***327X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =194 kVA | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7573 | -8.774
MV/LV Substation DO***328X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7677 | -8.7701
MV/LV Substation RY***334X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.19 | 0 | 0 | 0.204 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7627 | -8.7682
MV/LV Substation CO***339X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =501 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.8023 | -8.7716
MV/LV Substation GO***340X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7645 | -8.7963
MV/LV Substation BR***352X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =199 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | E17 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7689 | -8.8755
MV/LV Substation ES***355X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =153 kVA | --> | 0.19 | 0 | 0.017 | 0.184 | 0 |  | --> | C16 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7599 | -8.7559
MV/LV Substation MA***358X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7643 | -8.7787
MV/LV Substation HA***361X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =168 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7634 | -8.7748
MV/LV Substation RU***362X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7693 | -8.7747
MV/LV Substation WE***387X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =170 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.6907 | -8.7551
MV/LV Substation TR***4002 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7405 | -8.6281
MV/LV Substation CA***4007 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7967 | -8.79
MV/LV Substation CO***4025 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =291 kVA | --> | 0.38 | 0 | 0.316 | 0.156 | 0 |  | --> | E17 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7749 | -8.854
MV/LV Substation JO***4032 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7665 | -8.8285
MV/LV Substation TH***403X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =133 kVA | --> | 0.19 | 0 | 0 | 0.199 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7615 | -8.7754
MV/LV Substation CH***4043 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =145 kVA | --> | 0.19 | 0 | 0.006 | 0.193 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7648 | -8.7584
MV/LV Substation KI***4044 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =190 kVA | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7745 | -8.7651
MV/LV Substation BE***4045 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7668 | -8.8459
MV/LV Substation ME***4048 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.6843 | -8.7051
MV/LV Substation EI***4063 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7564 | -8.767
MV/LV Substation LE***407X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7439 | -8.7518
MV/LV Substation MO***4090 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7073 | -8.6688
MV/LV Substation B ***4094 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7589 | -8.773
MV/LV Substation SR***409X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =68 kVA | --> | 0.095 | 0 | 0 | 0.099 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7444 | -8.6394
MV/LV Substation MA***4123 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7746 | -8.7629
MV/LV Substation AL***4134 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =358 kVA | --> | 0.38 | 0 | 0 | 0.386 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7636 | -8.7703
MV/LV Substation CA***4137 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7653 | -8.7659
MV/LV Substation TO***4148 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7657 | -8.7738
MV/LV Substation BA***4155 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7431 | -8.6372
MV/LV Substation DE***420X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7558 | -8.7772
MV/LV Substation SP***424X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7876 | -8.7531
MV/LV Substation CO***425X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7416 | -8.6268
MV/LV Substation BR***426X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =27 kVA | --> | 0.048 | 0 | 0.016 | 0.039 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7643 | -8.7947
MV/LV Substation CL***431 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.095 | 0 | 0.014 | 0.092 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.6866 | -8.752
MV/LV Substation TH***432X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.19 | 0 | 0.038 | 0.168 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7598 | -8.775
MV/LV Substation CN***447X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.6847 | -8.7476
MV/LV Substation BL***458 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7634 | -8.6428
MV/LV Substation CL***481 |  | 20 kV | _ | LV | 150 kVA :Pole Substation | 0.15 | --> | 0.15 | 0 | 0 | Constrained, otherwise capacity available =150 kVA | --> | 0.142 | 0 | 0 | 0.143 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.737 | -8.6434
MV/LV Substation CH***483X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7604 | -8.7201
MV/LV Substation CR***500X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7268 | -8.5731
MV/LV Substation CA***505X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.8459 | -8.7999
MV/LV Substation CA***513 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0 | 0.196 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7417 | -8.6307
MV/LV Substation BA***573 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =146 kVA | --> | 0.19 | 0 | 0.008 | 0.191 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.743 | -8.6358
MV/LV Substation AB***632 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0.018 | 0.083 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7584 | -8.7602
MV/LV Substation DR***634 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7525 | -8.7662
MV/LV Substation NO***640 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7736 | -8.7625
MV/LV Substation CO***641 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7577 | -8.7734
MV/LV Substation CO***720 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7172 | -8.6464
MV/LV Substation JE***728 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0.005 | 0.046 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7644 | -8.7829
MV/LV Substation TU***730 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7031 | -8.7898
MV/LV Substation CO***731 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =26 kVA | --> | 0.095 | 0 | 0.005 | 0.101 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7667 | -8.7807
MV/LV Substation DE***743 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =21 kVA | --> | 0.048 | 0 | 0 | 0.051 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.76 | -8.75
MV/LV Substation PH***786 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7561 | -8.7651
MV/LV Substation BE***799 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E17 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.762 | -8.836
MV/LV Substation SP***800 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7887 | -8.7536
MV/LV Substation RE***807 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7795 | -8.8388
MV/LV Substation AD***810 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.743 | -8.6346
MV/LV Substation LA***817 |  | 20 kV | _ | LV | 150 kVA :Pole Substation | 0.15 | --> | 0.15 | 0 | 0 | Constrained, otherwise capacity available =145 kVA | --> | 0.142 | 0 | 0 | 0.143 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.6982 | -8.7622
MV/LV Substation GO***818 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0.005 | 0.045 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.6958 | -8.7552
MV/LV Substation I ***839 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =124 kVA | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7664 | -8.7784
MV/LV Substation GR***844 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.005 | 0.045 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7344 | -8.7595
MV/LV Substation PO***855 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7666 | -8.762
MV/LV Substation BR***857 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0.04 | 0.02 | 0 |  | --> | E17 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7651 | -8.8522
MV/LV Substation CR***882 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7241 | -8.5578
MV/LV Substation RI***889 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =73 kVA | --> | 0.095 | 0 | 0.005 | 0.095 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.6868 | -8.7549
MV/LV Substation ER***918 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7566 | -8.776
MV/LV Substation AB***923 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7543 | -8.7635
MV/LV Substation C/***928 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.6993 | -8.7592
MV/LV Substation BA***931 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =368 kVA | --> | 0.38 | 0 | 0 | 0.384 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7455 | -8.6419
MV/LV Substation GA***979 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.01 | 0.041 | 0 |  | --> | E18 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.6346 | -8.8236
MV/LV Substation KN***982 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7677 | -8.8275
MV/LV Substation HA***990 |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =979 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.8433 | -8.7932
MV/LV Substation AN***004Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =216 kVA | --> | 0.38 | 0 | 0.004 | 0.401 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9458 | -10.2292
MV/LV Substation GL***006Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =79 kVA | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0581 | -9.9351
MV/LV Substation AN***007Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9204 | -10.2954
MV/LV Substation SP***009Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9531 | -10.231
MV/LV Substation CH***015Y |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =570 kVA | --> | 0.598 | 0 | 0.004 | 0.5 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9478 | -10.2247
MV/LV Substation GL***020Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =87 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0643 | -9.9512
MV/LV Substation AP***027Y |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =538 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.948 | -10.2261
MV/LV Substation GL***030Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0525 | -9.9431
MV/LV Substation GA***037Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =190 kVA | --> | 0.19 | 0 | 0.007 | 0.186 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9349 | -10.237
MV/LV Substation CA***039Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8317 | -10.1728
MV/LV Substation BA***040Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8143 | -10.1693
MV/LV Substation AR***047Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9088 | -10.2688
MV/LV Substation AT***058Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 0.76 |  | --> | 0.095 | 0 | 0.003 | 0.094 | 0 |  | --> | E19 ex KENMARE | Kenmare [T421] | KNOCKEARAGH |  | 51.8373 | -9.9072
MV/LV Substation SL***062Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =150 kVA | --> | 0.19 | 0 | 0 | 0.197 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9252 | -10.3427
MV/LV Substation SN***064Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.76 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E19 ex KENMARE | Kenmare [T421] | KNOCKEARAGH |  | 51.8399 | -9.9087
MV/LV Substation GL***065 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7593 | -10.0918
MV/LV Substation AT***067Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.76 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E19 ex KENMARE | Kenmare [T421] | KNOCKEARAGH |  | 51.8364 | -9.9084
MV/LV Substation AG***076Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8878 | -10.2159
MV/LV Substation DO***092Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8797 | -10.372
MV/LV Substation LU***100Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0.013 | 0.184 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7795 | -10.0325
MV/LV Substation SN***104Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 0.76 |  | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E19 ex KENMARE | Kenmare [T421] | KNOCKEARAGH |  | 51.8343 | -9.9068
MV/LV Substation FE***108Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8665 | -10.2536
MV/LV Substation QU***111Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8921 | -10.0662
MV/LV Substation SU***118 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.862 | -10.2824
MV/LV Substation GO***119 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =92 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0513 | -9.9444
MV/LV Substation CR***124 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.02 | 0.034 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.1043 | -9.898
MV/LV Substation GA***155 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9343 | -10.2405
MV/LV Substation CA***157 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0.004 | 0.19 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9507 | -10.2086
MV/LV Substation BA***175 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8161 | -10.1616
MV/LV Substation VA***178 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.19 | 0 | 0 | 0.195 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8856 | -10.3632
MV/LV Substation CR***198 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.005 | 0.045 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.1253 | -9.8964
MV/LV Substation BA***212 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9539 | -10.1783
MV/LV Substation GL***243 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7582 | -10.0941
MV/LV Substation DU***263 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.095 | 0 | 0 | 0.102 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8339 | -10.2635
MV/LV Substation BA***273 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E12 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.073 | -9.8824
MV/LV Substation VA***278 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9131 | -10.294
MV/LV Substation WA***287 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.19 | 0 | 0.011 | 0.195 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8287 | -10.1715
MV/LV Substation CR***288 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.1374 | -9.8994
MV/LV Substation LA***291 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =16 kVA | --> | 0.048 | 0 | 0.005 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8744 | -10.3514
MV/LV Substation AN***293 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8546 | -10.2614
MV/LV Substation GL***302 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0566 | -9.9475
MV/LV Substation DO***304 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0.006 | 0.092 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0836 | -9.9219
MV/LV Substation AG***311 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8381 | -10.329
MV/LV Substation KN***333 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8892 | -10.3165
MV/LV Substation RE***336 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =153 kVA | --> | 0.19 | 0 | 0.009 | 0.19 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.949 | -10.2198
MV/LV Substation RA***357 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.758 | -10.0971
MV/LV Substation DE***360 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7791 | -10.0017
MV/LV Substation RE***362 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9317 | -10.2514
MV/LV Substation TU***4003 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8777 | -10.1914
MV/LV Substation BU***4017 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9895 | -10.1151
MV/LV Substation MA***4028 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =90 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9521 | -10.2161
MV/LV Substation WA***403 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.19 | 0 | 0.03 | 0.181 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8272 | -10.1705
MV/LV Substation RE***4030 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9516 | -10.2154
MV/LV Substation SC***4035 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8603 | -10.1587
MV/LV Substation FE***4036 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9389 | -10.2371
MV/LV Substation CA***404 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =517 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8315 | -10.1712
MV/LV Substation FA***4045 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0578 | -9.9574
MV/LV Substation WV***4066 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8282 | -10.1661
MV/LV Substation CU***4067 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =65 kVA | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8155 | -10.1561
MV/LV Substation SP***407 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.01 | 0.042 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8363 | -10.1708
MV/LV Substation AR***4078 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.76 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E19 ex KENMARE | Kenmare [T421] | KNOCKEARAGH |  | 51.8035 | -9.9843
MV/LV Substation DE***4080 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =25 kVA | --> | 0.048 | 0 | 0 | 0.051 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7621 | -10.1308
MV/LV Substation CR***4087 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0.006 | 0.043 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.127 | -9.8964
MV/LV Substation CL***4090 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8535 | -10.253
MV/LV Substation RE***4094 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8457 | -10.2367
MV/LV Substation LI***4095 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9901 | -10.1239
MV/LV Substation ST***410 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =61 kVA | --> | 0.095 | 0 | 0.006 | 0.096 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8507 | -10.1698
MV/LV Substation IR***4102 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =388 kVA | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0152 | -10.0142
MV/LV Substation HO***4103 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0 | 0.391 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.819 | -10.1695
MV/LV Substation HO***4105 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =398 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8199 | -10.1669
MV/LV Substation LO***4109 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =577 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8213 | -10.1655
MV/LV Substation ST***4116 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0966 | -9.9022
MV/LV Substation AR***4118 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9111 | -10.2667
MV/LV Substation ST***4119 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8472 | -10.3347
MV/LV Substation CR***4126 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.1318 | -9.8961
MV/LV Substation TR***4131 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0.01 | 0.041 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0805 | -9.9251
MV/LV Substation FO***4142 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7606 | -10.0962
MV/LV Substation AL***4144 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9457 | -10.2294
MV/LV Substation BR***4156 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8382 | -10.2619
MV/LV Substation KE***4174 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0245 | -10.1002
MV/LV Substation OH***4175 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9212 | -10.2401
MV/LV Substation GL***4192 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7594 | -10.0844
MV/LV Substation CA***4233 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.016 | -10.0995
MV/LV Substation MA***4236 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9533 | -10.2272
MV/LV Substation CA***431 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9113 | -10.2332
MV/LV Substation GO***432X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0459 | -9.9503
MV/LV Substation EM***436X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =104 kVA | --> | 0.19 | 0 | 0.004 | 0.2 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0554 | -9.9422
MV/LV Substation RE***442 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.929 | -10.2766
MV/LV Substation RO***443X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =66 kVA | --> | 0.095 | 0 | 0.006 | 0.095 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0529 | -9.9753
MV/LV Substation GL***444X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =156 kVA | --> | 0.19 | 0 | 0.015 | 0.185 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0585 | -9.9403
MV/LV Substation GL***445X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =54 kVA | --> | 0.095 | 0 | 0 | 0.101 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0589 | -9.9332
MV/LV Substation OB***446 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =87 kVA | --> | 0.19 | 0 | 0 | 0.205 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9383 | -10.2391
MV/LV Substation GU***448 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =120 kVA | --> | 0.19 | 0 | 0.006 | 0.196 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9427 | -10.2332
MV/LV Substation PR***449 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.19 | 0 | 0.005 | 0.187 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9446 | -10.2295
MV/LV Substation FA***450 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =491 kVA | --> | 0.598 | 0 | 0.029 | 0.5 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9465 | -10.221
MV/LV Substation CA***451 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9506 | -10.2132
MV/LV Substation CU***452X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0.011 | 0.042 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0662 | -9.9102
MV/LV Substation ST***454 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.005 | 0.045 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9629 | -10.1775
MV/LV Substation DO***459X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =27 kVA | --> | 0.048 | 0 | 0.005 | 0.047 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0808 | -9.9279
MV/LV Substation CA***468 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =9 kVA | --> | 0.048 | 0 | 0 | 0.053 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.986 | -10.0809
MV/LV Substation CR***476X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =7 kVA | --> | 0.048 | 0 | 0 | 0.053 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.111 | -9.9017
MV/LV Substation MU***479X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.009 | 0.042 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.1225 | -9.898
MV/LV Substation MA***489X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0.005 | 0.193 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9465 | -10.2309
MV/LV Substation WI***491X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =620 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9354 | -10.2402
MV/LV Substation KI***498X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0.005 | 0.093 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0515 | -9.9455
MV/LV Substation TU***512X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8745 | -10.1901
MV/LV Substation DO***516 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8831 | -10.3624
MV/LV Substation PO***517 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =104 kVA | --> | 0.19 | 0 | 0.015 | 0.192 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8849 | -10.3657
MV/LV Substation DE***518X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9671 | -10.1732
MV/LV Substation CH***522 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0.01 | 0.19 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9065 | -10.3359
MV/LV Substation DO***533X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9747 | -10.1668
MV/LV Substation KI***538 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9169 | -10.3022
MV/LV Substation RE***543 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =14 kVA | --> | 0.048 | 0 | 0 | 0.052 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9214 | -10.2945
MV/LV Substation KN***545 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =168 kVA | --> | 0.19 | 0 | 0.005 | 0.191 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9248 | -10.2911
MV/LV Substation RE***552X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =184 kVA | --> | 0.19 | 0 | 0.01 | 0.185 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8309 | -10.1721
MV/LV Substation ST***554X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9593 | -10.1845
MV/LV Substation BA***562X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =380 kVA | --> | 0.38 | 0 | 0.004 | 0.38 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8163 | -10.17
MV/LV Substation ST***563X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.962 | -10.1817
MV/LV Substation GA***570X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =166 kVA | --> | 0.19 | 0 | 0.003 | 0.192 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9449 | -10.2325
MV/LV Substation DU***580 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =67 kVA | --> | 0.095 | 0 | 0.01 | 0.092 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8347 | -10.2618
MV/LV Substation KI***583X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =178 kVA | --> | 0.19 | 0 | 0.05 | 0.156 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9599 | -10.2565
MV/LV Substation GL***599X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =320 kVA | --> | 0.38 | 0 | 0 | 0.391 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0556 | -9.9446
MV/LV Substation GA***606 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0.01 | 0.042 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9367 | -10.2403
MV/LV Substation CO***627X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =178 kVA | --> | 0.19 | 0 | 0.005 | 0.189 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9404 | -10.24
MV/LV Substation SP***628X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =92 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8372 | -10.176
MV/LV Substation OC***631X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9619 | -10.18
MV/LV Substation KE***641 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.095 | 0 | 0.004 | 0.095 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0125 | -10.0988
MV/LV Substation DU***642X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8359 | -10.261
MV/LV Substation KE***644X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =90 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9979 | -10.1165
MV/LV Substation GO***648 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0325 | -10.0782
MV/LV Substation LY***652X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.853 | -10.2595
MV/LV Substation KE***661 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9299 | -10.2771
MV/LV Substation HO***696X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =189 kVA | --> | 0.19 | 0 | 0.025 | 0.173 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8251 | -10.276
MV/LV Substation WA***713X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =366 kVA | --> | 0.38 | 0 | 0 | 0.385 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.834 | -10.1733
MV/LV Substation MI***715 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8465 | -10.1117
MV/LV Substation UD***719X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =397 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8379 | -10.2627
MV/LV Substation SH***720X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =59 kVA | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0559 | -9.9422
MV/LV Substation LO***726 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7632 | -10.1621
MV/LV Substation CA***733 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =62 kVA | --> | 0.095 | 0 | 0.012 | 0.091 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7691 | -10.1024
MV/LV Substation LO***733X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =90 kVA | --> | 0.095 | 0 | 0.005 | 0.093 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.942 | -10.242
MV/LV Substation GL***747 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =64 kVA | --> | 0.095 | 0 | 0.037 | 0.072 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7605 | -10.0824
MV/LV Substation MA***759X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =90 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9463 | -10.2346
MV/LV Substation PA***770X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0.003 | 0.094 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.924 | -10.2927
MV/LV Substation OH***786X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.91 | -10.2331
MV/LV Substation DO***794 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0814 | -9.9251
MV/LV Substation IN***802 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =193 kVA | --> | 0.19 | 0 | 0.011 | 0.183 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9676 | -10.1688
MV/LV Substation RE***810X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =81 kVA | --> | 0.095 | 0 | 0.005 | 0.094 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9517 | -10.2136
MV/LV Substation CA***811 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =178 kVA | --> | 0.19 | 0 | 0 | 0.193 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9216 | -10.2897
MV/LV Substation CR***816 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.911 | -10.2279
MV/LV Substation T ***820 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =59 kVA | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8687 | -10.3348
MV/LV Substation JO***831 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =21 kVA | --> | 0.048 | 0 | 0.016 | 0.04 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8338 | -10.1716
MV/LV Substation BA***832 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =129 kVA | --> | 0.19 | 0 | 0.03 | 0.177 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.826 | -10.171
MV/LV Substation KN***832X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =113 kVA | --> | 0.19 | 0 | 0 | 0.202 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9264 | -10.2899
MV/LV Substation KI***840X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.095 | 0 | 0.004 | 0.093 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8261 | -10.2734
MV/LV Substation IN***841 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.76 |  | --> | 0.048 | 0 | 0.006 | 0.044 | 0 |  | --> | E19 ex KENMARE | Kenmare [T421] | KNOCKEARAGH |  | 51.8388 | -9.9123
MV/LV Substation BA***843 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =169 kVA | --> | 0.38 | 0 | 0.025 | 0.392 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9472 | -10.226
MV/LV Substation BA***851 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8208 | -10.2754
MV/LV Substation CL***852 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0.045 | 0.065 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8373 | -10.1945
MV/LV Substation CO***870X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8588 | -10.295
MV/LV Substation PO***882 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =189 kVA | --> | 0.19 | 0 | 0.005 | 0.188 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8823 | -10.3755
MV/LV Substation BE***882X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8239 | -10.273
MV/LV Substation CO***884 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7797 | -10.0988
MV/LV Substation CA***897X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =90 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8252 | -10.2718
MV/LV Substation EI***899 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =79 kVA | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8117 | -10.155
MV/LV Substation SP***900X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0.006 | 0.188 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8364 | -10.1726
MV/LV Substation PU***901 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8426 | -10.1908
MV/LV Substation UN***904 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8599 | -10.2897
MV/LV Substation MU***911 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8438 | -10.1889
MV/LV Substation GO***919 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =64 kVA | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8383 | -10.1951
MV/LV Substation KE***920X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =384 kVA | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9437 | -10.2338
MV/LV Substation SN***926X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.367 | 0.76 |  | --> | 0.38 | 0 | 0.005 | 0.381 | 0 |  | --> | E19 ex KENMARE | Kenmare [T421] | KNOCKEARAGH |  | 51.8361 | -9.9062
MV/LV Substation BE***927 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =72 kVA | --> | 0.095 | 0 | 0.006 | 0.092 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7852 | -10.0493
MV/LV Substation GA***932 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.773 | -10.1161
MV/LV Substation DE***935 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9662 | -10.1712
MV/LV Substation SL***939X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8677 | -10.1315
MV/LV Substation KI***940 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8243 | -10.2737
MV/LV Substation DE***943X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9702 | -10.1764
MV/LV Substation RE***944X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =448 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9406 | -10.2384
MV/LV Substation HO***959X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0.003 | 0.046 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9204 | -10.2905
MV/LV Substation DU***961X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =160 kVA | --> | 0.19 | 0 | 0 | 0.195 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8249 | -10.1686
MV/LV Substation SP***963 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =382 kVA | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9341 | -10.2388
MV/LV Substation GL***971 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.005 | 0.045 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8497 | -10.3346
MV/LV Substation CO***973 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0402 | -9.9624
MV/LV Substation KI***975 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.005 | 0.044 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9047 | -10.0629
MV/LV Substation KN***977 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =565 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9351 | -10.2394
MV/LV Substation DU***978 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8388 | -10.2604
MV/LV Substation GU***984X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0.01 | 0.04 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9339 | -10.2328
MV/LV Substation CO***985X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8956 | -10.3528
MV/LV Substation QU***988 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =328 kVA | --> | 0.38 | 0 | 0 | 0.39 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9485 | -10.2256
MV/LV Substation SE***991 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9457 | -10.2378
MV/LV Substation AG***992 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =70 kVA | --> | 0.095 | 0 | 0 | 0.099 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8457 | -10.3302
MV/LV Substation DU***993 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8326 | -10.2665
MV/LV Substation DE***996 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0 | 0.198 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7582 | -10.0889
MV/LV Substation KI***999 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0538 | -9.9414
MV/LV Substation TH***999X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8281 | -10.2704
MV/LV Substation GU***101 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.167 | 3.03 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =194 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1946 | -7.047
MV/LV Substation DO***102 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.176 | 3.03 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =193 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1948 | -7.0502
MV/LV Substation CO***103 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.036 | 3.03 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =103 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1924 | -7.0466
MV/LV Substation GL***104 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1909 | -7.0471
MV/LV Substation I ***105 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 3.03 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1906 | -7.049
MV/LV Substation MA***106 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.099 | 3.03 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =203 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1891 | -7.042
MV/LV Substation LR***107 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.286 | 3.03 |  | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =388 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1884 | -7.0431
MV/LV Substation TH***122 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1853 | -7.0547
MV/LV Substation CA***123 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1847 | -7.0556
MV/LV Substation BA***126 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 3.03 |  | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1798 | -7.0696
MV/LV Substation CL***145 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1694 | -7.1098
MV/LV Substation RE***157 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.45 | 3.03 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =622 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1589 | -7.1227
MV/LV Substation WA***167 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1806 | -7.1606
MV/LV Substation BA***171 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 3.03 |  | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1544 | -7.1506
MV/LV Substation ST***172 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.022 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =51 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1512 | -7.1578
MV/LV Substation RO***201 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.119 | 3.03 |  | --> | 0.19 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1929 | -7.0405
MV/LV Substation MA***202 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.066 | 3.03 |  | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =205 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1906 | -7.042
MV/LV Substation BA***203 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1946 | -7.0387
MV/LV Substation CH***205 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.128 | 3.03 |  | --> | 0.19 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1913 | -7.0355
MV/LV Substation MA***206 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.046 | 3.03 |  | --> | 0.095 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.192 | -7.0292
MV/LV Substation RO***207 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.139 | 3.03 |  | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1966 | -7.0291
MV/LV Substation BA***226 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 3.03 |  | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2003 | -7.0063
MV/LV Substation CA***230 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2039 | -6.9968
MV/LV Substation ST***235 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.203 | -6.9911
MV/LV Substation SE***236 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.078 | 3.03 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =198 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2036 | -6.988
MV/LV Substation TH***237 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.168 | 3.03 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2055 | -6.9919
MV/LV Substation IR***241 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.073 | 3.03 |  | --> | 0.095 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2045 | -6.9843
MV/LV Substation IC***243 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.316 | 3.03 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =383 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2018 | -6.9841
MV/LV Substation TA***257 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.068 | 3.03 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2085 | -6.9704
MV/LV Substation FO***258 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.173 | 3.03 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2067 | -6.9722
MV/LV Substation AS***271 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2256 | -6.9447
MV/LV Substation CO***314 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.355 | 3.03 |  | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.188 | -7.0514
MV/LV Substation CA***338 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 3.03 |  | --> | 0.095 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E13 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2593 | -7.0696
MV/LV Substation FI***374 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.126 | 3.03 |  | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =197 kW | --> | E13 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2398 | -7.1466
MV/LV Substation SI***4042 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 3.03 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1968 | -7.0306
MV/LV Substation CA***4053 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1298 | -7.1919
MV/LV Substation CA***4064 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2175 | -6.9475
MV/LV Substation FO***4065 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1569 | -7.1525
MV/LV Substation ST***4066 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 3.03 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2309 | -6.9424
MV/LV Substation CA***4070 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2186 | -6.961
MV/LV Substation FI***4076 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.269 | 3.03 |  | --> | 0.38 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2049 | -6.9786
MV/LV Substation RO***417 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 3.03 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E13 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.258 | -7.208
MV/LV Substation GO***427 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 3.03 |  | --> | 0.095 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2116 | -6.9574
MV/LV Substation PU***431 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2498 | -7.171
MV/LV Substation C ***436 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2175 | -6.9475
MV/LV Substation OR***451 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.182 | 3.03 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =192 kW | --> | E13 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2419 | -7.1481
MV/LV Substation CA***496 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 3.03 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =98 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2178 | -6.9565
MV/LV Substation GA***531 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1943 | -7.0236
MV/LV Substation CR***569 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.265 | 3.03 |  | --> | 0.38 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =384 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1894 | -7.0403
MV/LV Substation CA***570 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =50 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2102 | -6.9858
MV/LV Substation RO***590 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 3.03 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2056 | -6.9808
MV/LV Substation WO***595 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.197 | 3.03 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1905 | -7.0444
MV/LV Substation MO***599 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.166 | 3.03 |  | --> | 0.19 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =158 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.191 | -7.0503
MV/LV Substation BA***601 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1975 | -7.0079
MV/LV Substation MI***624 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 3.03 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.194 | -7.0518
MV/LV Substation TR***626 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2699 | -7.0688
MV/LV Substation CR***630 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2016 | -7.0056
MV/LV Substation RE***637 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.164 | -7.1154
MV/LV Substation GR***661 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.182 | 3.03 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =192 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2173 | -6.9571
MV/LV Substation TU***690 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 3.03 |  | --> | 0.048 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1651 | -7.1079
MV/LV Substation BA***703 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1963 | -7.0333
MV/LV Substation GR***705 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2038 | -6.9945
MV/LV Substation GU***025 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.199 | 8.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.093 | -8.163
MV/LV Substation SE***038X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0534 | -8.1492
MV/LV Substation LI***045X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0543 | -8.1455
MV/LV Substation CA***049X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0578 | -8.1391
MV/LV Substation CO***079X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.027 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =51 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1678 | -8.1379
MV/LV Substation VO***104 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1699 | -8.1366
MV/LV Substation ST***112 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.17 | -8.1384
MV/LV Substation AR***116X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0794 | -8.1221
MV/LV Substation DO***118 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1886 | -8.0144
MV/LV Substation CN***121X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.169 | 8.5 |  | --> | 0.19 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0456 | -8.0441
MV/LV Substation DR***127X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1772 | -8.1549
MV/LV Substation AN***129X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.5 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1856 | -8.0263
MV/LV Substation LO***131X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.194 | 8.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =191 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0525 | -8.0457
MV/LV Substation CO***134 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1722 | -8.15
MV/LV Substation EI***136 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =50 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0852 | -8.1688
MV/LV Substation GO***137X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.2479 | -7.8883
MV/LV Substation AL***138 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0505 | -8.1469
MV/LV Substation ED***138X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.2357 | -7.8825
MV/LV Substation GA***147 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1674 | -8.1349
MV/LV Substation DO***147X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.2233 | -8.0129
MV/LV Substation MU***149 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0296 | -8.1222
MV/LV Substation GL***162X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1911 | -7.8543
MV/LV Substation DE***171X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0842 | -8.1089
MV/LV Substation LE***201X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =92 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9938 | -8.0649
MV/LV Substation DR***217X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 8.5 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0312 | -7.973
MV/LV Substation AG***230X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0566 | -8.0706
MV/LV Substation CA***235X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.371 | 8.5 |  | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0642 | -8.1846
MV/LV Substation KN***238X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 54.0152 | -8.0248
MV/LV Substation LI***395 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0752 | -8.1019
MV/LV Substation DR***4023 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0345 | -7.971
MV/LV Substation KE***406 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 8.5 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0512 | -8.1372
MV/LV Substation RO***4068 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.086 | -8.1293
MV/LV Substation RO***4069 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0667 | -8.152
MV/LV Substation MC***4077 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.2472 | -7.8902
MV/LV Substation LO***4078 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.268 | 8.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =398 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0549 | -8.046
MV/LV Substation BA***4083 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 8.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0743 | -8.2028
MV/LV Substation BA***412 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 8.5 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =110 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.072 | -8.2033
MV/LV Substation GR***418 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 8.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0855 | -8.1292
MV/LV Substation AR***570 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0756 | -8.1065
MV/LV Substation AR***572 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0954 | -8.0763
MV/LV Substation DR***577 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.191 | 8.5 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1651 | -8.1401
MV/LV Substation LI***751 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1384 | -8.1397
MV/LV Substation DR***766 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.016 | 8.5 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =102 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1686 | -8.1446
MV/LV Substation RY***774 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0887 | -8.1116
MV/LV Substation CO***791 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.188 | 8.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =192 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0716 | -8.2023
MV/LV Substation D/***798 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1685 | -8.1477
MV/LV Substation AG***807 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0644 | -8.0893
MV/LV Substation CO***833 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1697 | -8.0643
MV/LV Substation DO***852 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.145 | 8.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =197 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1893 | -8.0151
MV/LV Substation LE***947 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1471 | -8.1036
MV/LV Substation ME***956 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 8.5 |  | --> | 0.095 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =74 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1913 | -8.0102
MV/LV Substation TH***004 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =513 kVA | --> | 0.598 | 0 | 0.011 | 0.5 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1432 | -10.2686
MV/LV Substation GO***007 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =191 kVA | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1659 | -10.4124
MV/LV Substation SM***017 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1874 | -10.4129
MV/LV Substation AQ***039 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =240 kVA | --> | 0.38 | 0 | 0.08 | 0.342 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.14 | -10.2784
MV/LV Substation MU***044 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.005 | 0.044 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1845 | -10.3631
MV/LV Substation VE***050 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =53 kVA | --> | 0.095 | 0 | 0.041 | 0.071 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1327 | -10.3576
MV/LV Substation PO***060 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.126 | -10.4534
MV/LV Substation EI***069 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =199 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1551 | -10.2931
MV/LV Substation CO***078 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1063 | -10.4546
MV/LV Substation VE***089 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.01 | 0.042 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1345 | -10.3647
MV/LV Substation KI***091 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.2054 | -10.3156
MV/LV Substation MA***095 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =329 kVA | --> | 0.598 | 0 | 0.026 | 0.5 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1417 | -10.2679
MV/LV Substation BA***102 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =330 kVA | --> | 0.38 | 0 | 0 | 0.389 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1539 | -10.293
MV/LV Substation BL***108 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =394 kVA | --> | 0.38 | 0 | 0 | 0.381 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1324 | -10.4621
MV/LV Substation SE***115 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =361 kVA | --> | 0.38 | 0 | 0.006 | 0.381 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1356 | -10.2701
MV/LV Substation MI***118 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0.006 | 0.092 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1452 | -10.2877
MV/LV Substation MI***120 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1426 | -10.2876
MV/LV Substation LA***121 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1648 | -10.3611
MV/LV Substation BA***125 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1373 | -10.4511
MV/LV Substation WA***126 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =66 kVA | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1513 | -10.2412
MV/LV Substation BA***131 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =135 kVA | --> | 0.19 | 0 | 0.052 | 0.16 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1315 | -10.2474
MV/LV Substation BA***209 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1801 | -10.4434
MV/LV Substation BA***4008 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.2282 | -10.301
MV/LV Substation GR***402 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1344 | -10.2573
MV/LV Substation BU***4064 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0 | 0.39 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1359 | -10.2682
MV/LV Substation MA***4066 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =509 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1381 | -10.2695
MV/LV Substation SA***4075 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =605 kVA | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1398 | -10.266
MV/LV Substation BA***420 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1554 | -10.2931
MV/LV Substation BA***431 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0.015 | 0.039 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1402 | -10.3756
MV/LV Substation BA***442 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.004 | 0.046 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1559 | -10.3964
MV/LV Substation RE***447 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =66 kVA | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1704 | -10.3869
MV/LV Substation CL***454 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =374 kVA | --> | 0.38 | 0 | 0.005 | 0.38 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1681 | -10.4036
MV/LV Substation BA***456 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =330 kVA | --> | 0.38 | 0 | 0.005 | 0.386 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1657 | -10.407
MV/LV Substation DU***470 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =371 kVA | --> | 0.38 | 0 | 0.005 | 0.38 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1785 | -10.4424
MV/LV Substation BA***479 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0.015 | 0.039 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1757 | -10.3825
MV/LV Substation FE***486 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1385 | -10.4583
MV/LV Substation CA***511 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.2007 | -10.3545
MV/LV Substation BI***516 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.2012 | -10.3652
MV/LV Substation FE***521 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.005 | 0.044 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.2151 | -10.3442
MV/LV Substation BA***533 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =74 kVA | --> | 0.095 | 0 | 0.01 | 0.091 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.2285 | -10.3071
MV/LV Substation FE***541 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.2154 | -10.3492
MV/LV Substation BA***555 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =28 kVA | --> | 0.048 | 0 | 0.016 | 0.038 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.152 | -10.2843
MV/LV Substation BA***560 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1767 | -10.3826
MV/LV Substation HI***576 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0.005 | 0.193 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1438 | -10.2613
MV/LV Substation MI***594 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0.005 | 0.045 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1407 | -10.294
MV/LV Substation BA***611 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1321 | -10.3101
MV/LV Substation MU***621 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.006 | 0.044 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1403 | -10.318
MV/LV Substation EM***636 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =10 kVA | --> | 0.048 | 0 | 0.035 | 0.027 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1282 | -10.3792
MV/LV Substation SC***639 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =342 kVA | --> | 0.38 | 0 | 0.011 | 0.38 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1335 | -10.2683
MV/LV Substation NE***640 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =192 kVA | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1362 | -10.2724
MV/LV Substation TR***641 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =426 kVA | --> | 0.598 | 0 | 0.063 | 0.5 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1382 | -10.2705
MV/LV Substation UD***644 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =181 kVA | --> | 0.19 | 0 | 0.029 | 0.171 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1437 | -10.2899
MV/LV Substation MA***646 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =83 kVA | --> | 0.19 | 0 | 0.014 | 0.195 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1389 | -10.2663
MV/LV Substation QU***647 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =262 kVA | --> | 0.598 | 0 | 0.036 | 0.5 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1391 | -10.2732
MV/LV Substation HO***649 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0.01 | 0.091 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.145 | -10.2746
MV/LV Substation MI***652 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =149 kVA | --> | 0.19 | 0 | 0.028 | 0.176 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1417 | -10.2904
MV/LV Substation CR***653 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =269 kVA | --> | 0.38 | 0 | 0.005 | 0.394 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1419 | -10.2643
MV/LV Substation DU***656 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1712 | -10.402
MV/LV Substation BA***657 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1862 | -10.4311
MV/LV Substation KE***658 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1674 | -10.392
MV/LV Substation HI***659 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =545 kVA | --> | 0.598 | 0 | 0.04 | 0.5 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1436 | -10.2651
MV/LV Substation GL***660 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0.011 | 0.04 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.2077 | -10.359
MV/LV Substation CL***661 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =184 kVA | --> | 0.19 | 0 | 0.017 | 0.18 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1536 | -10.4528
MV/LV Substation GA***677 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =316 kVA | --> | 0.38 | 0 | 0 | 0.391 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1391 | -10.2721
MV/LV Substation GO***702 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =173 kVA | --> | 0.19 | 0 | 0.005 | 0.19 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1638 | -10.4119
MV/LV Substation CL***714 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =546 kVA | --> | 0.598 | 0 | 0.006 | 0.5 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.146 | -10.2636
MV/LV Substation TO***719 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =185 kVA | --> | 0.38 | 0 | 0.043 | 0.376 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1402 | -10.2701
MV/LV Substation FA***727 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1055 | -10.41
MV/LV Substation IC***729 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =382 kVA | --> | 0.38 | 0 | 0 | 0.382 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1371 | -10.2753
MV/LV Substation GO***736 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =287 kVA | --> | 0.38 | 0 | 0.038 | 0.367 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1427 | -10.2723
MV/LV Substation BA***753 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =87 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1554 | -10.2498
MV/LV Substation RA***767 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =169 kVA | --> | 0.19 | 0 | 0.011 | 0.186 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1408 | -10.2837
MV/LV Substation MO***788 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =367 kVA | --> | 0.38 | 0 | 0.008 | 0.379 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1488 | -10.2582
MV/LV Substation MA***793 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =91 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1352 | -10.2662
MV/LV Substation AR***795 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =344 kVA | --> | 0.38 | 0 | 0.033 | 0.363 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1421 | -10.2816
MV/LV Substation BA***801 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =82 kVA | --> | 0.095 | 0 | 0.005 | 0.094 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1452 | -10.258
MV/LV Substation HA***804 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1424 | -10.2744
MV/LV Substation VE***816 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.005 | 0.044 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1259 | -10.3825
MV/LV Substation CO***825 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =171 kVA | --> | 0.19 | 0 | 0.005 | 0.19 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1432 | -10.2676
MV/LV Substation BA***826 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.146 | -10.2789
MV/LV Substation TH***829 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =394 kVA | --> | 0.38 | 0 | 0.01 | 0.374 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1413 | -10.2866
MV/LV Substation BA***840 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1582 | -10.2854
MV/LV Substation GO***846 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =147 kVA | --> | 0.19 | 0 | 0.005 | 0.193 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.14 | -10.2609
MV/LV Substation BA***854 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =91 kVA | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1551 | -10.2895
MV/LV Substation CN***858 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =368 kVA | --> | 0.38 | 0 | 0.014 | 0.374 | 0 |  | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.145 | -10.2687
MV/LV Substation BA***863 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1266 | -10.3938
MV/LV Substation NE***867 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =126 kVA | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1373 | -10.2656
MV/LV Substation CO***001 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.147 | 5.75 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =197 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3847 | -9.2962
MV/LV Substation TH***018X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 5.75 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3738 | -9.3096
MV/LV Substation CO***038X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.257 | 5.75 |  | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =388 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3852 | -9.2993
MV/LV Substation LI***044X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.305 | 5.75 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =393 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3826 | -9.3019
MV/LV Substation G.***055X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 5.75 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.388 | -9.3052
MV/LV Substation FI***085X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3797 | -9.2842
MV/LV Substation KI***086X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3557 | -9.3225
MV/LV Substation SE***099X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.062 | 5.75 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =100 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3116 | -9.2849
MV/LV Substation EA***101 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.11 | 5.75 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =202 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3874 | -9.2842
MV/LV Substation DR***107X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 5.75 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3912 | -9.3039
MV/LV Substation FO***110X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.159 | 5.75 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =196 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3857 | -9.2945
MV/LV Substation TH***115X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.436 | 5.75 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =624 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3849 | -9.3021
MV/LV Substation FA***121 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 5.75 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3782 | -9.1393
MV/LV Substation BR***123X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =56 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3126 | -9.2735
MV/LV Substation AT***129 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.19 | 0.33 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.4644 | -9.2943
MV/LV Substation KO***141 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.312 | 5.75 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =382 kW | --> | E19 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3869 | -9.2866
MV/LV Substation EN***141X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3771 | -9.3007
MV/LV Substation MO***148X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 5.75 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3159 | -9.2342
MV/LV Substation MO***149 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 5.75 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3242 | -9.2382
MV/LV Substation PI***150X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =50 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3616 | -9.3092
MV/LV Substation TY***153X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.196 | 5.75 |  | --> | 0.19 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3895 | -9.2837
MV/LV Substation MI***162 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3097 | -9.1493
MV/LV Substation CA***168X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.122 | 5.75 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =200 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3416 | -9.2972
MV/LV Substation CA***172X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3526 | -9.2764
MV/LV Substation CR***178X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.321 | 5.75 |  | --> | 0.38 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3778 | -9.3028
MV/LV Substation WA***184 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.05 | 5.75 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =98 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3745 | -9.303
MV/LV Substation AT***222 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 0.33 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.4669 | -9.2973
MV/LV Substation AB***224X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.308 | 5.75 |  | --> | 0.38 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3859 | -9.2957
MV/LV Substation KN***236 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.3958 | -9.3035
MV/LV Substation TO***244X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3925 | -9.303
MV/LV Substation DR***249X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3835 | -9.2343
MV/LV Substation CA***250X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.178 | 5.75 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =193 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3847 | -9.2989
MV/LV Substation AB***253 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 0.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =50 kW | --> | C22 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.3909 | -9.3078
MV/LV Substation TE***255X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.33 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.4797 | -9.2205
MV/LV Substation AT***265 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 0.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.4585 | -9.2888
MV/LV Substation BR***271 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 5.75 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =100 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3127 | -9.2658
MV/LV Substation KN***276 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =50 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.394 | -9.2828
MV/LV Substation AT***280X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.4616 | -9.2862
MV/LV Substation KI***284 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.111 | 5.75 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =198 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3773 | -9.3081
MV/LV Substation KN***291 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 5.75 |  | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3558 | -9.1762
MV/LV Substation BE***292X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 5.75 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3837 | -9.2933
MV/LV Substation TH***293X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3701 | -9.3028
MV/LV Substation BA***307X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.4049 | -9.2506
MV/LV Substation TO***313 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3651 | -9.1516
MV/LV Substation RI***327X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.393 | 5.75 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =381 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3746 | -9.3102
MV/LV Substation GO***330 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.4509 | -9.2693
MV/LV Substation CE***331 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.13 | 5.75 |  | --> | 0.19 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =194 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3848 | -9.2955
MV/LV Substation EL***345X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.389 | 5.75 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =381 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3746 | -9.3076
MV/LV Substation AS***348X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 7.48 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex CHURCHTOWN | Churchtown [T422] | RATHKEALE |  | 52.3981 | -9.1711
MV/LV Substation CO***355X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 5.75 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3826 | -9.2841
MV/LV Substation DO***358 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 7.48 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E12 ex CHURCHTOWN | Churchtown [T422] | RATHKEALE |  | 52.4003 | -9.1682
MV/LV Substation CO***364 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 0.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.4348 | -9.2557
MV/LV Substation TE***367X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 5.75 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.387 | -9.2981
MV/LV Substation CA***370 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3663 | -9.2956
MV/LV Substation MO***400 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3232 | -9.2415
MV/LV Substation CR***4017 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.376 | -9.2924
MV/LV Substation AB***4039 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.341 | 5.75 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =388 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3874 | -9.2979
MV/LV Substation SE***4105 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 0.33 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.465 | -9.2891
MV/LV Substation KE***4111 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.39 | -9.2476
MV/LV Substation MC***4130 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3142 | -9.2817
MV/LV Substation BA***4147 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 7.48 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex CHURCHTOWN | Churchtown [T422] | RATHKEALE |  | 52.4127 | -9.1528
MV/LV Substation GA***4149 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.4625 | -9.2697
MV/LV Substation EO***4151 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 5.75 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3347 | -9.2614
MV/LV Substation CH***4163 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 7.48 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E12 ex CHURCHTOWN | Churchtown [T422] | RATHKEALE |  | 52.3896 | -9.142
MV/LV Substation PR***464 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 0.33 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.4579 | -9.2868
MV/LV Substation AT***466 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.068 | 0.33 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.4618 | -9.2917
MV/LV Substation AB***477 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.289 | 0.33 |  | --> | 0.38 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.461 | -9.2876
MV/LV Substation PA***482 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 0.33 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.4675 | -9.2516
MV/LV Substation BL***544 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.4935 | -9.2893
MV/LV Substation PU***621 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.046 | 5.75 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =102 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3789 | -9.3093
MV/LV Substation KI***622 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.292 | 5.75 |  | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =388 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3791 | -9.3037
MV/LV Substation SE***623 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 5.75 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3796 | -9.2992
MV/LV Substation FE***635 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =188 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =192 kW | --> | C23 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.352 | -9.3273
MV/LV Substation BR***662 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.053 | 5.75 |  | --> | 0.095 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3132 | -9.2698
MV/LV Substation MO***700 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 5.75 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3218 | -9.2382
MV/LV Substation MO***701 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.06 | 5.75 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3176 | -9.2343
MV/LV Substation MO***702 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3144 | -9.2365
MV/LV Substation NE***812 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 5.75 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3889 | -9.3017
MV/LV Substation CO***813 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 5.75 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3875 | -9.2962
MV/LV Substation CH***814 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.308 | 5.75 |  | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =388 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3868 | -9.3007
MV/LV Substation LI***815 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.06 | 5.75 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =208 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3875 | -9.2907
MV/LV Substation BA***840 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.177 | 5.75 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3954 | -9.2503
MV/LV Substation DE***853 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 5.75 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3837 | -9.2184
MV/LV Substation TE***856 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3742 | -9.2059
MV/LV Substation ME***877 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.196 | 5.75 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3574 | -9.2116
MV/LV Substation TO***910 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 5.75 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E21 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.379 | -9.1354
MV/LV Substation DE***919 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.1 | 7.48 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =195 kW | --> | E12 ex CHURCHTOWN | Churchtown [T422] | RATHKEALE |  | 52.3966 | -9.1735
MV/LV Substation IN***920 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 7.48 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E12 ex CHURCHTOWN | Churchtown [T422] | RATHKEALE |  | 52.3988 | -9.1719
MV/LV Substation RA***921 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 7.48 |  | --> | 0.095 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | E12 ex CHURCHTOWN | Churchtown [T422] | RATHKEALE |  | 52.3946 | -9.1607
MV/LV Substation AB***975 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 5.75 |  | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3833 | -9.2856
MV/LV Substation CA***001 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =394 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9027 | -8.5791
MV/LV Substation HO***003 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9054 | -8.5906
MV/LV Substation F ***004 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9045 | -8.5915
MV/LV Substation ST***005X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8879 | -8.4894
MV/LV Substation CO***006 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.19 | 0 | 0.005 | 0.191 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9008 | -8.5859
MV/LV Substation HO***007X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =131 kVA | --> | 0.19 | 0 | 0.008 | 0.193 | 0 |  | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9084 | -8.5877
MV/LV Substation PO***016 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =495 kVA | --> | 0.598 | 0 | 0.019 | 0.5 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.905 | -8.5752
MV/LV Substation CA***016X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =167 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8984 | -8.5849
MV/LV Substation GA***017X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8915 | -8.4851
MV/LV Substation BA***019 |  | 10 kV | _ | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =787 kVA | --> | 0.95 | 0 | 0.006 | 0.5 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9018 | -8.5835
MV/LV Substation CR***023 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 |  | --> | 0.095 | 0 | 0 | 0.109 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8999 | -8.5763
MV/LV Substation PU***026 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =122 kVA | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8991 | -8.561
MV/LV Substation MA***029 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =166 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9039 | -8.585
MV/LV Substation HA***037X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.853 | -8.725
MV/LV Substation SE***074X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8719 | -8.4032
MV/LV Substation HI***075X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.8944 | -8.7323
MV/LV Substation SE***086X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =159 kVA | --> | 0.19 | 0 | 0 | 0.196 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8973 | -8.5604
MV/LV Substation SE***097X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8934 | -8.5865
MV/LV Substation CA***101 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8842 | -8.4651
MV/LV Substation KI***101X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8808 | -8.4496
MV/LV Substation ST***103 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.8901 | -8.6869
MV/LV Substation DE***104 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.323 | 1.04 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =383 kW | --> | C12 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8711 | -8.4042
MV/LV Substation R ***111 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.095 | 0 | 0.021 | 0.086 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8212 | -8.556
MV/LV Substation LO***113 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8223 | -8.5632
MV/LV Substation TH***119X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =153 kVA | --> | 0.19 | 0 | 0.005 | 0.193 | 0 |  | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.907 | -8.5836
MV/LV Substation LA***131X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8823 | -8.5591
MV/LV Substation TH***145X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0 | 0.388 | 0 |  | --> | C11 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8993 | -8.5731
MV/LV Substation MO***181X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 2.45 |  | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C19 ex GURTEEN | Gurteen [T41] | TONROE |  | 53.9406 | -8.4925
MV/LV Substation BE***203X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =177 kVA | --> | 0.19 | 0 | 0 | 0.193 | 0 |  | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9027 | -8.5899
MV/LV Substation SE***216 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8206 | -8.5623
MV/LV Substation HO***230 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =197 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8845 | -8.5204
MV/LV Substation BD***230X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =602 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8961 | -8.5677
MV/LV Substation BR***232 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9215 | -8.6362
MV/LV Substation KI***240X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =134 kVA | --> | 0.19 | 0 | 0.009 | 0.192 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9047 | -8.5654
MV/LV Substation PR***268X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =183 kVA | --> | 0.19 | 0 | 0.011 | 0.184 | 0 |  | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8991 | -8.5982
MV/LV Substation WO***269X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8221 | -8.5654
MV/LV Substation CL***301X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =293 kVA | --> | 0.38 | 0 | 0 | 0.394 | 0 |  | --> | C11 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9006 | -8.5739
MV/LV Substation ST***303X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =521 kVA | --> | 0.598 | 0 | 0.012 | 0.5 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9007 | -8.5793
MV/LV Substation WE***305X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8777 | -8.396
MV/LV Substation BR***313X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =161 kVA | --> | 0.19 | 0 | 0.01 | 0.188 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8974 | -8.5848
MV/LV Substation MI***373X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =172 kVA | --> | 0.19 | 0 | 0.011 | 0.186 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8972 | -8.5741
MV/LV Substation CO***376X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =520 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9056 | -8.5726
MV/LV Substation FR***377X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =184 kVA | --> | 0.19 | 0 | 0.005 | 0.188 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8992 | -8.5889
MV/LV Substation CA***379X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9019 | -8.6844
MV/LV Substation GO***385X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.165 | 1.04 |  | --> | 0.19 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | C12 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8734 | -8.4051
MV/LV Substation PU***4027 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9125 | -8.6192
MV/LV Substation WO***403 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9341 | -8.7881
MV/LV Substation CA***4035 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.811 | -8.6709
MV/LV Substation CL***4058 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8303 | -8.6309
MV/LV Substation BA***4063 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | C14 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9665 | -8.7147
MV/LV Substation UR***4082 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.8559 | -8.7323
MV/LV Substation AG***4130 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.847 | -8.5787
MV/LV Substation BR***4135 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.9032 | -8.3856
MV/LV Substation DA***4161 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9066 | -8.5602
MV/LV Substation MI***4169 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8775 | -8.393
MV/LV Substation FL***4198 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.45 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C19 ex GURTEEN | Gurteen [T41] | TONROE |  | 53.9322 | -8.5259
MV/LV Substation CR***4218 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C14 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9406 | -8.6967
MV/LV Substation TH***433X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =2 kVA | --> | 0.048 | 0 | 0 | 0.054 | 0 |  | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9042 | -8.5902
MV/LV Substation LY***437X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8971 | -8.5688
MV/LV Substation CL***458X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8236 | -8.5878
MV/LV Substation PU***461X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.8896 | -8.6962
MV/LV Substation TR***462X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.8878 | -8.6907
MV/LV Substation FO***484X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =167 kVA | --> | 0.19 | 0 | 0 | 0.194 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9035 | -8.568
MV/LV Substation OA***503X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =163 kVA | --> | 0.19 | 0 | 0 | 0.195 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8974 | -8.5807
MV/LV Substation RI***513X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0 | 0.198 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.907 | -8.5658
MV/LV Substation SC***516X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =195 kVA | --> | 0.19 | 0 | 0.005 | 0.187 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9182 | -8.7761
MV/LV Substation LI***519X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8581 | -8.6292
MV/LV Substation CU***527X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.8902 | -8.6985
MV/LV Substation CO***542X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.8902 | -8.6914
MV/LV Substation CO***566 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =90 kVA | --> | 0.095 | 0 | 0.003 | 0.094 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8535 | -8.63
MV/LV Substation CL***578 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8316 | -8.6254
MV/LV Substation FR***599 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.009 | 1.04 |  | --> | 0.095 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =102 kW | --> | C12 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8681 | -8.4068
MV/LV Substation AS***603 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.171 | 1.04 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C12 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8755 | -8.4021
MV/LV Substation CO***758 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.011 | 0.041 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8858 | -8.5006
MV/LV Substation SH***789 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =22 kVA | --> | 0.048 | 0 | 0 | 0.051 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8813 | -8.4509
MV/LV Substation MO***875 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 2.45 |  | --> | 0.095 | 0 | 0.014 | 0.088 | 0 |  | --> | C19 ex GURTEEN | Gurteen [T41] | TONROE |  | 53.9432 | -8.496
MV/LV Substation MO***876 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 2.45 |  | --> | 0.095 | 0 | 0.005 | 0.092 | 0 |  | --> | C19 ex GURTEEN | Gurteen [T41] | TONROE |  | 53.944 | -8.4938
MV/LV Substation LI***900 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =26 kVA | --> | 0.048 | 0 | 0 | 0.051 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8744 | -8.4807
MV/LV Substation PU***906 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C11 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9009 | -8.5712
MV/LV Substation LO***910 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8306 | -8.5532
MV/LV Substation UG***912 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9101 | -8.7268
MV/LV Substation UR***915 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =74 kVA | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.8458 | -8.7359
MV/LV Substation O ***921 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =196 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9036 | -8.5814
MV/LV Substation CU***924 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =83 kVA | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8229 | -8.5682
MV/LV Substation WA***927 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =187 kVA | --> | 0.38 | 0 | 0.118 | 0.321 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9086 | -8.464
MV/LV Substation SO***931 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2.45 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | C19 ex GURTEEN | Gurteen [T41] | TONROE |  | 53.9331 | -8.5171
MV/LV Substation KI***936 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.095 | 0 | 0.004 | 0.099 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9067 | -8.5679
MV/LV Substation CA***939 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.173 | 1.04 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =194 kW | --> | C12 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8687 | -8.4104
MV/LV Substation B ***957 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.19 | 0 | 0 | 0.196 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9067 | -8.5573
MV/LV Substation PU***959 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9074 | -8.4835
MV/LV Substation MC***999 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C22 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9099 | -8.5552
MV/LV Substation TI***005 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.211 | 2.33 |  | --> | 0.38 | 0 | 0.019 | 0.391 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1159 | -9.1641
MV/LV Substation ME***006X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.33 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex MOY | Moy [T421,T422] | MOY |  | 54.1295 | -9.166
MV/LV Substation LA***008X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.33 |  | --> | 0.048 | 0 | 0.005 | 0.044 | 0 |  | --> | E11 ex MOY | Moy [T421,T422] | MOY |  | 54.1317 | -9.1664
MV/LV Substation MO***013 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.237 | 0.74 |  | --> | 0.38 | 0 | 0.027 | 0.382 | 0 |  | --> | C16 ex RAHANS | Rahans [T41] | MOY |  | 54.1069 | -9.1606
MV/LV Substation CA***016X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2.33 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1135 | -9.1728
MV/LV Substation AB***018X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.334 | 2.33 |  | --> | 0.38 | 0 | 0.027 | 0.369 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.1405 | -9.165
MV/LV Substation CO***029X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.033 | 0.74 |  | --> | 0.095 | 0 | 0.094 | 0.034 | 0 |  | --> | C15 ex RAHANS | Rahans [T41] | MOY |  | 54.0908 | -9.1687
MV/LV Substation MU***040X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 2.33 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1041 | -9.1685
MV/LV Substation FE***041 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.476 | 2.33 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1142 | -9.171
MV/LV Substation UN***044X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.33 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.115 | -9.1703
MV/LV Substation KE***047 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.338 | 2.33 |  | --> | 0.38 | 0 | 0.007 | 0.383 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1126 | -9.1606
MV/LV Substation CA***047X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.141 | 2.33 |  | --> | 0.19 | 0 | 0.02 | 0.183 | 0 |  | --> | E11 ex MOY | Moy [T421,T422] | MOY |  | 54.1307 | -9.1655
MV/LV Substation RA***059 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.35 | 0.74 |  | --> | 0.38 | 0 | 0 | 0.387 | 0 |  | --> | C16 ex RAHANS | Rahans [T41] | MOY |  | 54.1071 | -9.1631
MV/LV Substation CH***061 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.33 |  | --> | 0.598 | 0 | 0.041 | 0.5 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1034 | -9.1599
MV/LV Substation LA***061X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 2.33 |  | --> | 0.095 | 0 | 0.029 | 0.075 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.1551 | -9.1806
MV/LV Substation BR***062X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.33 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.1363 | -9.1665
MV/LV Substation RE***072X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.74 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex RAHANS | Rahans [T41] | MOY |  | 54.0923 | -9.1967
MV/LV Substation LO***079X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.74 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex RAHANS | Rahans [T41] | MOY |  | 54.1011 | -9.1787
MV/LV Substation WA***090X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.156 | 2.33 |  | --> | 0.19 | 0 | 0.016 | 0.184 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1023 | -9.1626
MV/LV Substation TO***091X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.167 | 2.33 |  | --> | 0.19 | 0 | 0.01 | 0.187 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.137 | -9.1681
MV/LV Substation KN***096X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.451 | 2.33 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1068 | -9.1648
MV/LV Substation NE***109X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.177 | 2.33 |  | --> | 0.19 | 0 | 0.01 | 0.186 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.1329 | -9.1691
MV/LV Substation LO***111X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 2.33 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | E13 ex MOY | Moy [T421,T422] | MOY |  | 54.0546 | -9.1566
MV/LV Substation RE***112X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.381 | 2.33 |  | --> | 0.38 | 0 | 0.005 | 0.379 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1014 | -9.1615
MV/LV Substation AR***119X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.054 | 0.74 |  | --> | 0.095 | 0 | 0 | 0.101 | 0 |  | --> | C15 ex RAHANS | Rahans [T41] | MOY |  | 54.0887 | -9.2304
MV/LV Substation TU***121 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.33 |  | --> | 0.048 | 0 | 0.01 | 0.04 | 0 |  | --> | E13 ex MOY | Moy [T421,T422] | MOY |  | 54.0912 | -9.1911
MV/LV Substation RA***125X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 0.74 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex RAHANS | Rahans [T41] | MOY |  | 54.0866 | -9.1642
MV/LV Substation RE***138X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.74 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex RAHANS | Rahans [T41] | MOY |  | 54.0912 | -9.164
MV/LV Substation CO***139X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.74 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C15 ex RAHANS | Rahans [T41] | MOY |  | 54.0939 | -9.1653
MV/LV Substation KN***144X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 2.33 |  | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1053 | -9.1698
MV/LV Substation CA***158 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.014 | 2.33 |  | --> | 0.048 | 0 | 0 | 0.052 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1161 | -9.1758
MV/LV Substation JO***163X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.33 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.1458 | -9.1699
MV/LV Substation BI***183 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.74 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C15 ex RAHANS | Rahans [T41] | MOY |  | 54.0835 | -9.1578
MV/LV Substation MO***199 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.135 | 2.33 |  | --> | 0.19 | 0 | 0.019 | 0.185 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1061 | -9.1601
MV/LV Substation GO***207 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.078 | 2.33 |  | --> | 0.095 | 0 | 0.005 | 0.094 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1174 | -9.1782
MV/LV Substation CU***221 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.33 |  | --> | 0.048 | 0 | 0.006 | 0.043 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.1448 | -9.1734
MV/LV Substation CR***231 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.33 |  | --> | 0.048 | 0 | 0.012 | 0.039 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.133 | -9.1744
MV/LV Substation RE***244 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 2.33 |  | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | E13 ex MOY | Moy [T421,T422] | MOY |  | 54.0854 | -9.1684
MV/LV Substation AR***249 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2.33 |  | --> | 0.048 | 0 | 0.003 | 0.046 | 0 |  | --> | E18 ex MOY | Moy [T421,T422] | MOY |  | 54.1245 | -9.1775
MV/LV Substation CA***267 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 2.33 |  | --> | 0.048 | 0 | 0.008 | 0.044 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.1357 | -9.1602
MV/LV Substation DO***289 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.376 | 2.33 |  | --> | 0.38 | 0 | 0.006 | 0.379 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1045 | -9.1622
MV/LV Substation RA***323 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.369 | 0.74 |  | --> | 0.38 | 0 | 0 | 0.384 | 0 |  | --> | C15 ex RAHANS | Rahans [T41] | MOY |  | 54.09 | -9.1537
MV/LV Substation JE***381 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 2.33 |  | --> | 0.095 | 0 | 0.014 | 0.086 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.1418 | -9.1677
MV/LV Substation CO***384 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 2.33 |  | --> | 0.095 | 0 | 0.005 | 0.095 | 0 |  | --> | E13 ex MOY | Moy [T421,T422] | MOY |  | 54.1174 | -9.1978
MV/LV Substation SA***4014 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.347 | 2.33 |  | --> | 0.38 | 0 | 0.01 | 0.38 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1173 | -9.1711
MV/LV Substation PR***4020 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.33 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1123 | -9.1608
MV/LV Substation BR***4022 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.33 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1153 | -9.1748
MV/LV Substation CU***4040 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.394 | 2.33 |  | --> | 0.38 | 0 | 0.01 | 0.374 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.137 | -9.1698
MV/LV Substation AR***4046 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.33 |  | --> | 0.598 | 0 | 0.029 | 0.5 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1193 | -9.176
MV/LV Substation RA***4047 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.338 | 0.74 |  | --> | 0.38 | 0 | 0 | 0.388 | 0 |  | --> | C16 ex RAHANS | Rahans [T41] | MOY |  | 54.1013 | -9.158
MV/LV Substation CU***429 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 2.33 |  | --> | 0.048 | 0 | 0.004 | 0.046 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.1382 | -9.1648
MV/LV Substation BA***487 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.33 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1225 | -9.1832
MV/LV Substation SH***620 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.058 | 0.74 |  | --> | 0.095 | 0 | 0.005 | 0.097 | 0 |  | --> | C15 ex RAHANS | Rahans [T41] | MOY |  | 54.0969 | -9.1665
MV/LV Substation HO***621 |  | 10 kV | _ | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0.5 | 0.74 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex RAHANS | Rahans [T41] | MOY |  | 54.0982 | -9.1602
MV/LV Substation KN***701 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.33 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1105 | -9.1781
MV/LV Substation BE***712 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 2.33 |  | --> | 0.048 | 0 | 0.008 | 0.044 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1004 | -9.1653
MV/LV Substation BA***738 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 2.33 |  | --> | 0.048 | 0 | 0.005 | 0.045 | 0 |  | --> | E13 ex MOY | Moy [T421,T422] | MOY |  | 54.0559 | -9.1697
MV/LV Substation MO***739 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.166 | 2.33 |  | --> | 0.19 | 0 | 0 | 0.195 | 0 |  | --> | E13 ex MOY | Moy [T421,T422] | MOY |  | 54.0575 | -9.1573
MV/LV Substation DI***762 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.33 |  | --> | 0.048 | 0 | 0.005 | 0.044 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.1348 | -9.1669
MV/LV Substation MC***806 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.33 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1208 | -9.1811
MV/LV Substation BE***937 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.176 | 2.33 |  | --> | 0.19 | 0 | 0 | 0.193 | 0 |  | --> | E13 ex MOY | Moy [T421,T422] | MOY |  | 54.0584 | -9.1712
MV/LV Substation TE***955 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 2.33 |  | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1098 | -9.1665
MV/LV Substation BI***995 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.123 | 0.74 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C15 ex RAHANS | Rahans [T41] | MOY |  | 54.0834 | -9.1623
MV/LV Substation LO***998 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.121 | 2.33 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1131 | -9.1667
MV/LV Substation CL***206 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.078 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.8752 | -9.946
MV/LV Substation CU***222 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9183 | -9.7949
MV/LV Substation KE***224 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9722 | -10.0985
MV/LV Substation PU***225 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.099 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9664 | -10.1028
MV/LV Substation DO***228 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.976 | -10.0474
MV/LV Substation MU***253 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9052 | -9.7968
MV/LV Substation CA***255 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.196 | 1.5 |  | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9765 | -10.0564
MV/LV Substation KE***314 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.187 | 1.5 |  | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9723 | -10.1023
MV/LV Substation TO***333 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0067 | -9.9599
MV/LV Substation DE***341 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9033 | -9.9422
MV/LV Substation AC***351 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.342 | 1.5 |  | --> | 0.38 | 0 | 0 | 0.388 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9333 | -9.9147
MV/LV Substation BA***366 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 1.5 |  | --> | 0.095 | 0 | 0.005 | 0.092 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0272 | -9.8258
MV/LV Substation AC***376 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9345 | -9.9098
MV/LV Substation KE***377 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9723 | -10.0951
MV/LV Substation MU***378 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9067 | -9.771
MV/LV Substation SR***380 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.5 |  | --> | 0.048 | 0 | 0.017 | 0.035 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9267 | -9.9375
MV/LV Substation PO***4006 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E16 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9393 | -9.9153
MV/LV Substation AC***4010 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9298 | -9.9253
MV/LV Substation DO***4015 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0127 | -9.9998
MV/LV Substation RT***4016 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9574 | -10.0267
MV/LV Substation MU***4027 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 1.5 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9061 | -9.7853
MV/LV Substation DU***4038 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0108 | -10.0282
MV/LV Substation B ***4045 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9903 | -10.0411
MV/LV Substation SE***4054 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0097 | -10.0236
MV/LV Substation DO***4068 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0128 | -10.0178
MV/LV Substation MU***4096 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.197 | 1.5 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9067 | -9.7686
MV/LV Substation BU***416X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9703 | -9.986
MV/LV Substation MU***418X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9054 | -9.7609
MV/LV Substation TO***444X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.5 |  | --> | 0.048 | 0 | 0.005 | 0.045 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9534 | -9.8451
MV/LV Substation BA***447X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.361 | 1.5 |  | --> | 0.38 | 0 | 0 | 0.385 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0255 | -9.8256
MV/LV Substation MI***510X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9062 | -9.7691
MV/LV Substation MU***511X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9057 | -9.7861
MV/LV Substation DO***514X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9808 | -10.0394
MV/LV Substation SA***527X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9764 | -10.0773
MV/LV Substation AC***539X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.162 | 1.5 |  | --> | 0.19 | 0 | 0.005 | 0.191 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9299 | -9.9282
MV/LV Substation KE***553X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9765 | -10.0819
MV/LV Substation GL***559X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9325 | -9.9427
MV/LV Substation SL***563X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9965 | -10.0643
MV/LV Substation RO***565X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.5 |  | --> | 0.048 | 0 | 0.006 | 0.044 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9018 | -9.708
MV/LV Substation CU***569X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.194 | 1.5 |  | --> | 0.19 | 0 | 0 | 0.191 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9726 | -10.1598
MV/LV Substation BE***571X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9775 | -10.0756
MV/LV Substation SL***577X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.186 | 1.5 |  | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0011 | -10.0379
MV/LV Substation DU***579X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0095 | -10.0247
MV/LV Substation TH***584X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.184 | 1.5 |  | --> | 0.19 | 0 | 0.005 | 0.188 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.927 | -9.9299
MV/LV Substation NE***589 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.043 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.102 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.904 | -9.6895
MV/LV Substation ST***589X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.5 |  | --> | 0.048 | 0 | 0.005 | 0.044 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9293 | -9.9304
MV/LV Substation SE***595X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.343 | 1.5 |  | --> | 0.38 | 0 | 0 | 0.388 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9042 | -9.7962
MV/LV Substation WE***597X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 1.5 |  | --> | 0.048 | 0 | 0.005 | 0.046 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9777 | -10.0842
MV/LV Substation MU***599 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.105 | 1.5 |  | --> | 0.19 | 0 | 0.012 | 0.194 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.908 | -9.7677
MV/LV Substation MU***600 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.109 | 1.5 |  | --> | 0.19 | 0 | 0.034 | 0.177 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9065 | -9.7766
MV/LV Substation MU***603 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.168 | 1.5 |  | --> | 0.19 | 0 | 0.005 | 0.191 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9063 | -9.7815
MV/LV Substation CA***610X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9814 | -10.0517
MV/LV Substation AC***611X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.078 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9716 | -10.1033
MV/LV Substation CA***613X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9527 | -9.9706
MV/LV Substation PR***618X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 1.5 |  | --> | 0.095 | 0 | 0.015 | 0.086 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9289 | -9.929
MV/LV Substation MU***650X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9057 | -9.7445
MV/LV Substation RO***652X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 1.5 |  | --> | 0.095 | 0 | 0.005 | 0.092 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9029 | -9.7234
MV/LV Substation AR***684X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9773 | -9.9868
MV/LV Substation DO***690X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0097 | -10.0276
MV/LV Substation AC***697 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.027 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.104 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9329 | -9.9188
MV/LV Substation AC***698 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.299 | 1.5 |  | --> | 0.38 | 0 | 0.049 | 0.357 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9317 | -9.9237
MV/LV Substation DO***707X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9748 | -10.1152
MV/LV Substation MU***708X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.5 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9062 | -9.7839
MV/LV Substation SL***712X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.181 | 1.5 |  | --> | 0.19 | 0 | 0.01 | 0.185 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0064 | -10.0298
MV/LV Substation BU***717X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9792 | -9.981
MV/LV Substation AS***723X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9105 | -9.9665
MV/LV Substation B ***724X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9814 | -10.0022
MV/LV Substation BA***746X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9731 | -9.737
MV/LV Substation CA***747 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.958 | -9.9688
MV/LV Substation BC***747X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.097 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9706 | -9.7384
MV/LV Substation MU***754X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9049 | -9.766
MV/LV Substation LE***757X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0094 | -9.9911
MV/LV Substation VA***762 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0131 | -9.9708
MV/LV Substation DU***771X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0096 | -10.0244
MV/LV Substation CA***792 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 1.5 |  | --> | 0.095 | 0 | 0.005 | 0.093 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9791 | -10.0497
MV/LV Substation SA***794 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9771 | -10.073
MV/LV Substation KE***799 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.033 | 1.5 |  | --> | 0.095 | 0 | 0.004 | 0.101 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9754 | -10.0824
MV/LV Substation KE***800 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.052 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.101 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.975 | -10.0855
MV/LV Substation KE***802 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.974 | -10.0907
MV/LV Substation PU***804 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9647 | -10.0985
MV/LV Substation PO***805 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9725 | -10.1044
MV/LV Substation DO***813 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 1.5 |  | --> | 0.095 | 0 | 0.004 | 0.094 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9744 | -10.1339
MV/LV Substation DO***814 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.078 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.973 | -10.1379
MV/LV Substation CO***817 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.022 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.051 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9712 | -10.1621
MV/LV Substation DO***821 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 1.5 |  | --> | 0.095 | 0 | 0.005 | 0.092 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9282 | -10.0193
MV/LV Substation BU***861 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9718 | -9.9847
MV/LV Substation DO***873 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.153 | 1.5 |  | --> | 0.19 | 0 | 0.006 | 0.192 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9753 | -10.1289
MV/LV Substation BU***883 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.162 | 1.5 |  | --> | 0.19 | 0 | 0 | 0.195 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9716 | -9.9822
MV/LV Substation MA***921 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 1.5 |  | --> | 0.095 | 0 | 0.01 | 0.089 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9784 | -9.9844
MV/LV Substation ST***4002 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E18 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3394 | -6.4634
MV/LV Substation TO***001X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0072 | -7.4903
MV/LV Substation AL***004X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9899 | -7.4176
MV/LV Substation KI***4005 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9787 | -7.4176
MV/LV Substation MO***4014 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0595 | -7.4035
MV/LV Substation MO***402 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =99 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.017 | -7.4788
MV/LV Substation HA***4025 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.152 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =196 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0378 | -7.3862
MV/LV Substation CA***4026 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.69 |  | --> | 0.048 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9943 | -7.5209
MV/LV Substation PO***4030 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.69 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =600 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0528 | -7.4039
MV/LV Substation GA***4031 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9773 | -7.435
MV/LV Substation PO***4036 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9876 | -7.4687
MV/LV Substation GO***4037 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9769 | -7.5279
MV/LV Substation TO***4038 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9631 | -7.4299
MV/LV Substation HE***4064 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.386 | 1.69 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =382 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9958 | -7.5104
MV/LV Substation DR***4065 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0671 | -7.3468
MV/LV Substation BO***4066 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.056 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =101 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0171 | -7.4765
MV/LV Substation PU***4067 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9647 | -7.5677
MV/LV Substation TO***4090 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0073 | -7.488
MV/LV Substation DO***410 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.15 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =197 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0139 | -7.4211
MV/LV Substation MU***414 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0319 | -7.4794
MV/LV Substation MU***423 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.69 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0236 | -7.4892
MV/LV Substation O ***428 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0219 | -7.5132
MV/LV Substation MO***434 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 1.69 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0307 | -7.4579
MV/LV Substation MO***436 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 1.69 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0328 | -7.4518
MV/LV Substation GR***439 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0416 | -7.4407
MV/LV Substation IN***442 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =99 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.051 | -7.4437
MV/LV Substation AN***444 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.13 | 1.69 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =191 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0393 | -7.4347
MV/LV Substation BU***445 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 1.69 |  | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0398 | -7.428
MV/LV Substation LI***456 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0424 | -7.4086
MV/LV Substation BR***458 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.012 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =214 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0418 | -7.3824
MV/LV Substation NA***460 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.025 | 1.69 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.036 | -7.3819
MV/LV Substation SE***463 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.167 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =194 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0373 | -7.3844
MV/LV Substation PE***464 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.124 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =200 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0392 | -7.3761
MV/LV Substation HO***467 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0372 | -7.3715
MV/LV Substation BA***480 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0538 | -7.4004
MV/LV Substation CU***482 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.073 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =99 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0553 | -7.4017
MV/LV Substation BU***485 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.114 | 1.69 |  | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =195 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.059 | -7.4043
MV/LV Substation SE***486 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =98 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0592 | -7.4014
MV/LV Substation PU***497 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0636 | -7.3745
MV/LV Substation FI***500 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0708 | -7.3684
MV/LV Substation BL***507 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.192 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =191 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0712 | -7.3467
MV/LV Substation R.***515 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.165 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =195 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9987 | -7.4003
MV/LV Substation K/***520 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9841 | -7.4191
MV/LV Substation GR***526 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.05 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =102 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9798 | -7.4471
MV/LV Substation GA***527 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9758 | -7.4356
MV/LV Substation CL***528 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =56 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9696 | -7.4423
MV/LV Substation IN***540 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.69 |  | --> | 0.95 | 0 | 0.12 | 0 | 0 | Constrained, otherwise capacity available =868 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9951 | -7.474
MV/LV Substation CA***545 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9974 | -7.4912
MV/LV Substation PO***548 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.125 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =200 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9994 | -7.5025
MV/LV Substation WO***550 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.256 | 1.69 |  | --> | 0.38 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =390 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9967 | -7.5059
MV/LV Substation CO***551 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.144 | 1.69 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =194 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9979 | -7.51
MV/LV Substation DO***555 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.396 | 1.69 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =381 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9955 | -7.5154
MV/LV Substation WE***556 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.257 | 1.69 |  | --> | 0.38 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =386 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9961 | -7.5174
MV/LV Substation CO***572 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 1.69 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.984 | -7.5337
MV/LV Substation SH***635 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9957 | -7.4423
MV/LV Substation BU***649 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0054 | -7.4839
MV/LV Substation HA***650 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0683 | -7.3818
MV/LV Substation GL***652 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.055 | 1.69 |  | --> | 0.095 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =64 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9992 | -7.4858
MV/LV Substation GA***655 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.189 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =191 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9807 | -7.4188
MV/LV Substation FA***668 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9942 | -7.442
MV/LV Substation KI***671 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.078 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =98 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9817 | -7.4098
MV/LV Substation TO***681 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9894 | -7.4222
MV/LV Substation BR***683 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.129 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =200 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0444 | -7.382
MV/LV Substation TO***709 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9654 | -7.4299
MV/LV Substation DU***711 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.69 |  | --> | 0.048 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =35 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9543 | -7.4211
MV/LV Substation KI***760 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9869 | -7.5543
MV/LV Substation RO***765 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.014 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =52 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9779 | -7.5543
MV/LV Substation VE***766 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.69 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9757 | -7.5743
MV/LV Substation MU***768 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9731 | -7.5845
MV/LV Substation MI***769 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9701 | -7.5834
MV/LV Substation FA***770 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.966 | -7.587
MV/LV Substation PO***772 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9715 | -7.5641
MV/LV Substation LA***783 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.392 | 1.69 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =381 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9529 | -7.5721
MV/LV Substation HA***824 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0397 | -7.4175
MV/LV Substation KI***831 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.237 | 1.69 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =393 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9797 | -7.4104
MV/LV Substation RO***832 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9972 | -7.4956
MV/LV Substation TO***842 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.396 | 1.69 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9801 | -7.4167
MV/LV Substation CA***850 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9959 | -7.5124
MV/LV Substation SE***859 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =98 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0393 | -7.3756
MV/LV Substation ST***864 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.035 | 1.69 |  | --> | 0.095 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0392 | -7.3808
MV/LV Substation CO***866 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 1.69 |  | --> | 0.095 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9995 | -7.5022
MV/LV Substation GA***888 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =50 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.065 | -7.3694
MV/LV Substation BR***893 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.144 | 1.69 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =194 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0393 | -7.3795
MV/LV Substation FI***894 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.059 | 1.69 |  | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =96 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0318 | -7.4531
MV/LV Substation BI***905 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0468 | -7.3755
MV/LV Substation HA***911 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.355 | 1.69 |  | --> | 0.38 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9971 | -7.5017
MV/LV Substation KE***916 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.093 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =204 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9978 | -7.5137
MV/LV Substation BL***918 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 1.69 |  | --> | 0.048 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.007 | -7.4929
MV/LV Substation MO***936 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 1.69 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =100 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9932 | -7.5242
MV/LV Substation GO***939 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.134 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =199 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9773 | -7.5301
MV/LV Substation GR***956 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.152 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =196 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.054 | -7.4053
MV/LV Substation BR***959 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.14 | 1.69 |  | --> | 0.19 | 0 | 0.065 | 0 | 0 | Constrained, otherwise capacity available =150 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0423 | -7.3776
MV/LV Substation BA***984 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0549 | -7.3982
MV/LV Substation LI***002 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C11 ex OLDTOWN |  |  |  | 53.0189 | -7.2985
MV/LV Substation RA***003 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C16 ex MEELICK |  |  |  | 53.0194 | -7.298
MV/LV Substation DR***006 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C12 ex OLDTOWN |  |  |  | 53.0189 | -7.2989
MV/LV Substation CO***018 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C18 ex MEELICK |  |  |  | 53.0192 | -7.2966
MV/LV Substation ST***020 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C16 ex MEELICK |  |  |  | 53.0192 | -7.2975
MV/LV Substation OD***021 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C16 ex MEELICK |  |  |  | 53.019 | -7.2963
MV/LV Substation BO***022 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C16 ex MEELICK |  |  |  | 53.0193 | -7.2964
MV/LV Substation AR***025 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex OLDTOWN |  |  |  | 53.0195 | -7.2983
MV/LV Substation CO***028 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex OLDTOWN |  |  |  | 53.0192 | -7.2993
MV/LV Substation RO***029 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex MEELICK |  |  |  | 53.0189 | -7.2962
MV/LV Substation PR***030 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C18 ex MEELICK |  |  |  | 53.0199 | -7.2968
MV/LV Substation NY***101 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5465 | -9.269
MV/LV Substation LI***104 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.05 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5406 | -9.2679
MV/LV Substation LI***105 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5393 | -9.2705
MV/LV Substation CO***107 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E15 ex CONG |  |  |  | 53.5138 | -9.4481
MV/LV Substation CO***109 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5309 | -9.2744
MV/LV Substation LI***116 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5382 | -9.2721
MV/LV Substation CR***132 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 1.43 |  | --> | 0.048 | 0 | 0.01 | 0.042 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5407 | -9.2176
MV/LV Substation EB***150 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =97 kW | --> | E15 ex CONG |  |  |  | 53.5231 | -9.3772
MV/LV Substation CA***154 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5061 | -9.2158
MV/LV Substation DE***173 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E15 ex CONG |  |  |  | 53.5427 | -9.2816
MV/LV Substation CO***174 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =7 kVA | --> | 0.048 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E15 ex CONG |  |  |  | 53.5432 | -9.2871
MV/LV Substation CO***175 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =51 kVA | --> | 0.19 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E15 ex CONG |  |  |  | 53.5415 | -9.2862
MV/LV Substation CL***200 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex CONG |  |  |  | 53.5426 | -9.3075
MV/LV Substation RI***203 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex CONG |  |  |  | 53.5358 | -9.2924
MV/LV Substation AS***207 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =339 kVA | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | E15 ex CONG |  |  |  | 53.535 | -9.2865
MV/LV Substation DO***225 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =49 kW | --> | E15 ex CONG |  |  |  | 53.5262 | -9.3504
MV/LV Substation CL***238 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =194 kW | --> | E15 ex CONG |  |  |  | 53.5455 | -9.3659
MV/LV Substation TH***331 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =98 kW | --> | E15 ex CONG |  |  |  | 53.5269 | -9.3799
MV/LV Substation CO***375 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E15 ex CONG |  |  |  | 53.5109 | -9.4611
MV/LV Substation TE***376 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex CONG |  |  |  | 53.508 | -9.4604
MV/LV Substation CO***377 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =396 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E15 ex CONG |  |  |  | 53.5111 | -9.4657
MV/LV Substation GA***378 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =26 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =51 kW | --> | E15 ex CONG |  |  |  | 53.5112 | -9.4665
MV/LV Substation CR***4005 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5391 | -9.2201
MV/LV Substation KI***4021 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 1.43 |  | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | E18 ex CONG | Cong [T421,T422] | CLOON |  | 53.5413 | -9.4024
MV/LV Substation NE***4038 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex CONG | Cong [T421,T422] | CLOON |  | 53.5753 | -9.2217
MV/LV Substation AS***4039 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E15 ex CONG |  |  |  | 53.5369 | -9.2834
MV/LV Substation KN***4060 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.078 | 1.43 |  | --> | 0.095 | 0 | 0.05 | 0.061 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5414 | -9.2431
MV/LV Substation CR***4069 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.062 | 1.43 |  | --> | 0.095 | 0 | 0.033 | 0.076 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5427 | -9.2143
MV/LV Substation LI***4075 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.43 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5356 | -9.2748
MV/LV Substation AR***4079 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex CONG |  |  |  | 53.5325 | -9.3396
MV/LV Substation CR***4087 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.43 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5422 | -9.2122
MV/LV Substation RA***432 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex CONG |  |  |  | 53.5269 | -9.619
MV/LV Substation CN***433 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex CONG |  |  |  | 53.5283 | -9.6274
MV/LV Substation CO***493 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 1.43 |  | --> | 0.095 | 0 | 0 | 0.098 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5322 | -9.2678
MV/LV Substation CO***503 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =396 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E15 ex CONG |  |  |  | 53.5364 | -9.3091
MV/LV Substation BO***512 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex CONG |  |  |  | 53.5115 | -9.4687
MV/LV Substation MA***516 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex CONG |  |  |  | 53.516 | -9.5605
MV/LV Substation ST***535 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.106 | 1.43 |  | --> | 0.19 | 0 | 0.01 | 0.195 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5352 | -9.2734
MV/LV Substation CO***542X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5171 | -9.2122
MV/LV Substation CD***549 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.165 | 1.43 |  | --> | 0.19 | 0 | 0 | 0.195 | 0 |  | --> | E18 ex CONG | Cong [T421,T422] | CLOON |  | 53.5401 | -9.4552
MV/LV Substation RU***566X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex CONG | Cong [T421,T422] | CLOON |  | 53.5451 | -9.3519
MV/LV Substation CU***577X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5418 | -9.2648
MV/LV Substation CO***580X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex CONG |  |  |  | 53.5142 | -9.452
MV/LV Substation NE***608X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex CONG | Cong [T421,T422] | CLOON |  | 53.5699 | -9.2326
MV/LV Substation CR***723X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5047 | -9.2202
MV/LV Substation WO***735X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.184 | 1.43 |  | --> | 0.19 | 0 | 0 | 0.192 | 0 |  | --> | E18 ex CONG | Cong [T421,T422] | CLOON |  | 53.5441 | -9.3624
MV/LV Substation NY***743X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex CONG |  |  |  | 53.5478 | -9.2825
MV/LV Substation EI***797X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 1.43 |  | --> | 0.095 | 0 | 0 | 0.096 | 0 |  | --> | E18 ex CONG | Cong [T421,T422] | CLOON |  | 53.5464 | -9.359
MV/LV Substation MA***799X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex CONG |  |  |  | 53.5177 | -9.5633
MV/LV Substation IN***864X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E16 ex CONG | Cong [T421,T422] | CLOON |  | 53.5836 | -9.3181
MV/LV Substation DO***865X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex CONG |  |  |  | 53.5304 | -9.3658
MV/LV Substation LA***866X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.049 | 0 |  | --> | E16 ex CONG | Cong [T421,T422] | CLOON |  | 53.5829 | -9.2607
MV/LV Substation LI***880X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 1.43 |  | --> | 0.048 | 0 | 0.005 | 0.044 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5394 | -9.2691
MV/LV Substation LY***886X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.43 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5342 | -9.2444
MV/LV Substation MC***901X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E15 ex CONG |  |  |  | 53.5453 | -9.2913
MV/LV Substation GR***001 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =360 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =385 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.2942 | -6.4731
MV/LV Substation GR***003 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =558 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =608 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.296 | -6.4691
MV/LV Substation GR***004 |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =845 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =971 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.2959 | -6.4729
MV/LV Substation GR***005 |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =867 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =968 kW | --> | E60 ex GRANGE CASTLE |  |  |  | 53.2993 | -6.4634
MV/LV Substation GR***006 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =570 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =607 kW | --> | E60 ex GRANGE CASTLE |  |  |  | 53.2987 | -6.4703
MV/LV Substation AE***007 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =533 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =612 kW | --> | E60 ex GRANGE CASTLE |  |  |  | 53.2941 | -6.466
MV/LV Substation AE***008 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =521 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =613 kW | --> | E60 ex GRANGE CASTLE |  |  |  | 53.2911 | -6.4652
MV/LV Substation AE***009 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =538 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =611 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.2921 | -6.4683
MV/LV Substation AE***010 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =304 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =642 kW | --> | E60 ex GRANGE CASTLE |  |  |  | 53.2909 | -6.4653
MV/LV Substation GR***011 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =606 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =602 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.298 | -6.4691
MV/LV Substation GR***012 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =307 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =393 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.293 | -6.4739
MV/LV Substation JO***4002 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =311 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =392 kW | --> | E60 ex GRANGE CASTLE |  |  |  | 53.2912 | -6.4743
MV/LV Substation AE***4004 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =559 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =608 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.2948 | -6.4661
MV/LV Substation AE***4005 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =581 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =605 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.2919 | -6.4679
MV/LV Substation JO***4007 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =222 kVA | --> | 0.38 | 0 | 0.1 | 0 | 0 | Constrained, otherwise capacity available =323 kW | --> | E60 ex GRANGE CASTLE |  |  |  | 53.289 | -6.4683
MV/LV Substation AE***4009 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =180 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =605 kW | --> | E60 ex GRANGE CASTLE |  |  |  | 53.2936 | -6.4634
_ESB Networks Capacity Heat Map Publication. HV Load data from revenue metering Jan2025 and Special Load Readings winter 2024/2025. Generation and demand commitments up to 08 Oct 2025. | _HV header | Report compiled 12/12/2025 | _ |  |  | 0 | --> | 0 | 0 | 0 |  | --> | 0 | 0 | 0 | 0 | 0 |  | -->
FOXHOLE (621000) 38 kV STATION | Foxhole [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 10.1 | 0 | 0 | Constrained, otherwise capacity available =5.28 MW | --> |  | Dungarvan [T141,T142] | DUNGARVAN |  | 51.9759 | -7.855
RATHDOWNEY (391000) 38 kV STATION | Rathdowney [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 | Constrained, otherwise capacity available =0.04 MVA | --> | 4.8 | 0 | 1 | 0 | 0 | Constrained, otherwise capacity available =4.62 MW | --> |  | Ikerrin [T141] | IKERRIN |  | 52.8498 | -7.5926
BISHOPSTOWN (254000) 38 kV STATION | Bishopstown [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 4.1 | 11 | 4.852 |  | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.8918 | -8.5522
BLAKE (120000) 110 kV STATION | Blake [T41,T42] | 110 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 7 | 0.7 | 2.439 |  | --> |  | Blake [T142] | BLAKE |  | 53.2952 | -6.8636
BALLYCOOLIN (514000) 38 kV STATION | Ballycoolin [T41,T42,T43] | 38 kV | _ | MV | 3x10 MVA @ 10 kV | 30 | --> | 27 | 0 | 0 |  | --> | 28.5 | 4.75 | 2.1 | 33.2 | 4.899 |  | --> |  | Finglas [T143,T144] | FINGLAS |  | 53.4024 | -6.3597
TRAMORE (032000) 38 kV STATION | Tramore [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =0.84 MVA | --> | 12.4 | 4.75 | 13.4 | 0 | 0 | Constrained, otherwise capacity available =1.34 MW | --> |  | Butlerstown [T141,T142] | BUTLERSTOWN |  | 52.1603 | -7.1467
BALLYBODEN (198000) 38 kV STATION | Ballyboden [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 6.1 | 8.9 | 4.844 |  | --> |  | Cookstown [T141,T142] | COOKSTOWN |  | 53.2821 | -6.2837
CAHERDAVIN (098000) 38 kV STATION | Caherdavin [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =2.71 MVA | --> | 12.4 | 4.75 | 2.5 | 11.7 | 4.795 |  | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.6639 | -8.6494
DRUMCONDRA (344000) 38 kV STATION | Drumcondra [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =5.15 MVA | --> | 12.4 | 4.75 | 0.5 | 13.8 | 4.797 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | MCDERMOTT |  | 53.3609 | -6.2538
CAHIRCALLA (186000) 38 kV STATION | Cahircalla [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 3 | 2.7 | 2.437 | Constrained, otherwise capacity available =4.65 MW | --> |  | Ennis [T141,T142] | ENNIS |  | 52.8271 | -8.9999
SCARIFF (229000) 38 kV STATION | Scariff [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 |  | --> | 4.8 | 0 | 1.8 | 2.7 | 0 | Constrained, otherwise capacity available =3.65 MW | --> |  | Ennis [T141,T142] | ENNIS |  | 52.9016 | -8.5292
CAPPAMORE (152000) 38 kV STATION | Cappamore [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 6.6 | 0.9 | 2.421 |  | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.6179 | -8.3228
CAPPAMORE (152000) 38 kV STATION | Cappamore [T424] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =8.91 MVA | --> | 9.5 | 0 | 7.5 | 2.3 | 0 |  | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.6179 | -8.3228
CARRIGSHANE (459000) 38 kV STATION | Carrigshane [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =5.99 MVA | --> | 9.5 | 0 | 1.1 | 8.8 | 0 |  | --> |  | Midleton [T141] | MIDLETON |  | 51.9116 | -8.1493
TERMONFECKIN ROAD (263000) 38 kV STATION | Termonfeckin Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 6.6 | 1.5 | 2.499 |  | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.7295 | -6.3184
BLESSINGTON (430000) 38 kV STATION | Blessington [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 18 | 0 | 0 | Constrained, otherwise capacity available =7.03 MVA | --> | 19 | 4.75 | 15.8 | 5.1 | 4.777 | Constrained, otherwise capacity available =5.41 MW | --> |  | Kilteel [T141,T142] | KILTEEL |  | 53.1918 | -6.5168
BALBRIGGAN (065000) 38 kV STATION | Balbriggan [T42] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =5.96 MVA | --> | 9.5 | 0 | 0.2 | 9.9 | 0 |  | --> |  | Glasmore [T141,T142] | GLASMORE |  | 53.6076 | -6.1858
ADAMSTOWN (497000) 110 kV STATION | Adamstown [T121,T122] | 110 kV | _ | MV | 2x20 MVA @ 20 kV | 40 | --> | 30 | 0 | 0 | Constrained, otherwise capacity available =16.39 MVA | --> | 24.7 | 9.5 | 4.1 | 24.5 | 9.595 |  | --> |  | Inchicore County 220/110 kV [T2101,T2106] | INCHICORE 220KV |  | 53.3485 | -6.4623
ASHBOURNE (335000) 38 kV STATION | Ashbourne [T421,T422] | 38 kV | _ | MV | 1x10,1x15 MVA @ 20 kV | 25 | --> | 18.75 | 0 | 0 |  | --> | 12.4 | 7.125 | 13.2 | 3 | 7.459 |  | --> |  | Finglas [T143,T144] | FINGLAS |  | 53.4828 | -6.3871
WHITESTOWN (423000) 38 kV STATION | Whitestown [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =5.25 MVA | --> | 12.4 | 4.75 | 1.2 | 12.4 | 4.769 |  | --> |  | Cookstown [T141,T142] | COOKSTOWN |  | 53.2802 | -6.3801
WHITEHALL (183000) 38 kV STATION | Whitehall [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =1.68 MVA | --> | 9.5 | 0 | 1.9 | 8.9 | 0 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | FINGLAS |  | 53.3782 | -6.2569
WHITECHURCH (167000) 38 kV STATION | Whitechurch [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =1.09 MVA | --> | 12.4 | 4.75 | 9.1 | 6 | 4.849 |  | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.9901 | -8.4998
ATHENRY (142000) 38 kV STATION | Athenry [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 2.4 | 5.1 | 2.422 |  | --> |  | Galway 110kv [T141,T142] | GALWAY 110KV |  | 53.2785 | -8.719
ATHENRY (142000) 38 kV STATION | Athenry [T423] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =2.4 MVA | --> | 9.5 | 0 | 3.3 | 7.5 | 0 |  | --> |  | Galway 110kv [T141,T142] | GALWAY 110KV |  | 53.2785 | -8.719
ATHGARVAN (394000) 38 kV STATION | Athgarvan [T41,T44] | 38 kV | _ | MV | 2x15 MVA @ 10 kV | 30 | --> | 22.5 | 0 | 0 |  | --> | 18.5 | 7.125 | 7.4 | 15.3 | 7.32 | Constrained, otherwise capacity available =15.59 MW | --> |  | Newbridge [T141,T142] | NEWBRIDGE |  | 53.1648 | -6.7899
TULLA (182000) 38 kV STATION | Tulla [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 3.75 | 0 | 0 |  | --> | 3.1 | 1.1875 | 1.6 | 2.4 | 1.246 |  | --> |  | Ennis [T141,T142] | ENNIS |  | 52.8543 | -8.7626
WATERFORD IND EST (348000) 38 kV STATION | Waterford Ind Est [T41,T42,T44] | 38 kV | _ | MV | 3x10 MVA @ 10 kV | 30 | --> | 27 | 0 | 0 | Constrained, otherwise capacity available =12.9 MVA | --> | 28.5 | 4.75 | 0.8 | 0 | 0 | Constrained, otherwise capacity available =32.39 MW | --> |  | Butlerstown [T141,T142] | BUTLERSTOWN |  | 52.2426 | -7.1558
TOGHER (336000) 38 kV STATION | Togher [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =3.24 MVA | --> | 12.4 | 4.75 | 2.3 | 12.7 | 4.848 |  | --> |  | Trabeg [T141,T142] | TRABEG |  | 51.8827 | -8.5056
BALGADDY (623000) 38 kV STATION | Balgaddy [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =2.54 MVA | --> | 12.4 | 4.75 | 2.5 | 12.2 | 4.825 |  | --> |  | Grange Castle [T141] | GRANGE CASTLE |  | 53.328 | -6.4495
BALLINACURRA (126000) 38 kV STATION | Ballinacurra [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 11.25 | 0 | 0 | Constrained, otherwise capacity available =2.65 MVA | --> | 6.2 | 4.75 | 1.3 | 6.8 | 4.939 |  | --> |  | Limerick [T141,T142] | LIMERICK |  | 52.6525 | -8.6293
BALLINCOLLIG (341000) 38 kV STATION | Ballincollig [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =7.51 MVA | --> | 12.4 | 4.75 | 3.1 | 10.5 | 4.769 |  | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.8753 | -8.6135
UNIDARE (245000) 38 kV STATION | Unidare [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 0.9 | 13.6 | 4.808 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | FINGLAS |  | 53.3995 | -6.3031
TYMON (424000) 38 kV STATION | Tymon [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =1.42 MVA | --> | 12.4 | 4.75 | 2.9 | 11.9 | 4.835 |  | --> |  | Cookstown [T141,T142] | COOKSTOWN |  | 53.2972 | -6.3369
BALLINCOLLIG (341000) 38 kV STATION | Ballincollig [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =9 MVA | --> | 9.5 | 0 | 0 | 9.5 | 0 |  | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.8753 | -8.6135
BALLINCOLLIG (341000) 38 kV STATION | Ballincollig [T422] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =9 MVA | --> | 9.5 | 0 | 0 | 9.5 | 0 |  | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.8753 | -8.6135
BALLINROBE (238000) 38 kV STATION | Ballinrobe [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =5.21 MVA | --> | 12.4 | 4.75 | 2.5 | 12.1 | 4.816 |  | --> |  | Dalton [T142] | DALTON |  | 53.6351 | -9.1986
BALBRIGGAN (065000) 38 kV STATION | Balbriggan [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =8.84 MVA | --> | 9.5 | 0 | 0.1 | 9.4 | 0 |  | --> |  | Glasmore [T141,T142] | GLASMORE |  | 53.6076 | -6.1858
SLANE (208000) 38 kV STATION | Slane [T422] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =9 MVA | --> | 9.5 | 0 | 0 | 9.5 | 0 |  | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.7558 | -6.5442
COLLINSTOWN (267000) 38 kV STATION | Collinstown [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =5.21 MVA | --> | 6.2 | 2.375 | 0 | 7 | 2.392 |  | --> |  | Grange (dr) [T141,T142] | GRANGE (DR) |  | 53.4222 | -6.2216
SPRINGS (585000) 38 kV STATION | Springs [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =8.09 MVA | --> | 12.4 | 4.75 | 11.5 | 0 | 0 | Constrained, otherwise capacity available =3.37 MW | --> |  | Dungarvan [T141,T142] | DUNGARVAN |  | 52.0866 | -7.6482
CRATLOE (273000) 38 kV STATION | Cratloe [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =0.54 MVA | --> | 6.2 | 2.375 | 2.8 | 4.7 | 2.429 |  | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.7015 | -8.7607
CRANNY (582000) 38 kV STATION | Cranny [T41] | 38 kV | _ | MV | 1x2 MVA @ 10 kV | 2 | --> | 1.8 | 0 | 0 | Constrained, otherwise capacity available =0.6 MVA | --> | 1.9 | 0 | 0.4 | 1.7 | 0 |  | --> |  | Ennis [T141,T142] | ENNIS |  | 52.6971 | -9.2202
CORBALLY (195000) 38 kV STATION | Corbally [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =0.99 MVA | --> | 6.2 | 2.375 | 1.2 | 6.3 | 2.419 |  | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.6735 | -8.6203
CLARKSTOWN (620000) 38 kV STATION | Clarkstown [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 | Constrained, otherwise capacity available =4.47 MVA | --> | 4.8 | 0 | 0 | 2.6 | 0 | Constrained, otherwise capacity available =4.76 MW | --> |  | Griffinrath [T141,T142] | GRIFFINRATH |  | 53.4525 | -6.6902
SLANE (208000) 38 kV STATION | Slane [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =1.51 MVA | --> | 9.5 | 0 | 9.2 | 1.8 | 0 |  | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.7558 | -6.5442
STEPHENSTOWN (730000) 110 kV STATION | Stephenstown [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | 0 | Constrained, otherwise capacity available =13.21 MVA | --> | 24.7 | 9.5 | 15 | 12.9 | 9.563 |  | --> |  | Finglas Rural TSO 220/110 kV [T2101,T2106] | FINGLAS |  | 53.6057 | -6.1974
CLONSHAUGH (411000) 38 kV STATION | Clonshaugh [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =7.12 MVA | --> | 12.4 | 4.75 | 0.2 | 13.7 | 4.778 |  | --> |  | Finglas [T143,T144] | FINGLAS |  | 53.4072 | -6.2262
CLOONLOUGH (369000) 38 kV STATION | Cloonlough [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =1.12 MVA | --> | 6.2 | 2.375 | 2.3 | 0 | 0 | Constrained, otherwise capacity available =5.31 MW | --> |  | Barrymore [T141] | BARRYMORE |  | 52.2556 | -8.2695
TEMPLEMORE (057000) 38 kV STATION | Templemore [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =7.06 MVA | --> | 12.4 | 4.75 | 2.3 | 0 | 0 | Constrained, otherwise capacity available =11.43 MW | --> |  | Ikerrin [T141] | IKERRIN |  | 52.7898 | -7.8383
COOLCARRON (234000) 38 kV STATION | Coolcarron [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0 | 0 |  | --> | 1.2 | 1.1875 | 1.2 | 0 | 0 | Constrained, otherwise capacity available =0.59 MW | --> |  | Barrymore [T141] | BARRYMORE |  | 52.133 | -8.2814
COOKSTOWN (672000) 110 kV STATION | Cookstown [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | 0 | Constrained, otherwise capacity available =20.1 MVA | --> | 77.8 | 0 | 24 | 67.6 | 0 |  | --> |  | Inchicore County 220/110 kV [T2101,T2106] | INCHICORE 220KV |  | 53.2947 | -6.3826
COLLIGAN (516000) 38 kV STATION | Colligan [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =4.69 MVA | --> | 12.4 | 4.75 | 2.3 | 0 | 0 | Constrained, otherwise capacity available =11.93 MW | --> |  | Dungarvan [T141,T142] | DUNGARVAN |  | 52.0906 | -7.6179
COOLMINE (407000) 38 kV STATION | Coolmine [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 5.4 | 10.5 | 4.945 |  | --> |  | Finglas [T143,T144] | FINGLAS |  | 53.3768 | -6.4167
SWORDS (066000) 38 kV STATION | Swords [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =1.29 MVA | --> | 12.4 | 4.75 | 3.1 | 13.4 | 5.061 |  | --> |  | Glasmore [T141,T142] | GLASMORE |  | 53.4613 | -6.2256
DALTON (909000) 110 kV STATION | Dalton [T421,T422] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =4.01 MVA | --> | 12.4 | 4.75 | 11.9 | 2.7 | 4.813 |  | --> |  | Dalton [T142] | DALTON |  | 53.7163 | -8.9756
CURRALEIGH (450000) 38 kV STATION | Curraleigh [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 7.6 | 0 | 2.438 |  | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.912 | -8.6593
CASTLEKNOCK (154000) 38 kV STATION | Castleknock [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =3.42 MVA | --> | 6.2 | 2.375 | 2.3 | 4.6 | 2.388 |  | --> |  | Finglas [T143,T144] | FINGLAS |  | 53.3624 | -6.3628
SEMPERIT (360000) 38 kV STATION | Semperit [T41,T42,T43] | 38 kV | _ | MV | 3x10 MVA @ 10 kV | 30 | --> | 27 | 0 | 0 |  | --> | 28.5 | 4.75 | 2.1 | 31.8 | 4.838 |  | --> |  | Grange Castle [T141] | GRANGE CASTLE |  | 53.3359 | -6.3539
CASTLELYONS (455000) 38 kV STATION | Castlelyons [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =0.45 MVA | --> | 6.2 | 2.375 | 1.8 | 0 | 0 | Constrained, otherwise capacity available =5.3 MW | --> |  | Barrymore [T141] | BARRYMORE |  | 52.0798 | -8.2327
CLONDALKIN (072000) 38 kV STATION | Clondalkin [T41,T42,T44] | 38 kV | _ | MV | 3x10 MVA @ 10 kV | 30 | --> | 27 | 0 | 0 | Constrained, otherwise capacity available =1.25 MVA | --> | 28.5 | 4.75 | 5.3 | 28 | 4.816 |  | --> |  | Inchicore 220kv [T144,T145] | INCHICORE 220KV |  | 53.3206 | -6.3859
CASTLETROY (558000) 38 kV STATION | Castletroy [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 2.3 | 5.8 | 2.502 |  | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.6786 | -8.5636
CLOYNE (232000) 38 kV STATION | Cloyne [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 |  | --> | 4.8 | 0 | 6.9 | 0 | 0 |  | --> |  | Midleton [T141] | MIDLETON |  | 51.8695 | -8.1197
CELBRIDGE (016000) 38 kV STATION | Celbridge [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 4.6 | 2.6 | 2.635 | Constrained, otherwise capacity available =10.39 MW | --> |  | Griffinrath [T141,T142] | GRIFFINRATH |  | 53.3409 | -6.5446
SUTTON (333000) 38 kV STATION | Sutton [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =1.63 MVA | --> | 12.4 | 4.75 | 4 | 10.5 | 4.81 |  | --> |  | Grange (dr) [T141,T142] | GRANGE (DR) |  | 53.3875 | -6.1215
CITYWEST (454000) 110 kV STATION | Citywest [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | 0 |  | --> | 24.7 | 9.5 | 1.4 | 30.6 | 9.939 |  | --> |  | Inchicore County 220/110 kV [T2101,T2106] | INCHICORE 220KV |  | 53.2916 | -6.4214
CLAREGALWAY (251000) 38 kV STATION | Claregalway [T42,T421] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 5.5 | 2.8 | 2.541 |  | --> |  | Galway 110kv [T141,T142] | GALWAY 110KV |  | 53.3678 | -8.9067
STICKILLEN (063000) 38 kV STATION | Stickillen [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =1.03 MVA | --> | 6.2 | 2.375 | 3.1 | 4.2 | 2.41 |  | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.8627 | -6.533
CURRAGLASS (586000) 38 kV STATION | Curraglass [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 | Constrained, otherwise capacity available =2.18 MVA | --> | 4.8 | 0 | 0.5 | 0 | 0 | Constrained, otherwise capacity available =4.53 MW | --> |  | Barrymore [T141] | BARRYMORE |  | 52.0896 | -8.0562
SHANNON (325000) 38 kV STATION | Shannon [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0.4 |  | --> | 12.4 | 4.75 | 0.4 | 14.9 | 4.875 |  | --> |  | Drumline [T141,T142] | DRUMLINE |  | 52.698 | -8.8964
DRUMLINE (629000) 110 kV STATION | Drumline [T421,T422] | 110 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0.4 |  | --> | 6.2 | 2.375 | 2.6 | 6.2 | 2.81 |  | --> |  | Drumline [T141,T142] | DRUMLINE |  | 52.7309 | -8.8496
RINEANNA (109000) 38 kV STATION | Rineanna [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.4 | 0.4 | Constrained, otherwise capacity available =1.05 MVA | --> | 12.4 | 4.75 | 1.6 | 13.8 | 4.879 |  | --> |  | Drumline [T141,T142] | DRUMLINE |  | 52.7096 | -8.8866
KILCULLEN (323000) 38 kV STATION | Kilcullen [T41,T42,T424] | 38 kV | _ | MV | 2x5,1x10 MVA @ 10 kV | 20 | --> | 18 | 0.6 | 0.6 | Constrained, otherwise capacity available =4.13 MVA | --> | 19 | 4.75 | 3.7 | 0 | 0 | Constrained, otherwise capacity available =16.07 MW | --> |  | Stratford [T141] | STRATFORD |  | 53.1216 | -6.7474
BALTINGLASS (294000) 38 kV STATION | Baltinglass [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0.6 |  | --> | 6.2 | 2.375 | 5.8 | 0 | 0 | Constrained, otherwise capacity available =2.31 MW | --> |  | Stratford [T141] | STRATFORD |  | 52.9404 | -6.6817
KILGARVAN (110000) 38 kV STATION | Kilgarvan [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.8 | 0.8 | Constrained, otherwise capacity available =2.38 MVA | --> | 4.8 | 0 | 1.7 | 3.7 | 0 |  | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 51.9092 | -9.4416
WOODFORD (276000) 38 kV STATION | Woodford [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.8 | 0.8 | Constrained, otherwise capacity available =2.99 MVA | --> | 12.4 | 4.75 | 3.5 | 7.2 | 4.844 | Constrained, otherwise capacity available =11.44 MW | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 52.0537 | -9.4547
COOLCORCORAN (020000) 38 kV STATION | Coolcorcoran [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0.8 |  | --> | 12.4 | 4.75 | 3.7 | 7.2 | 5.016 | Constrained, otherwise capacity available =12.54 MW | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 52.0758 | -9.5109
KENMARE (414000) 38 kV STATION | Kenmare [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.8 | 0.8 | Constrained, otherwise capacity available =2.04 MVA | --> | 4.8 | 0 | 1.1 | 4.4 | 0 |  | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 51.8856 | -9.5643
KENMARE (414000) 38 kV STATION | Kenmare [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.8 | 0.8 | Constrained, otherwise capacity available =1.96 MVA | --> | 4.8 | 0 | 0.7 | 4.6 | 0 |  | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 51.8856 | -9.5643
RATHMORE (221000) 38 kV STATION | Rathmore [T42,T421] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.8 | 0.8 | Constrained, otherwise capacity available =2.63 MVA | --> | 6.2 | 2.375 | 1.8 | 5.1 | 2.388 |  | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 52.0803 | -9.1908
BREWERY ROAD (773000) 38 kV STATION | Brewery Road [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.2 | 1.2 | Constrained, otherwise capacity available =2.9 MVA | --> | 12.4 | 4.75 | 2.4 | 12.8 | 4.86 |  | --> |  | Carrickmines [T141,T142] | CARRICKMINES |  | 53.283 | -6.1924
SANDYFORD (288000) 38 kV STATION | Sandyford [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 1.2 |  | --> | 12.4 | 4.75 | 4.5 | 10.4 | 4.841 |  | --> |  | Carrickmines [T141,T142] | CARRICKMINES |  | 53.2665 | -6.2258
DEANSGRANGE (001000) 38 kV STATION | Deansgrange [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.2 | 1.2 | Constrained, otherwise capacity available =5.35 MVA | --> | 12.4 | 4.75 | 3.3 | 10.8 | 4.785 |  | --> |  | Carrickmines [T141,T142] | CARRICKMINES |  | 53.2716 | -6.1525
CARRICKMINES (649000) 220 kV STATION | Carrickmines [T41,T42] | 220 kV | _ | MV | 1x10,1x15 MVA @ 10 kV | 25 | --> | 18.75 | 0 | 1.2 |  | --> | 12.4 | 7.125 | 7 | 8.4 | 7.315 |  | --> |  | Carrickmines [T141,T142] | CARRICKMINES |  | 53.2549 | -6.1921
LOUGHLINSTOWN (199000) 38 kV STATION | Loughlinstown [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 1.2 |  | --> | 12.4 | 4.75 | 2.9 | 12.3 | 4.871 |  | --> |  | Carrickmines [T141,T142] | CARRICKMINES |  | 53.2528 | -6.1374
MOUNT MERRION (101000) 38 kV STATION | Mount Merrion [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.2 | 1.2 | Constrained, otherwise capacity available =2.51 MVA | --> | 12.4 | 4.75 | 3.3 | 11.2 | 4.806 |  | --> |  | Carrickmines [T141,T142] | CARRICKMINES |  | 53.2994 | -6.2114
DONEGAL (149000) 38 kV STATION | Donegal [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 1.6 |  | --> | 6.2 | 2.375 | 34.6 | 0 | 0 |  | --> |  | Cathaleens Fall [T141] | CATHALEENS FALL |  | 54.6538 | -8.0773
BALLYSHANNON (108000) 38 kV STATION | Ballyshannon [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.6 | 1.6 | Constrained, otherwise capacity available =2.23 MVA | --> | 6.2 | 2.375 | 2 | 0 | 0 | Constrained, otherwise capacity available =5.34 MW | --> |  | Cathaleens Fall [T141] | CATHALEENS FALL |  | 54.499 | -8.2003
BUNDORAN (350000) 38 kV STATION | Bundoran [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.6 | 1.6 | Constrained, otherwise capacity available =2.7 MVA | --> | 6.2 | 2.375 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =6.05 MW | --> |  | Cathaleens Fall [T141] | CATHALEENS FALL |  | 54.4694 | -8.2598
BALLYCONRA (479000) 38 kV STATION | Ballyconra [T423] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 8.7 | 10.3 |  | --> | 9.5 | 0 | 9.2 | 0.6 | 0 |  | --> |  | Ballyragget [T141] | BALLYRAGGET |  | 52.7979 | -7.3452
CASTLECOMER (144000) 38 kV STATION | Castlecomer [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 10.3 |  | --> | 6.2 | 2.375 | 6.2 | 1.2 | 2.412 |  | --> |  | Ballyragget [T141] | BALLYRAGGET |  | 52.8442 | -7.1771
BALLYRAGGET (329000) 38 kV STATION | Ballyragget [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 2.8 | 10.3 |  | --> | 6.2 | 2.375 | 1.8 | 5.2 | 2.394 |  | --> |  | Ballyragget [T141] | BALLYRAGGET |  | 52.7962 | -7.3349
BALLYHALE (010000) 38 kV STATION | Ballyhale [T42,T421] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 10.4 |  | --> | 6.2 | 2.375 | 3.2 | 4.4 | 2.436 |  | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.4755 | -7.181
GORESBRIDGE (247000) 38 kV STATION | Goresbridge [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 10.4 |  | --> | 6.2 | 2.375 | 5 | 2.3 | 2.414 |  | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.6397 | -6.9995
GRAIGUENAMANAGH (382000) 38 kV STATION | Graiguenamanagh [T41,T42] | 38 kV | _ | MV | 2x2 MVA @ 10 kV | 4 | --> | 3 | 0 | 10.4 |  | --> | 2.5 | 0.95 | 1.4 | 1.7 | 0.983 |  | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.5297 | -6.9767
MCDONAGH (390000) 38 kV STATION | Mcdonagh [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5 | 10.4 |  | --> | 12.4 | 4.75 | 3.1 | 8.6 | 4.8 | Constrained, otherwise capacity available =11.24 MW | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.6596 | -7.2484
CALLAN (460000) 38 kV STATION | Callan [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 10.4 |  | --> | 6.2 | 2.375 | 6 | 1.2 | 2.401 |  | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.5351 | -7.3914
PURCELLS INCH (485000) 38 kV STATION | Purcells Inch [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 7.5 | 2.8 | 10.4 |  | --> | 3.1 | 2.375 | 2.1 | 1.8 | 2.439 |  | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.647 | -7.214
ROSEHILL (193000) 38 kV STATION | Rosehill [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 10.4 |  | --> | 12.4 | 4.75 | 3.1 | 8.6 | 4.887 | Constrained, otherwise capacity available =12.25 MW | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.6399 | -7.2705
TALBOTS INCH (508000) 38 kV STATION | Talbots Inch [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 10.4 |  | --> | 6.2 | 2.375 | 8.2 | 0 | 2.496 |  | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.6758 | -7.2636
CLOON (907000) 110 kV STATION | Cloon [T42,T421] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 10.7 | 10.8 |  | --> | 12.4 | 4.75 | 13.1 | 0.5 | 4.762 |  | --> |  | Cloon [T141,T142] | CLOON |  | 53.4879 | -8.8539
HEADFORD (527000) 38 kV STATION | Headford [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0 | 10.8 |  | --> | 1.2 | 1.1875 | 3.3 | 0 | 1.449 |  | --> |  | Cloon [T141,T142] | CLOON |  | 53.4969 | -9.1181
CONG (590000) 38 kV STATION | Cong [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 1.4 | 10.8 |  | --> | 6.2 | 2.375 | 0.8 | 6.3 | 2.396 |  | --> |  | Cloon [T141,T142] | CLOON |  | 53.544 | -9.2569
TUAM NORTH (253000) 38 kV STATION | Tuam North [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 10.8 |  | --> | 6.2 | 2.375 | 3 | 4.9 | 2.473 |  | --> |  | Cloon [T141,T142] | CLOON |  | 53.5329 | -8.8772
TUAM SOUTH (040000) 38 kV STATION | Tuam South [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 10.8 |  | --> | 4.8 | 0 | 0.4 | 5.8 | 0 |  | --> |  | Cloon [T141,T142] | CLOON |  | 53.516 | -8.8665
MOHILL (048000) 38 kV STATION | Mohill [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 2 | 11.5 |  | --> | 6.2 | 2.375 | 1.8 | 5.5 | 2.407 |  | --> |  | Carrick On Shannon [T141,T142] | CARRICK ON SHANNON |  | 53.9048 | -7.8689
CASTLEREA (256000) 38 kV STATION | Castlerea [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.3 | 11.5 |  | --> | 6.2 | 2.375 | 4.4 | 3.1 | 2.419 |  | --> |  | Carrick On Shannon [T141,T142] | CARRICK ON SHANNON |  | 53.7675 | -8.4446
CARRIGALLEN (157000) 38 kV STATION | Carrigallen [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.6 | 11.5 |  | --> | 4.8 | 0 | 0.9 | 4.5 | 0 |  | --> |  | Carrick On Shannon [T141,T142] | CARRICK ON SHANNON |  | 53.9723 | -7.6967
CARRICK ON SHANNON (074000) 110 kV STATION | Carrick On Shannon [T41,T42] | 110 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 11.5 |  | --> | 6.2 | 2.375 | 2.2 | 6.1 | 2.544 |  | --> |  | Carrick On Shannon [T141,T142] | CARRICK ON SHANNON |  | 53.9295 | -8.1261
BOYLE (047000) 38 kV STATION | Boyle [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1 | 11.5 |  | --> | 6.2 | 2.375 | 9.3 | 0 | 2.419 |  | --> |  | Carrick On Shannon [T141,T142] | CARRICK ON SHANNON |  | 53.9561 | -8.3176
SPA ROAD (205000) 38 kV STATION | Spa Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.9 | 11.6 |  | --> | 6.2 | 2.375 | 2.1 | 0 | 0 | Constrained, otherwise capacity available =5.38 MW | --> |  | Doon [T141,T142] | DOON |  | 52.3529 | -7.6775
ARDGEEHA (034000) 38 kV STATION | Ardgeeha [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.9 | 11.6 |  | --> | 12.4 | 4.75 | 8.3 | 0 | 0 | Constrained, otherwise capacity available =6.09 MW | --> |  | Doon [T141,T142] | DOON |  | 52.3777 | -7.6967
LAWLESSTOWN (542000) 38 kV STATION | Lawlesstown [T42,T421] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.6 | 11.6 |  | --> | 12.4 | 4.75 | 3.5 | 0 | 0 | Constrained, otherwise capacity available =12.19 MW | --> |  | Doon [T141,T142] | DOON |  | 52.3763 | -7.7249
CREESLOUGH (258000) 38 kV STATION | Creeslough [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.9 | 11.8 |  | --> | 4.8 | 0 | 0.9 | 0 | 0 | Constrained, otherwise capacity available =4.47 MW | --> |  | Ardnagappary [T141] | ARDNAGAPPARY |  | 55.1166 | -7.9019
GWEEDORE (192000) 38 kV STATION | Gweedore [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.7 | 11.8 |  | --> | 4.8 | 0 | 1.1 | 0 | 0 | Constrained, otherwise capacity available =4.34 MW | --> |  | Ardnagappary [T141] | ARDNAGAPPARY |  | 55.0328 | -8.2027
DERRYBEG (399000) 38 kV STATION | Derrybeg [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.6 | 11.8 |  | --> | 6.2 | 2.375 | 1.4 | 0 | 0 | Constrained, otherwise capacity available =5.84 MW | --> |  | Ardnagappary [T141] | ARDNAGAPPARY |  | 55.0668 | -8.2661
DUNGLOE (340000) 38 kV STATION | Dungloe [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0 | 11.8 |  | --> | 1.2 | 1.1875 | 2.3 | 0 | 0 |  | --> |  | Ardnagappary [T141] | ARDNAGAPPARY |  | 54.9422 | -8.3626
MILLTOWN (DR) (069000) 110 kV STATION | Milltown (dr) [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 7.8 | 113 |  | --> | 24.7 | 9.5 | 3.2 | 26.2 | 9.645 |  | --> |  | Inchicore City 220/110 kV [T2102,T2104] | INCHICORE 220KV |  | 53.3176 | -6.2456
MILLTOWN (DR) (069000) 110 kV STATION | Mesh: Green [MiltT142,InciT143] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 29.5 | 113 |  | --> | 77.8 | 0 | 26.8 | 65.5 | 0 |  | --> |  | Inchicore City 220/110 kV [T2102,T2104] | INCHICORE 220KV |  | 53.3176 | -6.2456
HEUSTON SQUARE (504000) 110 kV STATION | Heuston Square [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 20.8 | 113 |  | --> | 24.7 | 9.5 | 0.2 | 27.9 | 9.575 |  | --> |  | Inchicore City 220/110 kV [T2102,T2104] | INCHICORE 220KV |  | 53.347 | -6.3042
FRANCIS STREET (733000) 110 kV STATION | Mesh: Red [InciT141,FranT142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 14.7 | 113 |  | --> | 77.8 | 0 | 9.9 | 81.5 | 0 |  | --> |  | Inchicore City 220/110 kV [T2102,T2104] | INCHICORE 220KV |  | 53.3374 | -6.2793
CHURCHTOWN (971000) 38 kV STATION | Churchtown [T422] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 7.5 | 12.7 |  | --> | 9.5 | 0 | 0.9 | 0 | 0 | Constrained, otherwise capacity available =8.81 MW | --> |  | Rathkeale [T141,T142] | RATHKEALE |  | 52.4634 | -9.0494
CHURCHTOWN (971000) 38 kV STATION | Churchtown [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 4.2 | 12.7 |  | --> | 9.5 | 0 | 0.4 | 0 | 0 | Constrained, otherwise capacity available =9.76 MW | --> |  | Rathkeale [T141,T142] | RATHKEALE |  | 52.4634 | -9.0494
NEWCASTLEWEST (185000) 38 kV STATION | Newcastlewest [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.1 | 12.7 |  | --> | 6.2 | 2.375 | 2.8 | 0 | 0 | Constrained, otherwise capacity available =4.84 MW | --> |  | Rathkeale [T141,T142] | RATHKEALE |  | 52.4479 | -9.0462
FOYNES (314000) 38 kV STATION | Foynes [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.6 | 12.7 |  | --> | 6.2 | 2.375 | 4.8 | 0 | 0 | Constrained, otherwise capacity available =2.44 MW | --> |  | Rathkeale [T141,T142] | RATHKEALE |  | 52.6067 | -9.0798
RATHKEALE (712000) 110 kV STATION | Rathkeale [T421,T422] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 2 | 12.7 |  | --> | 12.4 | 4.75 | 3.2 | 0 | 0 | Constrained, otherwise capacity available =11.72 MW | --> |  | Rathkeale [T141,T142] | RATHKEALE |  | 52.5406 | -8.9745
KELLS (180000) 38 kV STATION | Kells [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.4 | 12.8 |  | --> | 6.2 | 2.375 | 1.7 | 5.5 | 2.402 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.716 | -6.8746
RANDALSTOWN (463000) 38 kV STATION | Randalstown [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.6 | 12.8 |  | --> | 4.8 | 0 | 0.8 | 4.4 | 0 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.6705 | -6.7238
RANDALSTOWN (463000) 38 kV STATION | Randalstown [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.8 | 12.8 |  | --> | 4.8 | 0 | 0.4 | 4.8 | 0 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.6705 | -6.7238
ABBEYLAND (270000) 38 kV STATION | Abbeyland [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2 | 12.8 |  | --> | 12.4 | 4.75 | 3.5 | 10.8 | 4.8 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.671 | -6.6874
ACADEMY STREET (617000) 38 kV STATION | Academy Street [T421,T422,T44] | 38 kV | _ | MV | 2x5,1x10 MVA @ 20 kV | 20 | --> | 18 | 0 | 12.8 |  | --> | 19 | 4.75 | 8.3 | 14.8 | 4.857 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.6496 | -6.6735
ATHBOY (177000) 38 kV STATION | Athboy [T423] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.3 | 12.8 |  | --> | 4.8 | 0 | 5.2 | 0 | 0 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.6447 | -6.9298
TRIM (196000) 38 kV STATION | Trim [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 12.8 |  | --> | 6.2 | 2.375 | 7.9 | 0 | 2.447 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.5544 | -6.7864
TRIM (196000) 38 kV STATION | Trim [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.3 | 12.8 |  | --> | 4.8 | 0 | 1.7 | 3.6 | 0 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.5544 | -6.7864
LLOYD (711000) 38 kV STATION | Lloyd [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 3.3 | 12.8 |  | --> | 6.2 | 2.375 | 0.6 | 6.3 | 2.388 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.7333 | -6.9117
ATHBOY (177000) 38 kV STATION | Athboy [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 12.8 |  | --> | 4.8 | 0 | 5.7 | 0 | 0 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.6447 | -6.9298
MOY (774000) 110 kV STATION | Moy [T421,T422] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 2.3 | 13 |  | --> | 12.4 | 4.75 | 7.9 | 7.5 | 4.889 |  | --> |  | Moy [T141,T142] | MOY |  | 54.1315 | -9.1748
ENNISCRONE (492000) 38 kV STATION | Enniscrone [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 3.6 | 13 |  | --> | 6.2 | 2.375 | 7.5 | 0.1 | 2.404 |  | --> |  | Moy [T141,T142] | MOY |  | 54.2051 | -9.0628
RAHANS (461000) 38 kV STATION | Rahans [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.7 | 13 |  | --> | 4.8 | 0 | 0.5 | 5.5 | 0 |  | --> |  | Moy [T141,T142] | MOY |  | 54.1078 | -9.1659
CROSSMOLINA (220000) 38 kV STATION | Crossmolina [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 5.25 | 1.4 | 13 |  | --> | 2.5 | 2.375 | 1.3 | 2.1 | 2.517 |  | --> |  | Moy [T141,T142] | MOY |  | 54.1164 | -9.3359
ARDNAREE (089000) 38 kV STATION | Ardnaree [T42,T421] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 9.1 | 13 |  | --> | 12.4 | 4.75 | 1.6 | 12 | 4.768 |  | --> |  | Moy [T141,T142] | MOY |  | 54.1178 | -9.1521
GORTLEE (646000) 38 kV STATION | Gortlee [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.5 | 13.2 |  | --> | 12.4 | 4.75 | 1.1 | 0 | 0 | Constrained, otherwise capacity available =13.46 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.9707 | -7.7144
CONVOY (162000) 38 kV STATION | Convoy [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 11.25 | 7.2 | 13.2 |  | --> | 6.2 | 4.75 | 0.7 | 0 | 0 | Constrained, otherwise capacity available =6.29 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.8604 | -7.6599
STRANORLAR (150000) 38 kV STATION | Stranorlar [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 4 | 13.2 |  | --> | 12.4 | 4.75 | 11.1 | 0 | 0 | Constrained, otherwise capacity available =3.66 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.808 | -7.7617
NEWTOWNCUNNINGHAM (503000) 38 kV STATION | Newtowncunningham [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.7 | 13.2 |  | --> | 6.2 | 2.375 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =6.15 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 55.008 | -7.4657
MILFORD (NR) (209000) 38 kV STATION | Milford (nr) [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 13.2 |  | --> | 6.2 | 2.375 | 7.9 | 0 | 0 | Constrained, otherwise capacity available =0.54 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 55.075 | -7.6985
CULLION (099000) 38 kV STATION | Cullion [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 13.2 |  | --> | 6.2 | 2.375 | 2.5 | 0 | 0 | Constrained, otherwise capacity available =5.63 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.939 | -7.7183
BALLYRAINE (442000) 38 kV STATION | Ballyraine [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 11.25 | 3 | 13.2 |  | --> | 6.2 | 4.75 | 2.5 | 0 | 0 | Constrained, otherwise capacity available =5.34 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.9515 | -7.7105
ROSSGEIR (489000) 38 kV STATION | Rossgeir [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.2 | 13.2 |  | --> | 6.2 | 2.375 | 1.9 | 0 | 0 | Constrained, otherwise capacity available =5.64 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.8614 | -7.5172
GLENGOOLE (207000) 38 kV STATION | Glengoole [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.9 | 13.7 |  | --> | 4.8 | 0 | 0.5 | 0 | 0 | Constrained, otherwise capacity available =4.54 MW | --> |  | Thurles [T141,T142] | THURLES |  | 52.6084 | -7.6267
BLANCHFIELD (432000) 38 kV STATION | Blanchfield [T421] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13.2 | 13.7 |  | --> | 14.2 | 0 | 11.5 | 0 | 0 | Constrained, otherwise capacity available =3.05 MW | --> |  | Thurles [T141,T142] | THURLES |  | 52.6547 | -7.5021
URLINGFORD (910000) 38 kV STATION | Urlingford [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 13.7 |  | --> | 9.5 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =9.5 MW | --> |  | Thurles [T141,T142] | THURLES |  | 52.705 | -7.5965
BLANCHFIELD (432000) 38 kV STATION | Blanchfield [T422] | 38 kV | _ | MV | 1x31.5 MVA @ 20 kV | 31.5 | --> | 28.35 | 13.7 | 13.7 | Constrained, otherwise capacity available =28.13 MVA | --> | 29.9 | 0 | 23.4 | 0 | 0 | Constrained, otherwise capacity available =6.86 MW | --> |  | Thurles [T141,T142] | THURLES |  | 52.6547 | -7.5021
HOLYCROSS ROAD (328000) 38 kV STATION | Holycross Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 13.7 |  | --> | 6.2 | 2.375 | 3.5 | 0 | 0 | Constrained, otherwise capacity available =4.71 MW | --> |  | Thurles [T141,T142] | THURLES |  | 52.6664 | -7.8399
LOUGHTAGALLA (127000) 38 kV STATION | Loughtagalla [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 13.7 |  | --> | 6.2 | 2.375 | 2 | 0 | 0 | Constrained, otherwise capacity available =5.51 MW | --> |  | Thurles [T141,T142] | THURLES |  | 52.693 | -7.7696
GLENGOOLE (207000) 38 kV STATION | Glengoole [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 3.4 | 13.7 |  | --> | 9.5 | 0 | 8 | 0 | 0 | Constrained, otherwise capacity available =3.61 MW | --> |  | Thurles [T141,T142] | THURLES |  | 52.6084 | -7.6267
BALLYJAMESDUFF (139000) 38 kV STATION | Ballyjamesduff [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4 | 13.8 |  | --> | 12.4 | 4.75 | 6.1 | 8.2 | 4.785 |  | --> |  | Shankill [T141,T142] | SHANKILL |  | 53.8459 | -7.202
FINEA (587000) 38 kV STATION | Finea [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 13.8 |  | --> | 6.2 | 2.375 | 5 | 3 | 2.477 |  | --> |  | Shankill [T141,T142] | SHANKILL |  | 53.7997 | -7.3943
CLONES (246000) 38 kV STATION | Clones [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 13.8 |  | --> | 6.2 | 2.375 | 1.5 | 6.5 | 2.484 |  | --> |  | Shankill [T141,T142] | SHANKILL |  | 54.1892 | -7.2291
ERRIGAL (517000) 38 kV STATION | Errigal [T41,T422] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.6 | 13.8 |  | --> | 12.4 | 4.75 | 5.8 | 8.3 | 4.832 | Constrained, otherwise capacity available =9.36 MW | --> |  | Shankill [T141,T142] | SHANKILL |  | 54.0567 | -7.0805
DERRYCRAMPH (545000) 38 kV STATION | Derrycramph [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 13.8 |  | --> | 6.2 | 2.375 | 1.5 | 6 | 2.43 |  | --> |  | Shankill [T141,T142] | SHANKILL |  | 53.9752 | -7.378
CAVAN (059000) 38 kV STATION | Cavan [T42,T421] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 13.8 |  | --> | 12.4 | 4.75 | 4.2 | 8.3 | 4.984 | Constrained, otherwise capacity available =11.87 MW | --> |  | Shankill [T141,T142] | SHANKILL |  | 54.0066 | -7.3417
TULLABRACK (722000) 110 kV STATION | Tullabrack [T421,T422] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 14.4 | 14.4 | Constrained, otherwise capacity available =15 MVA | --> | 12.4 | 4.75 | 0 | 0 | 0 | Constrained, otherwise capacity available =12.35 MW | --> |  | Tullabrack [T141] | TULLABRACK |  | 52.6666 | -9.462
KILRUSH (095000) 38 kV STATION | Kilrush [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.7 | 14.4 |  | --> | 6.2 | 2.375 | 1.9 | 0 | 0 | Constrained, otherwise capacity available =5.54 MW | --> |  | Tullabrack [T141] | TULLABRACK |  | 52.655 | -9.4708
MILLTOWN MALBAY (439000) 38 kV STATION | Milltown Malbay [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.8 | 14.4 |  | --> | 4.8 | 0 | 1.7 | 0 | 0 | Constrained, otherwise capacity available =3.78 MW | --> |  | Tullabrack [T141] | TULLABRACK |  | 52.8439 | -9.4124
KILKEE (275000) 38 kV STATION | Kilkee [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.1 | 14.4 |  | --> | 4.8 | 0 | 5.7 | 0 | 0 |  | --> |  | Tullabrack [T141] | TULLABRACK |  | 52.6854 | -9.6296
KINGSBRIDGE (107000) 38 kV STATION | Kingsbridge [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.6 | 14.7 |  | --> | 12.4 | 4.75 | 0.2 | 15.6 | 4.939 |  | --> |  | Mesh: Red [InciT141,FranT142] | INCHICORE 220KV |  | 53.343 | -6.2973
NEWMARKET (DR) (217000) 38 kV STATION | Newmarket (dr) [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 14.7 |  | --> | 9.5 | 0 | 0.5 | 10.9 | 0 |  | --> |  | Mesh: Red [InciT141,FranT142] | FRANCIS STREET |  | 53.3347 | -6.2819
CAMDEN ROW (103000) 38 kV STATION | Camden Row [T41] | 38 kV | _ | MV | 1x15 MVA @ 10 kV | 15 | --> | 13.5 | 0 | 14.7 |  | --> | 14.2 | 0 | 0.2 | 17 | 0 |  | --> |  | Mesh: Red [InciT141,FranT142] | FRANCIS STREET |  | 53.3344 | -6.2628
INCHICORE CENTRAL (081000) 110 kV STATION | Inchicore Central [T43,T45] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3 | 14.7 |  | --> | 12.4 | 4.75 | 1.4 | 13.3 | 4.82 |  | --> |  | Mesh: Red [InciT141,FranT142] | INCHICORE 220KV |  | 53.3333 | -6.3419
WATLING STREET (361000) 38 kV STATION | Watling Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 14.7 |  | --> | 12.4 | 4.75 | 8.3 | 5.9 | 4.793 |  | --> |  | Mesh: Red [InciT141,FranT142] | FRANCIS STREET |  | 53.3469 | -6.2808
MARROWBONE LANE (128000) 38 kV STATION | Marrowbone Lane [T42] | 38 kV | _ | MV | 1x15 MVA @ 10 kV | 15 | --> | 13.5 | 1.5 | 14.7 |  | --> | 14.2 | 0 | 0.3 | 16.6 | 0 |  | --> |  | Mesh: Red [InciT141,FranT142] | INCHICORE 220KV |  | 53.3353 | -6.2922
ABBEYFEALE (429000) 38 kV STATION | Abbeyfeale [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.3 | 14.8 |  | --> | 4.8 | 0 | 1.2 | 0 | 0 | Constrained, otherwise capacity available =4.37 MW | --> |  | Trien [T141,T142] | TRIEN |  | 52.387 | -9.2926
ABBEYFEALE (429000) 38 kV STATION | Abbeyfeale [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 5.8 | 14.8 |  | --> | 9.5 | 0 | 9.8 | 0 | 0 | Constrained, otherwise capacity available =1.41 MW | --> |  | Trien [T141,T142] | TRIEN |  | 52.387 | -9.2926
SMEARLA (018000) 38 kV STATION | Smearla [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.8 | 14.8 |  | --> | 12.4 | 4.75 | 4.4 | 0 | 0 | Constrained, otherwise capacity available =10.12 MW | --> |  | Trien [T141,T142] | TRIEN |  | 52.4372 | -9.446
BALLYBUNION (363000) 38 kV STATION | Ballybunion [T424] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 8.4 | 14.8 |  | --> | 9.5 | 0 | 10 | 0 | 0 |  | --> |  | Trien [T141,T142] | TRIEN |  | 52.4988 | -9.6482
BALLYBUNION (363000) 38 kV STATION | Ballybunion [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 3.3 | 14.8 |  | --> | 6.2 | 2.375 | 1.6 | 0 | 0 | Constrained, otherwise capacity available =5.73 MW | --> |  | Trien [T141,T142] | TRIEN |  | 52.4988 | -9.6482
LEE BRIDGE (176000) 38 kV STATION | Lee Bridge [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 11.25 | 7.6 | 16.1 |  | --> | 6.2 | 4.75 | 1.9 | 0 | 0 | Constrained, otherwise capacity available =5.17 MW | --> |  | Macroom [T142] | MACROOM |  | 51.8978 | -8.9379
MACROOM (630000) 110 kV STATION | Macroom [T422] | 110 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 3.75 | 0 | 16.1 |  | --> | 3.3 | 0 | 12.5 | 0 | 0 |  | --> |  | Macroom [T142] | MACROOM |  | 51.8936 | -8.8878
DEERPARK (033000) 38 kV STATION | Deerpark [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 16.9 |  | --> | 6.2 | 2.375 | 6.9 | 0.6 | 2.429 |  | --> |  | Ballydine [T141] | BALLYDINE |  | 52.3507 | -7.4248
CREGG ROAD (181000) 38 kV STATION | Cregg Road [T41,T42] | 38 kV | _ | MV | 2x2 MVA @ 10 kV | 4 | --> | 3 | 0 | 16.9 |  | --> | 2.5 | 0.95 | 1.3 | 2 | 1.001 |  | --> |  | Ballydine [T141] | BALLYDINE |  | 52.354 | -7.4099
CASTLETOWNROCHE (080000) 38 kV STATION | Castletownroche [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.2 | 18.1 |  | --> | 4.8 | 0 | 0.8 | 4.3 | 0 |  | --> |  | Mallow [T141,T142] | MALLOW |  | 52.1709 | -8.465
SCARTEEN (211000) 38 kV STATION | Scarteen [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 18.1 |  | --> | 6.2 | 2.375 | 5.5 | 2.4 | 2.478 |  | --> |  | Mallow [T141,T142] | MALLOW |  | 52.1463 | -8.6725
MALLOW (689000) 110 kV STATION | Mallow [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.6 | 18.1 |  | --> | 12.4 | 4.75 | 2.6 | 11.7 | 4.801 |  | --> |  | Mallow [T141,T142] | MALLOW |  | 52.1463 | -8.6155
BUTTEVANT (024000) 38 kV STATION | Buttevant [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2.1 | 18.1 |  | --> | 6.2 | 2.375 | 1.7 | 5.5 | 2.403 |  | --> |  | Mallow [T141,T142] | MALLOW |  | 52.2276 | -8.6577
CAHIR (668000) 110 kV STATION | Cahir [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 6.2 | 18.2 |  | --> | 12.4 | 4.75 | 6.1 | 0 | 0 | Constrained, otherwise capacity available =8.49 MW | --> |  | Cahir [T141,T142] | CAHIR |  | 52.3824 | -7.8857
ARDFINNAN (386000) 38 kV STATION | Ardfinnan [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 3.9 | 18.2 |  | --> | 4.8 | 0 | 3 | 0 | 0 | Constrained, otherwise capacity available =1.9 MW | --> |  | Cahir [T141,T142] | CAHIR |  | 52.3019 | -7.8809
ARDFINNAN (386000) 38 kV STATION | Ardfinnan [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.5 | 18.2 |  | --> | 4.8 | 0 | 1.9 | 0 | 0 | Constrained, otherwise capacity available =3.6 MW | --> |  | Cahir [T141,T142] | CAHIR |  | 52.3019 | -7.8809
ARDFINNAN (386000) 38 kV STATION | Ardfinnan [T424] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 18.2 |  | --> | 9.5 | 0 | 6.2 | 0 | 0 | Constrained, otherwise capacity available =3.26 MW | --> |  | Cahir [T141,T142] | CAHIR |  | 52.3019 | -7.8809
KILSHANNY (125000) 38 kV STATION | Kilshanny [T41,T42] | 38 kV | _ | MV | 2x2 MVA @ 10 kV | 4 | --> | 3 | 0.2 | 18.2 |  | --> | 2.5 | 0.95 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =1.82 MW | --> |  | Cahir [T141,T142] | CAHIR |  | 52.2627 | -8.2479
CASHEL (169000) 38 kV STATION | Cashel [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.9 | 18.2 |  | --> | 12.4 | 4.75 | 3 | 0 | 0 | Constrained, otherwise capacity available =11.19 MW | --> |  | Cahir [T141,T142] | CAHIR |  | 52.5019 | -7.8903
BRAY (002000) 38 kV STATION | Bray [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.4 | 19.8 |  | --> | 12.4 | 4.75 | 3.9 | 11.1 | 4.843 |  | --> |  | Fassaroe [T141,T142] | FASSAROE |  | 53.195 | -6.1243
LITTLE BRAY (223000) 38 kV STATION | Little Bray [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 19.8 |  | --> | 12.4 | 4.75 | 3.7 | 11.8 | 4.899 |  | --> |  | Fassaroe [T141,T142] | FASSAROE |  | 53.2051 | -6.1369
KILCOOLE (498000) 38 kV STATION | Kilcoole [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.6 | 19.8 |  | --> | 12.4 | 4.75 | 3.3 | 10.8 | 4.789 |  | --> |  | Fassaroe [T141,T142] | FASSAROE |  | 53.0942 | -6.0848
BOGHALL ROAD (969000) 38 kV STATION | Boghall Road [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.5 | 19.8 |  | --> | 12.4 | 4.75 | 1.9 | 13.1 | 4.844 |  | --> |  | Fassaroe [T141,T142] | FASSAROE |  | 53.1834 | -6.1028
GREYSTONES (071000) 38 kV STATION | Greystones [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 19.8 |  | --> | 12.4 | 4.75 | 7.1 | 8.6 | 4.929 |  | --> |  | Fassaroe [T141,T142] | FASSAROE |  | 53.1386 | -6.0918
BALLYCROSSAUN (250000) 38 kV STATION | Ballycrossaun [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 1.3 | 2 |  | --> | 6.2 | 2.375 | 4.7 | 2.3 | 2.389 |  | --> |  | Somerset [T142] | SOMERSET |  | 53.161 | -8.1805
BALLINASLOE (118000) 38 kV STATION | Ballinasloe [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2 | 2 | Constrained, otherwise capacity available =2.73 MVA | --> | 6.2 | 2.375 | 0.9 | 6.5 | 2.418 |  | --> |  | Somerset [T142] | SOMERSET |  | 53.3136 | -8.1996
CURRA (528000) 38 kV STATION | Curra [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.6 | 2 |  | --> | 4.8 | 0 | 1.4 | 3.8 | 0 |  | --> |  | Somerset [T142] | SOMERSET |  | 53.1308 | -8.4456
LOUGHREA (132000) 38 kV STATION | Loughrea [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 2 |  | --> | 6.2 | 2.375 | 7.8 | 0.3 | 2.504 |  | --> |  | Somerset [T142] | SOMERSET |  | 53.2119 | -8.5846
KILROSS ROAD (213000) 38 kV STATION | Kilross Road [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.8 | 2.8 | Constrained, otherwise capacity available =3.11 MVA | --> | 4.8 | 0 | 0.3 | 4.6 | 0 |  | --> |  | Tipperary [T141] | TIPPERARY |  | 52.4642 | -8.1856
KILROSS ROAD (213000) 38 kV STATION | Kilross Road [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.4 | 2.8 |  | --> | 4.8 | 0 | 4.4 | 0.9 | 0 |  | --> |  | Tipperary [T141] | TIPPERARY |  | 52.4642 | -8.1856
GLEBE (416000) 38 kV STATION | Glebe [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.8 | 2.8 | Constrained, otherwise capacity available =2.97 MVA | --> | 12.4 | 4.75 | 0.8 | 6 | 4.954 | Constrained, otherwise capacity available =15.15 MW | --> |  | Richmond [T141,T142] | RICHMOND |  | 53.7374 | -7.793
GARRANACANTY (036000) 38 kV STATION | Garranacanty [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 2.8 |  | --> | 12.4 | 4.75 | 4.2 | 8.1 | 5.078 | Constrained, otherwise capacity available =12.34 MW | --> |  | Tipperary [T141] | TIPPERARY |  | 52.4853 | -8.1521
LONGFORD (049000) 38 kV STATION | Longford [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0.2 | 2.8 |  | --> | 12.4 | 4.75 | 9.7 | 5.3 | 4.851 |  | --> |  | Richmond [T141,T142] | RICHMOND |  | 53.745 | -7.8022
EDGEWORTHSTOWN (130000) 38 kV STATION | Edgeworthstown [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 2.5 | 2.8 |  | --> | 12.4 | 4.75 | 4.5 | 6 | 4.781 | Constrained, otherwise capacity available =9.47 MW | --> |  | Richmond [T141,T142] | RICHMOND |  | 53.7144 | -7.6198
ROOSKY (434000) 38 kV STATION | Roosky [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.3 | 2.8 |  | --> | 4.8 | 0 | 1.1 | 4.3 | 0 |  | --> |  | Richmond [T141,T142] | RICHMOND |  | 53.8405 | -7.9198
GARRYSPILLANE (292000) 38 kV STATION | Garryspillane [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 2.8 |  | --> | 4.8 | 0 | 6.1 | 0 | 0 |  | --> |  | Tipperary [T141] | TIPPERARY |  | 52.3983 | -8.3769
FACTORY CROSS (370000) 38 kV STATION | Factory Cross [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 10.8 | 20.5 |  | --> | 12.4 | 4.75 | 0.2 | 13.3 | 4.766 |  | --> |  | Barnahely [T141,T142] | BARNAHELY |  | 51.8186 | -8.3341
RINGASKIDDY 110KV (603000) 110 kV STATION | Ringaskiddy 110kv [T42] | 110 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 4.3 | 20.5 |  | --> | 9.5 | 0 | 1.3 | 8.9 | 0 |  | --> |  | Barnahely [T141,T142] | BARNAHELY |  | 51.8315 | -8.3406
CARRIGALINE (166000) 38 kV STATION | Carrigaline [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 20.5 |  | --> | 6.2 | 2.375 | 4.7 | 3 | 2.446 |  | --> |  | Barnahely [T141,T142] | BARNAHELY |  | 51.8185 | -8.3894
BUSH (488000) 38 kV STATION | Bush [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 3.5 | 21 |  | --> | 6.2 | 2.375 | 5.6 | 0 | 0 | Constrained, otherwise capacity available =1.33 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 54.0011 | -6.1682
JENKINSTOWN (264000) 38 kV STATION | Jenkinstown [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 4.2 | 21 |  | --> | 6.2 | 2.375 | 2 | 0 | 0 | Constrained, otherwise capacity available =5.28 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 54.0241 | -6.2867
DUNDALK (062000) 110 kV STATION | Dundalk [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.3 | 21 |  | --> | 12.4 | 4.75 | 2.9 | 0 | 0 | Constrained, otherwise capacity available =11.81 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 54.0085 | -6.4194
RAMPARTS (175000) 38 kV STATION | Ramparts [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.7 | 21 |  | --> | 12.4 | 4.75 | 1.2 | 0 | 0 | Constrained, otherwise capacity available =13 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 54.0064 | -6.4047
CASTLEBLAYNEY (184000) 38 kV STATION | Castleblayney [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.4 | 21 |  | --> | 12.4 | 4.75 | 1.7 | 0 | 0 | Constrained, otherwise capacity available =12.94 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 54.1291 | -6.7624
MARSHES (358000) 38 kV STATION | Marshes [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.1 | 21 |  | --> | 12.4 | 4.75 | 5.3 | 0 | 0 | Constrained, otherwise capacity available =9.32 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 53.9768 | -6.3937
MARSHES (358000) 38 kV STATION | Marshes [T423] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 21 |  | --> | 9.5 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =9.5 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 53.9768 | -6.3937
COES ROAD (367000) 38 kV STATION | Coes Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.7 | 21 |  | --> | 6.2 | 2.375 | 1.6 | 0 | 0 | Constrained, otherwise capacity available =5.79 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 53.9951 | -6.3872
BALLYBAILIE (269000) 38 kV STATION | Ballybailie [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0 | 21 |  | --> | 1.2 | 1.1875 | 1.8 | 0 | 0 |  | --> |  | Dundalk [T141,T142] | DUNDALK |  | 53.8666 | -6.5464
LITTLE MILLS (316000) 38 kV STATION | Little Mills [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1 | 21 |  | --> | 4.8 | 0 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =4.27 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 53.9887 | -6.4426
MERRION SQUARE (105000) 38 kV STATION | Merrion Square [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.4 | 21.3 |  | --> | 12.4 | 4.75 | 0.1 | 14.7 | 4.834 |  | --> |  | Mesh: Blue [RingT141,MiltT141] | RINGSEND |  | 53.3348 | -6.2424
PEMBROKE (094000) 38 kV STATION | Pembroke [T41,T42,T43,T44] | 38 kV | _ | MV | 4x10 MVA @ 10 kV | 40 | --> | 36 | 9.3 | 21.3 |  | --> | 38 | 4.75 | 1.6 | 41.9 | 4.799 |  | --> |  | Mesh: Blue [RingT141,MiltT141] | RINGSEND |  | 53.3428 | -6.2348
DONNYBROOK (308000) 38 kV STATION | Donnybrook [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 21.3 |  | --> | 12.4 | 4.75 | 0.8 | 14.7 | 4.901 |  | --> |  | Mesh: Blue [RingT141,MiltT141] | MILLTOWN (DR) |  | 53.3177 | -6.226
LEESON STREET (342000) 38 kV STATION | Leeson Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1 | 21.3 |  | --> | 12.4 | 4.75 | 0.3 | 15 | 4.882 |  | --> |  | Mesh: Blue [RingT141,MiltT141] | MILLTOWN (DR) |  | 53.3276 | -6.2585
KNOCKMULLEN (957000) 38 kV STATION | Knockmullen [T42,T421] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 21.5 |  | --> | 12.4 | 4.75 | 3.7 | 0 | 0 | Constrained, otherwise capacity available =11.64 MW | --> |  | Great Island [T141,T142] | GREAT ISLAND |  | 52.3846 | -6.944
BEALISTOWN (375000) 38 kV STATION | Bealistown [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0.2 | 21.5 |  | --> | 6.2 | 2.375 | 8.5 | 0 | 0 |  | --> |  | Great Island [T141,T142] | GREAT ISLAND |  | 52.263 | -6.8747
GRAIGUE (012000) 38 kV STATION | Graigue [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2 | 22 |  | --> | 12.4 | 4.75 | 3 | 0 | 0 | Constrained, otherwise capacity available =11.78 MW | --> |  | Carlow [T141,T142] | CARLOW |  | 52.8391 | -6.9503
POLLERTON (242000) 38 kV STATION | Pollerton [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 22 |  | --> | 12.4 | 4.75 | 4.8 | 0 | 0 | Constrained, otherwise capacity available =11.09 MW | --> |  | Carlow [T141,T142] | CARLOW |  | 52.8431 | -6.9178
BAGENALSTOWN (389000) 38 kV STATION | Bagenalstown [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 2.8 | 22 |  | --> | 12.4 | 4.75 | 7.9 | 0 | 0 | Constrained, otherwise capacity available =6.9 MW | --> |  | Carlow [T141,T142] | CARLOW |  | 52.7094 | -6.9462
SHILLELAGH (708000) 38 kV STATION | Shillelagh [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 22 |  | --> | 6.2 | 2.375 | 6.6 | 0 | 0 | Constrained, otherwise capacity available =1.73 MW | --> |  | Carlow [T141,T142] | CARLOW |  | 52.7481 | -6.5265
TULLOW (293000) 38 kV STATION | Tullow [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0.4 | 22 |  | --> | 12.4 | 4.75 | 13.7 | 0 | 0 | Constrained, otherwise capacity available =1.47 MW | --> |  | Carlow [T141,T142] | CARLOW |  | 52.8003 | -6.7211
FAIRVIEW (113000) 38 kV STATION | Fairview [T41] | 38 kV | _ | MV | 1x15 MVA @ 10 kV | 15 | --> | 13.5 | 1.9 | 22.3 |  | --> | 14.2 | 0 | 1.9 | 14.7 | 0 |  | --> |  | Mesh: Purple [FingT141,McDrT141] | MCDERMOTT |  | 53.3678 | -6.2215
COOLOCK (277000) 38 kV STATION | Coolock [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.8 | 22.3 |  | --> | 12.4 | 4.75 | 1.2 | 13.2 | 4.803 |  | --> |  | Mesh: Purple [FingT141,McDrT141] | FINGLAS |  | 53.4 | -6.2054
BALLYMUN (093000) 38 kV STATION | Ballymun [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.9 | 22.3 |  | --> | 12.4 | 4.75 | 1.9 | 12.3 | 4.789 |  | --> |  | Mesh: Purple [FingT141,McDrT141] | FINGLAS |  | 53.3839 | -6.2803
EAST WALL ROAD (112000) 38 kV STATION | East Wall Road [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 6.6 | 22.3 |  | --> | 12.4 | 4.75 | 0.4 | 14.6 | 4.853 |  | --> |  | Mesh: Purple [FingT141,McDrT141] | MCDERMOTT |  | 53.3506 | -6.2282
CLONTARF (283000) 38 kV STATION | Clontarf [T42] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 22.3 |  | --> | 9.5 | 0 | 2.9 | 8.4 | 0 |  | --> |  | Mesh: Purple [FingT141,McDrT141] | FINGLAS |  | 53.3668 | -6.2009
SANTRY (315000) 38 kV STATION | Santry [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 22.3 |  | --> | 12.4 | 4.75 | 1.6 | 13.2 | 4.836 |  | --> |  | Mesh: Purple [FingT141,McDrT141] | FINGLAS |  | 53.3928 | -6.2492
MOUNTMELLICK (387000) 38 kV STATION | Mountmellick [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 23.7 |  | --> | 6.2 | 2.375 | 2.1 | 5.4 | 2.422 |  | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 53.0963 | -7.2946
MOUNTRATH (388000) 38 kV STATION | Mountrath [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 23.7 |  | --> | 6.2 | 2.375 | 2 | 5.4 | 2.415 |  | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 52.9827 | -7.4771
PORTLAOISE (201000) 110 kV STATION | Portlaoise [T423,T424] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 5.5 | 23.7 |  | --> | 12.4 | 4.75 | 1.7 | 11.9 | 4.767 |  | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 53.022 | -7.3041
PORTLAOISE (201000) 110 kV STATION | Portlaoise [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 23.7 |  | --> | 12.4 | 4.75 | 1.6 | 13.4 | 5.043 | Constrained, otherwise capacity available =14.83 MW | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 53.022 | -7.3041
PALLAS (559000) 38 kV STATION | Pallas [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 23.7 |  | --> | 6.2 | 2.375 | 2.2 | 5.7 | 2.465 |  | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 53.0378 | -7.3205
PORTARLINGTON (160000) 38 kV STATION | Portarlington [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 23.7 |  | --> | 6.2 | 2.375 | 4.9 | 2.5 | 2.418 |  | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 53.1553 | -7.1994
ABBEYLEIX (565000) 38 kV STATION | Abbeyleix [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.1 | 23.7 |  | --> | 4.8 | 0 | 2.7 | 2.7 | 0 |  | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 52.8889 | -7.2961
TURLOUGH ROAD (042000) 38 kV STATION | Turlough Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.9 | 25 |  | --> | 6.2 | 2.375 | 1.4 | 0 | 0 | Constrained, otherwise capacity available =5.76 MW | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.8678 | -9.2871
KNOCKAPHUNTA (979000) 38 kV STATION | Knockaphunta [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 25 |  | --> | 6.2 | 2.375 | 2.4 | 0 | 0 | Constrained, otherwise capacity available =5.33 MW | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.8352 | -9.3173
WINDSOR (608000) 38 kV STATION | Windsor [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 25 |  | --> | 6.2 | 2.375 | 6 | 0 | 0 | Constrained, otherwise capacity available =2.65 MW | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.8745 | -9.2555
SWINFORD (043000) 38 kV STATION | Swinford [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.4 | 25 |  | --> | 6.2 | 2.375 | 1.7 | 0 | 0 | Constrained, otherwise capacity available =5.87 MW | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.9394 | -8.9569
TURLOUGH ROAD (042000) 38 kV STATION | Turlough Road [T43] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.5 | 25 |  | --> | 4.8 | 0 | 0.3 | 0 | 0 | Constrained, otherwise capacity available =5.1 MW | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.8678 | -9.2871
KILTIMAGH (349000) 38 kV STATION | Kiltimagh [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.4 | 25 |  | --> | 4.8 | 0 | 5.6 | 0 | 0 |  | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.8517 | -9.0045
WESTPORT (116000) 38 kV STATION | Westport [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 8.1 | 25 |  | --> | 12.4 | 4.75 | 3.2 | 0 | 0 | Constrained, otherwise capacity available =10.88 MW | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.7963 | -9.4872
GRANAGH (226000) 38 kV STATION | Granagh [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 25.2 |  | --> | 6.2 | 2.375 | 6.1 | 1.8 | 2.464 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2752 | -7.1748
WATERFORD (808000) 110 kV STATION | Waterford [T41,T42] | 110 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 3.8 | 25.2 |  | --> | 6.2 | 2.375 | 0.3 | 6.7 | 2.39 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2685 | -7.1278
MANOR STREET (346000) 38 kV STATION | Manor Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.5 | 25.2 |  | --> | 12.4 | 4.75 | 1.9 | 13.5 | 4.897 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2516 | -7.1197
TYCOR (286000) 38 kV STATION | Tycor [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1 | 25.2 |  | --> | 6.2 | 2.375 | 1.1 | 6.3 | 2.418 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2539 | -7.1345
MOUNT MISERY (009000) 38 kV STATION | Mount Misery [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 8.2 | 25.2 |  | --> | 12.4 | 4.75 | 7.6 | 7.1 | 4.826 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2659 | -7.1183
BELVIEW (605000) 38 kV STATION | Belview [T421,T422] | 38 kV | _ | MV | 2x15 MVA @ 20 kV | 30 | --> | 22.5 | 3.8 | 25.2 |  | --> | 18.5 | 7.125 | 0.7 | 22.6 | 7.356 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2631 | -7.0386
ROSBERCON (179000) 38 kV STATION | Rosbercon [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0.2 | 25.2 |  | --> | 1.2 | 1.1875 | 6 | 0 | 1.262 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.3977 | -6.9486
ROSBERCON (179000) 38 kV STATION | Rosbercon [T424] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13.2 | 25.2 |  | --> | 14.2 | 0 | 14.3 | 0.3 | 0 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.3977 | -6.9486
KINGSCOURT (122000) 38 kV STATION | Kingscourt [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.2 | 26.4 |  | --> | 12.4 | 4.75 | 2.6 | 0 | 0 | Constrained, otherwise capacity available =11.33 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.8796 | -6.7932
BAILIEBORO (138000) 38 kV STATION | Bailieboro [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2.2 | 26.4 |  | --> | 6.2 | 2.375 | 7.2 | 0 | 0 | Constrained, otherwise capacity available =0.4 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.9033 | -6.9569
MULLAGH (428000) 38 kV STATION | Mullagh [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 4.1 | 26.4 |  | --> | 6.2 | 2.375 | 0 | 0 | 0 | Constrained, otherwise capacity available =6.28 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.8021 | -6.9384
KINGSCOURT (122000) 38 kV STATION | Kingscourt [T423] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13 | 26.4 |  | --> | 14.2 | 0 | 11.5 | 0 | 0 | Constrained, otherwise capacity available =3.05 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.8796 | -6.7932
TULLYNAMALRA (466000) 38 kV STATION | Tullynamalra [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.1 | 26.4 |  | --> | 6.2 | 2.375 | 3.1 | 0 | 0 | Constrained, otherwise capacity available =4.76 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 54.0666 | -6.8262
MULLAGH (428000) 38 kV STATION | Mullagh [T44] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.7 | 26.4 |  | --> | 4.8 | 0 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =4.07 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.8021 | -6.9384
BAILIEBORO (138000) 38 kV STATION | Bailieboro [T423] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13 | 26.4 |  | --> | 14.2 | 0 | 13.5 | 0 | 0 | Constrained, otherwise capacity available =1.23 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.9033 | -6.9569
VIRGINIA (452000) 38 kV STATION | Virginia [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 26.4 |  | --> | 6.2 | 2.375 | 1 | 0 | 0 | Constrained, otherwise capacity available =7.24 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.8085 | -7.0378
CARRICKMACROSS (210000) 38 kV STATION | Carrickmacross [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 26.4 |  | --> | 12.4 | 4.75 | 4.2 | 0 | 0 | Constrained, otherwise capacity available =11.15 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.9862 | -6.7454
SHERCOCK (539000) 38 kV STATION | Shercock [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.5 | 26.4 |  | --> | 6.2 | 2.375 | 0.7 | 0 | 0 | Constrained, otherwise capacity available =7.39 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.9961 | -6.9203
OAKFIELD (240000) 38 kV STATION | Oakfield [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.8 | 27.1 |  | --> | 12.4 | 4.75 | 3.8 | 10.1 | 4.781 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.2573 | -8.505
CRANMORE (046000) 38 kV STATION | Cranmore [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 27.1 |  | --> | 6.2 | 2.375 | 0.9 | 7.3 | 2.529 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.272 | -8.4578
MANORHAMILTON (345000) 38 kV STATION | Manorhamilton [T424] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13 | 27.1 |  | --> | 14.2 | 0 | 13.6 | 1.1 | 0 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.299 | -8.1601
FINISKLIN (511000) 38 kV STATION | Finisklin [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 27.1 |  | --> | 6.2 | 2.375 | 0.1 | 8.2 | 2.54 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.2766 | -8.4905
COLLOONEY (117000) 38 kV STATION | Collooney [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 3.75 | 0 | 27.1 |  | --> | 3.1 | 1.1875 | 5.9 | 0 | 1.369 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.1747 | -8.4924
BALLYMOTE (496000) 38 kV STATION | Ballymote [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.3 | 27.1 |  | --> | 4.8 | 0 | 5.1 | 0.5 | 0 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.0922 | -8.5182
MANORHAMILTON (345000) 38 kV STATION | Manorhamilton [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0 | 27.1 |  | --> | 4.8 | 0 | 1.7 | 4.2 | 0 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.299 | -8.1601
BALLYTIVNAN (445000) 38 kV STATION | Ballytivnan [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.5 | 27.1 |  | --> | 12.4 | 4.75 | 2.5 | 12.8 | 4.883 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.2887 | -8.4701
AGHAGAD (645000) 38 kV STATION | Aghagad [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 4.1 | 27.1 |  | --> | 6.2 | 2.375 | 1.9 | 5 | 2.386 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.3731 | -8.524
BALLYRICKARD (173000) 38 kV STATION | Ballyrickard [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.2 | 28.6 |  | --> | 12.4 | 4.75 | 3 | 10.6 | 4.834 | Constrained, otherwise capacity available =11.86 MW | --> |  | Tralee [T141,T142] | TRALEE |  | 52.2743 | -9.7183
KILFLYNN (137000) 38 kV STATION | Kilflynn [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 3.7 | 28.6 |  | --> | 6.2 | 2.375 | 5.1 | 2.1 | 2.386 |  | --> |  | Tralee [T141,T142] | TRALEE |  | 52.342 | -9.6307
CAUSEWAY (483000) 38 kV STATION | Causeway [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2 | 28.6 |  | --> | 6.2 | 2.375 | 6.7 | 0.6 | 2.409 |  | --> |  | Tralee [T141,T142] | TRALEE |  | 52.4138 | -9.7472
BALLYBEGGAN (462000) 38 kV STATION | Ballybeggan [T43,T44] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 28.6 |  | --> | 12.4 | 4.75 | 3.1 | 10.6 | 4.855 | Constrained, otherwise capacity available =11.98 MW | --> |  | Tralee [T141,T142] | TRALEE |  | 52.2752 | -9.6854
CASTLEISLAND (233000) 38 kV STATION | Castleisland [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 28.6 |  | --> | 6.2 | 2.375 | 9.4 | 0 | 2.464 |  | --> |  | Tralee [T141,T142] | TRALEE |  | 52.2368 | -9.4809
BALLYARD (278000) 38 kV STATION | Ballyard [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.5 | 28.6 |  | --> | 6.2 | 2.375 | 2.1 | 5.5 | 2.433 |  | --> |  | Tralee [T141,T142] | TRALEE |  | 52.2539 | -9.7005
CRUMLIN (259000) 38 kV STATION | Crumlin [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.9 | 29.5 |  | --> | 12.4 | 4.75 | 1.5 | 12.8 | 4.801 |  | --> |  | Mesh: Green [MiltT142,InciT143] | INCHICORE 220KV |  | 53.3214 | -6.3094
DODDER ROAD (330000) 38 kV STATION | Dodder Road [T42] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 2.9 | 29.5 |  | --> | 9.5 | 0 | 2 | 8.6 | 0 |  | --> |  | Mesh: Green [MiltT142,InciT143] | MILLTOWN (DR) |  | 53.3014 | -6.2613
GARVILLE AVENUE (230000) 38 kV STATION | Garville Avenue [T42] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0.9 | 29.5 |  | --> | 9.5 | 0 | 1.3 | 9.8 | 0 |  | --> |  | Mesh: Green [MiltT142,InciT143] | MILLTOWN (DR) |  | 53.3199 | -6.2755
GREENHILLS (290000) 38 kV STATION | Greenhills [T42] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 3.3 | 29.5 |  | --> | 9.5 | 0 | 1.4 | 9.1 | 0 |  | --> |  | Mesh: Green [MiltT142,InciT143] | INCHICORE 220KV |  | 53.3166 | -6.3254
KIMMAGE (145000) 38 kV STATION | Kimmage [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.9 | 29.5 |  | --> | 12.4 | 4.75 | 3.6 | 11.3 | 4.843 |  | --> |  | Mesh: Green [MiltT142,InciT143] | INCHICORE 220KV |  | 53.3076 | -6.3089
TEMPLEOGUE (146000) 38 kV STATION | Templeogue [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.5 | 29.5 |  | --> | 12.4 | 4.75 | 4.7 | 9.5 | 4.794 |  | --> |  | Mesh: Green [MiltT142,InciT143] | MILLTOWN (DR) |  | 53.3005 | -6.308
BELLFIELD (006000) 38 kV STATION | Bellfield [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.1 | 3.1 | Constrained, otherwise capacity available =5.19 MVA | --> | 12.4 | 4.75 | 2.7 | 0 | 0 | Constrained, otherwise capacity available =11.21 MW | --> |  | Crane [T141] | CRANE |  | 52.5084 | -6.5651
BUNCLODY (470000) 38 kV STATION | Bunclody [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 1.1 | 3.1 |  | --> | 6.2 | 2.375 | 2.1 | 0 | 0 | Constrained, otherwise capacity available =5.6 MW | --> |  | Crane [T141] | CRANE |  | 52.6432 | -6.6311
BUNCLODY (470000) 38 kV STATION | Bunclody [T424] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 3.1 | 3.1 | Constrained, otherwise capacity available =8.82 MVA | --> | 9.5 | 0 | 7.5 | 0 | 0 | Constrained, otherwise capacity available =2.33 MW | --> |  | Crane [T141] | CRANE |  | 52.6432 | -6.6311
RAMSTOWN (287000) 38 kV STATION | Ramstown [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 3 | 3.1 |  | --> | 6.2 | 2.375 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =5.95 MW | --> |  | Crane [T141] | CRANE |  | 52.6637 | -6.3193
FERNS (075000) 38 kV STATION | Ferns [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.6 | 3.1 |  | --> | 4.8 | 0 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =4.2 MW | --> |  | Crane [T141] | CRANE |  | 52.5871 | -6.5101
KINSALE (225000) 38 kV STATION | Kinsale [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 3.2 |  | --> | 6.2 | 2.375 | 7.4 | 0.6 | 2.485 |  | --> |  | Bandon [T141,T142] | BANDON |  | 51.7193 | -8.5569
BEALNABLATH (235000) 38 kV STATION | Bealnablath [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 3.2 | 3.2 | Constrained, otherwise capacity available =4.5 MVA | --> | 4.8 | 0 | 0 | 4.8 | 0 |  | --> |  | Bandon [T141,T142] | BANDON |  | 51.8282 | -8.8934
BEALNABLATH (235000) 38 kV STATION | Bealnablath [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 3.2 |  | --> | 9.5 | 0 | 11.4 | 0.4 | 0 |  | --> |  | Bandon [T141,T142] | BANDON |  | 51.8282 | -8.8934
ENNISKEANE (090000) 38 kV STATION | Enniskeane [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 3.2 | 3.2 | Constrained, otherwise capacity available =5.59 MVA | --> | 6.2 | 2.375 | 7.9 | 0 | 2.375 |  | --> |  | Bandon [T141,T142] | BANDON |  | 51.744 | -8.9399
TIMOLEAGUE (163000) 38 kV STATION | Timoleague [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 3.2 |  | --> | 4.8 | 0 | 6.9 | 0 | 0 |  | --> |  | Bandon [T141,T142] | BANDON |  | 51.6825 | -8.7671
NEWBROOK (465000) 38 kV STATION | Newbrook [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 3.4 |  | --> | 4.8 | 0 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =4.69 MW | --> |  | Mullingar [T141,T142] | MULLINGAR |  | 53.5214 | -7.3821
BALLINDERRY (383000) 38 kV STATION | Ballinderry [T41,T422] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 3.4 |  | --> | 12.4 | 4.75 | 9 | 0 | 0 | Constrained, otherwise capacity available =6.03 MW | --> |  | Mullingar [T141,T142] | MULLINGAR |  | 53.5134 | -7.3166
LOUGHANALLA (613000) 38 kV STATION | Loughanalla [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.3 | 3.4 |  | --> | 6.2 | 2.375 | 4 | 0 | 0 | Constrained, otherwise capacity available =3.03 MW | --> |  | Mullingar [T141,T142] | MULLINGAR |  | 53.6761 | -7.3044
DELVIN (123000) 38 kV STATION | Delvin [T41,T42] | 38 kV | _ | MV | 1x3.2,1x5 MVA @ 10 kV | 8.2 | --> | 2.4 | 0 | 3.4 |  | --> | 2 | 1.1875 | 2 | 0 | 0 | Constrained, otherwise capacity available =0.69 MW | --> |  | Mullingar [T141,T142] | MULLINGAR |  | 53.6035 | -7.0789
OLDCASTLE (538000) 38 kV STATION | Oldcastle [T41,T422] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2.7 | 3.4 |  | --> | 6.2 | 2.375 | 5 | 0 | 0 | Constrained, otherwise capacity available =2.03 MW | --> |  | Mullingar [T141,T142] | MULLINGAR |  | 53.7816 | -7.1696
MONFIN (297000) 38 kV STATION | Monfin [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 5.25 | 1.3 | 33.6 |  | --> | 2.5 | 2.375 | 0.9 | 2 | 2.399 |  | --> |  | Wexford [T141,T142] | WEXFORD |  | 52.4915 | -6.5881
CLONROCHE (515000) 38 kV STATION | Clonroche [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 33.6 |  | --> | 6.2 | 2.375 | 3.1 | 4.2 | 2.409 |  | --> |  | Wexford [T141,T142] | WEXFORD |  | 52.4438 | -6.6979
CARRIGLAWN (188000) 38 kV STATION | Carriglawn [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.1 | 33.6 |  | --> | 6.2 | 2.375 | 1.6 | 6.1 | 2.443 |  | --> |  | Wexford [T141,T142] | WEXFORD |  | 52.3464 | -6.4809
CLONARD (547000) 38 kV STATION | Clonard [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.9 | 33.6 |  | --> | 6.2 | 2.375 | 1.7 | 5.8 | 2.423 |  | --> |  | Wexford [T141,T142] | WEXFORD |  | 52.3265 | -6.4957
KILLINICK (298000) 38 kV STATION | Killinick [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 1.4 | 33.6 |  | --> | 12.4 | 4.75 | 12.3 | 2.7 | 4.843 |  | --> |  | Wexford [T141,T142] | WEXFORD |  | 52.2534 | -6.4483
MULGANNON (174000) 38 kV STATION | Mulgannon [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 33.6 |  | --> | 12.4 | 4.75 | 2.6 | 14.1 | 5.128 |  | --> |  | Wexford [T141,T142] | WEXFORD |  | 52.3204 | -6.4567
FASSAROE (678000) 110 kV STATION | Fassaroe [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 19.8 | 348.6 |  | --> | 77.8 | 0 | 19.9 | 71.2 | 0 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.191 | -6.1672
BALLYBEG (781000) 110 kV STATION | Ballybeg [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 11.6 | 348.6 |  | --> | 24.7 | 9.5 | 24.5 | 3.6 | 9.573 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 52.9969 | -6.1046
COOKSTOWN (672000) 110 kV STATION | Cookstown [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13.9 | 348.6 |  | --> | 24.7 | 9.5 | 1.2 | 28.6 | 9.677 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2947 | -6.3826
CARRICKMINES (649000) 220 kV STATION | Carrickmines [T141,T142] | 220 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 1.2 | 348.6 |  | --> | 77.8 | 0 | 35.6 | 60.5 | 0 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2549 | -6.1921
CHERRYWOOD (499000) 110 kV STATION | Cherrywood [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 70.4 | 348.6 |  | --> | 77.8 | 0 | 8.1 | 73 | 0 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2412 | -6.1614
CHERRYWOOD (499000) 110 kV STATION | Cherrywood [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 30 | 348.6 |  | --> | 24.7 | 9.5 | 0 | 24.7 | 9.5 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2412 | -6.1614
CENTRAL PARK (993000) 110 kV STATION | Central Park [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 15.2 | 348.6 |  | --> | 24.7 | 9.5 | 0.6 | 27.9 | 9.593 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2678 | -6.2094
POTTERY ROAD (317000) 110 kV STATION | Pottery Road [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13.4 | 348.6 |  | --> | 24.7 | 9.5 | 2.9 | 26.8 | 9.673 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2765 | -6.1586
TANEY (953000) 110 kV STATION | Taney [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 19.5 | 348.6 |  | --> | 24.7 | 9.5 | 0.8 | 25.8 | 9.52 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2846 | -6.2385
BELFIELD (310000) 38 kV STATION | Belfield [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.9 | 36.3 |  | --> | 12.4 | 4.75 | 2.4 | 13.5 | 4.949 |  | --> |  | Blackrock [T141,T142] | BLACKROCK |  | 53.31 | -6.2168
DUNDRUM (134000) 38 kV STATION | Dundrum [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 36.3 |  | --> | 12.4 | 4.75 | 5.6 | 9.4 | 4.845 |  | --> |  | Blackrock [T141,T142] | BLACKROCK |  | 53.2963 | -6.2488
MONKSTOWN (222000) 38 kV STATION | Monkstown [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.5 | 36.3 |  | --> | 12.4 | 4.75 | 3.8 | 11 | 4.831 |  | --> |  | Blackrock [T141,T142] | BLACKROCK |  | 53.292 | -6.1664
DUN LAOGHAIRE (284000) 38 kV STATION | Dun Laoghaire [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.4 | 36.3 |  | --> | 12.4 | 4.75 | 1 | 13.4 | 4.801 |  | --> |  | Blackrock [T141,T142] | BLACKROCK |  | 53.2966 | -6.1497
BEDFORD ROW (068000) 38 kV STATION | Bedford Row [T41,T42,T43,T44] | 38 kV | _ | MV | 4x15 MVA @ 10 kV | 60 | --> | 54 | 28.4 | 36.8 |  | --> | 57 | 7.125 | 1 | 62.8 | 7.173 |  | --> |  | Mesh: Brown [FranT141,RingT144] | FRANCIS STREET |  | 53.3437 | -6.2564
SOUTH KING STREET (241000) 38 kV STATION | South King Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.4 | 36.8 |  | --> | 12.4 | 4.75 | 0 | 15.1 | 4.86 |  | --> |  | Mesh: Brown [FranT141,RingT144] | FRANCIS STREET |  | 53.3423 | -6.269
SHERIFF STREET (588000) 38 kV STATION | Sheriff Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 7.6 | 36.8 |  | --> | 12.4 | 4.75 | 0.3 | 13.3 | 4.769 |  | --> |  | Mesh: Brown [FranT141,RingT144] | FRANCIS STREET |  | 53.3488 | -6.2392
CLOONBANNIN (070000) 38 kV STATION | Cloonbannin [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 2.2 | 38.7 |  | --> | 4.8 | 0 | 0.4 | 4.6 | 0 |  | --> |  | Glenlara [T142] | GLENLARA |  | 52.1372 | -9.0556
NEWMARKET (SR) (481000) 38 kV STATION | Newmarket (sr) [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 4.2 | 38.7 |  | --> | 6.2 | 2.375 | 1.2 | 6.3 | 2.423 |  | --> |  | Glenlara [T142] | GLENLARA |  | 52.21 | -8.9982
KANTURK (119000) 38 kV STATION | Kanturk [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 38.7 |  | --> | 6.2 | 2.375 | 7.4 | 1.2 | 2.646 |  | --> |  | Glenlara [T142] | GLENLARA |  | 52.165 | -8.917
CLOONBANNIN (070000) 38 kV STATION | Cloonbannin [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.6 | 38.7 |  | --> | 4.8 | 0 | 0.7 | 4.5 | 0 |  | --> |  | Glenlara [T142] | GLENLARA |  | 52.1372 | -9.0556
NENAGH (946000) 110 kV STATION | Nenagh [T422] | 110 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 4.1 | 4.1 | Constrained, otherwise capacity available =8.74 MVA | --> | 9.5 | 0 | 9.6 | 0.2 | 0 |  | --> |  | Nenagh [T141] | NENAGH |  | 52.8664 | -8.1737
NENAGH (946000) 110 kV STATION | Nenagh [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3 | 4.1 |  | --> | 12.4 | 4.75 | 5.5 | 9 | 4.812 |  | --> |  | Nenagh [T141] | NENAGH |  | 52.8664 | -8.1737
KYLEERAGH (421000) 38 kV STATION | Kyleeragh [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 11.25 | 0 | 4.1 |  | --> | 6.2 | 4.75 | 2.5 | 6.4 | 5.958 |  | --> |  | Nenagh [T141] | NENAGH |  | 52.8742 | -8.1818
TOOMEVARA (385000) 38 kV STATION | Toomevara [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.2 | 4.1 |  | --> | 4.8 | 0 | 6.9 | 0 | 0 |  | --> |  | Nenagh [T141] | NENAGH |  | 52.8734 | -8.0397
CARNDONAGH (266000) 38 kV STATION | Carndonagh [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 4.9 |  | --> | 6.2 | 2.375 | 2.1 | 0 | 0 | Constrained, otherwise capacity available =5.6 MW | --> |  | Trillick [T141] | TRILLICK |  | 55.2526 | -7.26
BUNCRANA (204000) 38 kV STATION | Buncrana [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 4.9 |  | --> | 6.2 | 2.375 | 40.1 | 0 | 0 |  | --> |  | Trillick [T141] | TRILLICK |  | 55.1336 | -7.437
BALLYMACARRY (607000) 38 kV STATION | Ballymacarry [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 2 | 4.9 |  | --> | 4.8 | 0 | 0.4 | 0 | 0 | Constrained, otherwise capacity available =4.72 MW | --> |  | Trillick [T141] | TRILLICK |  | 55.1278 | -7.4459
MOVILLE (405000) 38 kV STATION | Moville [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 3 | 4.9 |  | --> | 6.2 | 2.375 | 5.4 | 0 | 0 | Constrained, otherwise capacity available =1.91 MW | --> |  | Trillick [T141] | TRILLICK |  | 55.1994 | -7.0601
BANTRY (111000) 38 kV STATION | Bantry [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 42.2 |  | --> | 6.2 | 2.375 | 5.8 | 0 | 0 | Constrained, otherwise capacity available =2.12 MW | --> |  | Ballylicky [T142] | BALLYLICKY |  | 51.6828 | -9.4156
GLENGARRIFF (384000) 38 kV STATION | Glengarriff [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 3.5 | 42.2 |  | --> | 4.8 | 0 | 0.4 | 0 | 0 | Constrained, otherwise capacity available =4.58 MW | --> |  | Ballylicky [T142] | BALLYLICKY |  | 51.7541 | -9.535
CASTLETOWNBERE (513000) 38 kV STATION | Castletownbere [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 3.6 | 42.2 |  | --> | 4.8 | 0 | 0.1 | 0 | 0 | Constrained, otherwise capacity available =4.91 MW | --> |  | Ballylicky [T142] | BALLYLICKY |  | 51.6478 | -9.9112
CASTLETOWNBERE (513000) 38 kV STATION | Castletownbere [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.9 | 42.2 |  | --> | 4.8 | 0 | 1.9 | 0 | 0 | Constrained, otherwise capacity available =3.61 MW | --> |  | Ballylicky [T142] | BALLYLICKY |  | 51.6478 | -9.9112
BALLYLICKY (728000) 110 kV STATION | Ballylicky [T421] | 110 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 42.2 |  | --> | 9.5 | 0 | 5.8 | 0 | 0 | Constrained, otherwise capacity available =3.98 MW | --> |  | Ballylicky [T142] | BALLYLICKY |  | 51.7191 | -9.4235
BALLYDEHOB (535000) 38 kV STATION | Ballydehob [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0 | 43.9 |  | --> | 4.8 | 0 | 2.1 | 3.5 | 0 |  | --> |  | Dunmanway [T141,T142] | DUNMANWAY |  | 51.5611 | -9.485
DUNMANWAY (676000) 110 kV STATION | Dunmanway [T422,T43] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 7.8 | 43.9 |  | --> | 12.4 | 4.75 | 8.4 | 5.6 | 4.772 |  | --> |  | Dunmanway [T141,T142] | DUNMANWAY |  | 51.7167 | -9.0773
SKIBBEREEN (164000) 38 kV STATION | Skibbereen [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 43.9 |  | --> | 6.2 | 2.375 | 7.5 | 0.9 | 2.507 |  | --> |  | Dunmanway [T141,T142] | DUNMANWAY |  | 51.567 | -9.255
ROSS CARBERY (352000) 38 kV STATION | Ross Carbery [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.9 | 43.9 |  | --> | 6.2 | 2.375 | 6.3 | 0.9 | 2.392 |  | --> |  | Dunmanway [T141,T142] | DUNMANWAY |  | 51.6071 | -9.0157
CLONAKILTY (165000) 38 kV STATION | Clonakilty [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 43.9 |  | --> | 6.2 | 2.375 | 3.7 | 4.6 | 2.538 |  | --> |  | Dunmanway [T141,T142] | DUNMANWAY |  | 51.6279 | -8.8884
BALLYCONNELL (571000) 38 kV STATION | Ballyconnell [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0.1 | 44.4 |  | --> | 6.2 | 2.375 | 8.3 | 0 | 2.46 |  | --> |  | Gortawee [T142] | GORTAWEE |  | 54.1215 | -7.6071
KILLESHANDRA (265000) 38 kV STATION | Killeshandra [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2.6 | 44.4 |  | --> | 6.2 | 2.375 | 0.9 | 7.2 | 2.494 |  | --> |  | Gortawee [T142] | GORTAWEE |  | 54.026 | -7.5458
TRIMMS LANE (427000) 38 kV STATION | Trimms Lane [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.5 | 44.9 |  | --> | 12.4 | 4.75 | 1.4 | 13.3 | 4.823 |  | --> |  | Salthill [T141] | SALTHILL |  | 53.2643 | -9.0739
DRUMBEAR (156000) 38 kV STATION | Drumbear [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 5.9 |  | --> | 6.2 | 2.375 | 1.9 | 0 | 0 | Constrained, otherwise capacity available =5.88 MW | --> |  | Lisdrum [T141,T142] | LISDRUM |  | 54.2263 | -6.9847
TELAYDON (415000) 38 kV STATION | Telaydon [T42,T421] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.5 | 5.9 |  | --> | 12.4 | 4.75 | 3.7 | 0 | 0 | Constrained, otherwise capacity available =11.02 MW | --> |  | Lisdrum [T141,T142] | LISDRUM |  | 54.2688 | -6.9899
BALLYBAY (061000) 38 kV STATION | Ballybay [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2 | 5.9 |  | --> | 6.2 | 2.375 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =6.07 MW | --> |  | Lisdrum [T141,T142] | LISDRUM |  | 54.1259 | -6.9173
LISDRUM (624000) 110 kV STATION | Lisdrum [T422] | 110 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 2.1 | 5.9 |  | --> | 4.8 | 0 | 0.8 | 0 | 0 | Constrained, otherwise capacity available =4.61 MW | --> |  | Lisdrum [T141,T142] | LISDRUM |  | 54.2488 | -6.9279
EMYVALE (502000) 38 kV STATION | Emyvale [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0 | 5.9 |  | --> | 4.8 | 0 | 1.4 | 0 | 0 | Constrained, otherwise capacity available =4.15 MW | --> |  | Lisdrum [T141,T142] | LISDRUM |  | 54.355 | -7.0362
BELMULLET (500000) 38 kV STATION | Belmullet [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.6 | 51.8 |  | --> | 4.8 | 0 | 13.2 | 0 | 0 |  | --> |  | Bellacorick [T141] | BELLACORICK |  | 54.2057 | -9.9522
BANGOR ERRIS (206000) 38 kV STATION | Bangor Erris [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 2.8 | 51.8 |  | --> | 4.8 | 0 | 0.3 | 4.9 | 0 |  | --> |  | Bellacorick [T141] | BELLACORICK |  | 54.1568 | -9.7598
TINAHASK (362000) 38 kV STATION | Tinahask [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 53.6 |  | --> | 6.2 | 2.375 | 2.8 | 0 | 0 | Constrained, otherwise capacity available =5 MW | --> |  | Arklow [T141,T142] | ARKLOW |  | 52.7921 | -6.1724
KILMARTIN (332000) 38 kV STATION | Kilmartin [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.5 | 53.6 |  | --> | 4.8 | 0 | 1.7 | 0 | 0 | Constrained, otherwise capacity available =4.27 MW | --> |  | Arklow [T141,T142] | ARKLOW |  | 53.0421 | -6.0865
RATHDRUM (602000) 38 kV STATION | Rathdrum [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 53.6 |  | --> | 4.8 | 0 | 6.7 | 0 | 0 |  | --> |  | Arklow [T141,T142] | ARKLOW |  | 52.9421 | -6.2583
GARDEN CITY (005000) 38 kV STATION | Garden City [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 53.6 |  | --> | 6.2 | 2.375 | 2.3 | 0 | 0 | Constrained, otherwise capacity available =5.87 MW | --> |  | Arklow [T141,T142] | ARKLOW |  | 52.6682 | -6.3057
KILMAGIG (301000) 38 kV STATION | Kilmagig [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.4 | 53.6 |  | --> | 4.8 | 0 | 0.8 | 0 | 0 | Constrained, otherwise capacity available =4.46 MW | --> |  | Arklow [T141,T142] | ARKLOW |  | 52.8551 | -6.2193
MULTEEN (752000) 38 kV STATION | Multeen [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 8.4 | 54.7 |  | --> | 9.5 | 0 | 9.7 | 0 | 0 | Constrained, otherwise capacity available =0.15 MW | --> |  | Cauteen [T141] | CAUTEEN |  | 52.6482 | -8.1336
BOOLTIAGH (887000) 110 kV STATION | Booltiagh [T421] | 110 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 12.6 | 56.4 |  | --> | 14.2 | 0 | 13.7 | 0 | 0 | Constrained, otherwise capacity available =0.95 MW | --> |  | Booltiagh [T143] | BOOLTIAGH |  | 52.7667 | -9.2556
HAROLDS CROSS (343000) 110 kV STATION | Harolds Cross [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 10 | 57.1 |  | --> | 24.7 | 9.5 | 1.7 | 28.1 | 9.672 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3321 | -6.2726
MILLTOWN (DR) (069000) 110 kV STATION | Mesh: Blue [RingT141,MiltT141] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 21.3 | 57.1 |  | --> | 77.8 | 0 | 2.8 | 89.8 | 0 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3176 | -6.2456
TRINITY (494000) 110 kV STATION | Trinity [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 7.2 | 57.1 |  | --> | 24.7 | 9.5 | 0.1 | 29.7 | 9.684 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3456 | -6.2435
RINGSEND (998000) 110 kV STATION | Ringsend [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 17.8 | 57.1 |  | --> | 24.7 | 9.5 | 0.1 | 29.4 | 9.653 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3447 | -6.2005
FRANCIS STREET (733000) 110 kV STATION | Mesh: Brown [FranT141,RingT144] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 36.8 | 57.1 |  | --> | 77.8 | 0 | 1.3 | 87.6 | 0 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3374 | -6.2793
NORTH QUAYS (981000) 110 kV STATION | North Quays [T101,T102,T103] | 110 kV | _ | MV | 3x20 MVA @ 10 kV | 60 | --> | 54 | 14.3 | 57.1 |  | --> | 57 | 9.5 | 0.9 | 62.7 | 9.557 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3532 | -6.2311
BLACKROCK (338000) 110 kV STATION | Blackrock [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 36.3 | 57.1 |  | --> | 77.8 | 0 | 29.1 | 64 | 0 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.2934 | -6.1704
MISERY HILL (980000) 110 kV STATION | Misery Hill [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 9 | 57.1 |  | --> | 24.7 | 9.5 | 0.2 | 29.7 | 9.688 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3412 | -6.2458
TUBBERCURRY (355000) 38 kV STATION | Tubbercurry [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0.1 | 6.1 |  | --> | 1.2 | 1.1875 | 1.3 | 0.5 | 1.407 |  | --> |  | Tonroe [T142] | TONROE |  | 54.0575 | -8.7418
CHARLESTOWN (078000) 38 kV STATION | Charlestown [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 6.1 |  | --> | 4.8 | 0 | 3.4 | 2.3 | 0 |  | --> |  | Tonroe [T142] | TONROE |  | 53.9536 | -8.7931
BALLAGHADERREEN (433000) 38 kV STATION | Ballaghaderreen [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 6.1 |  | --> | 6.2 | 2.375 | 6 | 2.5 | 2.536 |  | --> |  | Tonroe [T142] | TONROE |  | 53.919 | -8.5832
GURTEEN (045000) 38 kV STATION | Gurteen [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.4 | 6.1 |  | --> | 4.8 | 0 | 1 | 4.2 | 0 |  | --> |  | Tonroe [T142] | TONROE |  | 53.9883 | -8.5242
BANAGHER (305000) 38 kV STATION | Banagher [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 3.75 | 0.3 | 6.4 |  | --> | 3.1 | 1.1875 | 0.9 | 2.8 | 1.208 |  | --> |  | Dallow [T141] | DALLOW |  | 53.1941 | -8.0279
BIRR (056000) 38 kV STATION | Birr [T41,T422] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.9 | 6.4 |  | --> | 12.4 | 4.75 | 10.2 | 4.4 | 4.423 | Constrained, otherwise capacity available =4.58 MW | --> |  | Dallow [T141] | DALLOW |  | 53.0789 | -7.8766
LUMCLOON (147000) 38 kV STATION | Lumcloon [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 9 | 4.6 | 6.4 |  | --> | 9.5 | 9.5 | 6.3 | 4.2 | 4.423 |  | --> |  | Dallow [T141] | DALLOW |  | 53.2308 | -7.8337
DALLOW (673000) 110 kV STATION | Dallow [T421] | 110 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 6.4 | 6.4 | Constrained, otherwise capacity available =8.81 MVA | --> | 9.5 | 0 | 10 | 0 | 0 |  | --> |  | Dallow [T141] | DALLOW |  | 53.1167 | -7.9381
SCREEB (366000) 110 kV STATION | Screeb [T41] | 110 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.5 | 6.9 |  | --> | 4.8 | 0 | 0.9 | 4.6 | 0 |  | --> |  | Screeb [T142] | SCREEB |  | 53.3894 | -9.5708
CLIFDEN (252000) 38 kV STATION | Clifden [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.3 | 6.9 |  | --> | 6.2 | 2.375 | 1.7 | 5.9 | 2.441 |  | --> |  | Screeb [T142] | SCREEB |  | 53.4846 | -10.0109
OUGHTERARD (444000) 38 kV STATION | Oughterard [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 6.5 | 6.9 |  | --> | 6.2 | 2.375 | 2.1 | 4.1 | 2.375 |  | --> |  | Screeb [T142] | SCREEB |  | 53.4249 | -9.3117
CARRAROE (475000) 38 kV STATION | Carraroe [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.4 | 6.9 |  | --> | 4.8 | 0 | 4.5 | 1.5 | 0 |  | --> |  | Screeb [T142] | SCREEB |  | 53.2748 | -9.5356
SPIDDAL (443000) 38 kV STATION | Spiddal [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 4.5 | 6.9 |  | --> | 4.8 | 0 | 3.3 | 1.7 | 0 |  | --> |  | Screeb [T142] | SCREEB |  | 53.2582 | -9.3209
RECESS (581000) 38 kV STATION | Recess [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.8 | 6.9 |  | --> | 4.8 | 0 | 0.7 | 4.4 | 0 |  | --> |  | Screeb [T142] | SCREEB |  | 53.4543 | -9.7555
SRAH (484000) 38 kV STATION | Srah [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2.4 | 65.1 |  | --> | 6.2 | 2.375 | 6.5 | 0.9 | 2.42 |  | --> |  | Thornsberry [T141,T142] | THORNSBERRY |  | 53.2828 | -7.5199
CLARA (051000) 38 kV STATION | Clara [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 2.2 | 65.1 |  | --> | 12.4 | 4.75 | 6.6 | 8 | 4.821 |  | --> |  | Thornsberry [T141,T142] | THORNSBERRY |  | 53.3524 | -7.5884
CLONMINCH (650000) 38 kV STATION | Clonminch [T41,T422] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 65.1 |  | --> | 12.4 | 4.75 | 3.6 | 12.2 | 4.932 |  | --> |  | Thornsberry [T141,T142] | THORNSBERRY |  | 53.2586 | -7.4934
SRAH (484000) 38 kV STATION | Srah [T43] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 3.3 | 65.1 |  | --> | 9.5 | 0 | 0.9 | 9.8 | 0 |  | --> |  | Thornsberry [T141,T142] | THORNSBERRY |  | 53.2828 | -7.5199
GLENTIES (216000) 38 kV STATION | Glenties [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0 | 66.6 |  | --> | 1.2 | 1.1875 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =0.43 MW | --> |  | Binbane [T141,T142] | BINBANE |  | 54.7693 | -8.3082
KILLYBEGS (255000) 38 kV STATION | Killybegs [T422] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 0 | 66.6 |  | --> | 14.2 | 0 | 4.3 | 0 | 0 | Constrained, otherwise capacity available =12.31 MW | --> |  | Binbane [T141,T142] | BINBANE |  | 54.6554 | -8.4439
KILCAR (501000) 38 kV STATION | Kilcar [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.1 | 66.6 |  | --> | 4.8 | 0 | 3.1 | 0 | 0 | Constrained, otherwise capacity available =2.95 MW | --> |  | Binbane [T141,T142] | BINBANE |  | 54.6385 | -8.572
KILLYBEGS (255000) 38 kV STATION | Killybegs [T41] | 38 kV | _ | MV | 1x15 MVA @ 10 kV | 15 | --> | 13.5 | 13.5 | 66.6 |  | --> | 14.2 | 0 | 4.2 | 0 | 0 | Constrained, otherwise capacity available =10.35 MW | --> |  | Binbane [T141,T142] | BINBANE |  | 54.6554 | -8.4439
INCHICORE 220KV (964000) 220 kV STATION | Inchicore County 220/110 kV [T2101,T2106] | 220 kV | _ | 110 kV | 2x250 MVA @ 110 kV | 500 | --> | 350 | 0 | 67.1 |  | --> | 308.8 | 0 | 160.9 | 227.6 | 0 |  | --> |  | Transmission Source | INCHICORE 220KV |  | 53.3313 | -6.3371
BUSHFIELD (478000) 38 kV STATION | Bushfield [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 6.5 | 7.6 |  | --> | 12.4 | 4.75 | 3.1 | 12.3 | 4.884 |  | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.4341 | -7.9082
CREAGH (519000) 38 kV STATION | Creagh [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 7.6 |  | --> | 6.2 | 2.375 | 7.5 | 0.6 | 2.508 |  | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.3294 | -8.2061
BALLYGAR (324000) 38 kV STATION | Ballygar [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 3.75 | 0 | 7.6 |  | --> | 3.1 | 1.1875 | 1.2 | 2.8 | 1.235 |  | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.5265 | -8.306
GLENAMADDY (526000) 38 kV STATION | Glenamaddy [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0 | 7.6 |  | --> | 4.8 | 0 | 6.1 | 0 | 0 |  | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.6158 | -8.5908
BALLYMAHON (076000) 38 kV STATION | Ballymahon [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.1 | 7.6 |  | --> | 6.2 | 2.375 | 1.5 | 6 | 2.424 |  | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.5965 | -7.804
GARRYCASTLE (976000) 38 kV STATION | Garrycastle [T41,T42] | 38 kV | _ | MV | 2x15 MVA @ 10 kV | 30 | --> | 22.5 | 7.6 | 7.6 | Constrained, otherwise capacity available =9.45 MVA | --> | 18.5 | 7.125 | 2.5 | 15.5 | 7.213 | Constrained, otherwise capacity available =19.23 MW | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.426 | -7.8904
MOATE (073000) 38 kV STATION | Moate [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 3.75 | 0 | 7.6 |  | --> | 3.1 | 1.1875 | 2.4 | 1.5 | 1.226 |  | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.386 | -7.7209
ATHLONE (897000) 110 kV STATION | Athlone [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 7.6 |  | --> | 12.4 | 4.75 | 4.3 | 12.4 | 5.109 |  | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.4256 | -7.9672
CHARLEVILLE (456000) 110 kV STATION | Charleville [T421,T422] | 110 kV | _ | MV | 1x10,1x15 MVA @ 20 kV | 25 | --> | 18.75 | 3 | 7.9 |  | --> | 12.4 | 7.125 | 16 | 0 | 0 |  | --> |  | Charleville [T142] | CHARLEVILLE |  | 52.325 | -8.7025
CARROWBEG (699000) 110 kV STATION | Carrowbeg [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 7.3 | 7.9 |  | --> | 12.4 | 4.75 | 1.8 | 12.3 | 4.785 |  | --> |  | Carrowbeg [T142] | CARROWBEG |  | 53.8048 | -9.5016
CARROWBEG (699000) 110 kV STATION | Carrowbeg [T421] | 110 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 3 | 7.9 |  | --> | 9.5 | 0 | 0 | 12.1 | 0 |  | --> |  | Carrowbeg [T142] | CARROWBEG |  | 53.8048 | -9.5016
MILFORD (MWR) (236000) 38 kV STATION | Milford (mwr) [T422] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 6.2 | 7.9 |  | --> | 9.5 | 0 | 10 | 0 | 0 | Constrained, otherwise capacity available =1.65 MW | --> |  | Charleville [T142] | CHARLEVILLE |  | 52.3333 | -8.8451
MILFORD (MWR) (236000) 38 kV STATION | Milford (mwr) [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.9 | 7.9 |  | --> | 4.8 | 0 | 0.7 | 0 | 0 | Constrained, otherwise capacity available =4.5 MW | --> |  | Charleville [T142] | CHARLEVILLE |  | 52.3333 | -8.8451
ACHILL (495000) 38 kV STATION | Achill [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.5 | 7.9 |  | --> | 4.8 | 0 | 1.1 | 4.4 | 0 |  | --> |  | Carrowbeg [T142] | CARROWBEG |  | 53.9495 | -9.9002
NEWPORT (260000) 38 kV STATION | Newport [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.7 | 7.9 |  | --> | 4.8 | 0 | 1.8 | 3.5 | 0 |  | --> |  | Carrowbeg [T142] | CARROWBEG |  | 53.8858 | -9.5017
KILMALLOCK (412000) 38 kV STATION | Kilmallock [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 3.75 | 0 | 7.9 |  | --> | 3.1 | 1.1875 | 1.2 | 0 | 0 | Constrained, otherwise capacity available =2.71 MW | --> |  | Charleville [T142] | CHARLEVILLE |  | 52.4131 | -8.5896
SALLYNOGGIN ROAD (133000) 38 kV STATION | Sallynoggin Road [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.2 | 70.4 |  | --> | 12.4 | 4.75 | 5.9 | 8.7 | 4.815 |  | --> |  | Cherrywood [T141,T142] | CHERRYWOOD |  | 53.281 | -6.1416
BALLINCLEA (396000) 38 kV STATION | Ballinclea [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 4 | 70.4 |  | --> | 9.5 | 0 | 2.2 | 8.1 | 0 |  | --> |  | Cherrywood [T141,T142] | CHERRYWOOD |  | 53.2683 | -6.1245
CARRIGTWOHILL (351000) 38 kV STATION | Carrigtwohill [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.3 | 8.8 |  | --> | 4.8 | 0 | 0 | 6.1 | 0 |  | --> |  | Cow Cross [T142] | COW CROSS |  | 51.8928 | -8.2549
CABRA (231000) 110 kV STATION | Cabra [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 11.1 | 87.1 |  | --> | 24.7 | 9.5 | 3.3 | 25.4 | 9.6 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.3695 | -6.294
WOLFE TONE STREET (769000) 110 kV STATION | Wolfe Tone Street [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 2.6 | 87.1 |  | --> | 24.7 | 9.5 | 0.4 | 30.2 | 9.751 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.3519 | -6.2732
FINGLAS (318000) 220 kV STATION | Mesh: Purple [FingT141,McDrT141] | 220 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 22.3 | 87.1 |  | --> | 77.8 | 0 | 10 | 81.1 | 0 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.4075 | -6.3161
ARTANE (966000) 110 kV STATION | Artane [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13 | 87.1 |  | --> | 24.7 | 9.5 | 4.1 | 23.3 | 9.54 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.3903 | -6.1919
FINGLAS (318000) 220 kV STATION | Mesh: Orange [FingT142,McDrT142] | 220 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | 87.1 |  | --> | 77.8 | 0 | 7.9 | 87 | 0 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.4075 | -6.3161
PELLETSTOWN (092000) 110 kV STATION | Pelletstown [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 7.9 | 87.1 |  | --> | 24.7 | 9.5 | 4.9 | 23.4 | 9.579 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.3788 | -6.3228
AGHAMORE (124000) 38 kV STATION | Aghamore [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0 | 9.2 |  | --> | 1.2 | 1.1875 | 1.6 | 0.2 | 1.341 |  | --> |  | Lanesboro [T141] | LANESBORO |  | 53.6642 | -7.9855
ROSCOMMON (136000) 38 kV STATION | Roscommon [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 9.2 |  | --> | 12.4 | 4.75 | 11.7 | 3.5 | 4.844 |  | --> |  | Lanesboro [T141] | LANESBORO |  | 53.6305 | -8.1528
MEATH HILL (691000) 110 kV STATION | Meath Hill [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 26.4 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 95.4 | 0 | 0 |  | --> |  | Transmission Source | MEATH HILL |  | 53.8968 | -6.7244
INCHICORE 220KV (964000) 220 kV STATION | Inchicore City 220/110 kV [T2102,T2104] | 220 kV | _ | 110 kV | 2x250 MVA @ 110 kV | 500 | --> | 350 | 113 | N/A, consult Eirgrid |  | --> | 308.8 | 0 | 57.7 | 315.1 | 0 |  | --> |  | Transmission Source | INCHICORE 220KV |  | 53.3313 | -6.3371
CORDAL (865000) 110 kV STATION | Cordal [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 54.3 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 57.8 | 2.4 | 0 |  | --> |  | Transmission Source | CORDAL |  | 52.2248 | -9.2712
CORDERRY (972000) 110 kV STATION | Corderry [T121] | 110 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 18 | 17.6 | N/A, consult Eirgrid |  | --> | 19 | 0 | 38.8 | 0 | 0 |  | --> |  | Transmission Source | CORDERRY |  | 54.204 | -8.1807
CORDERRY (972000) 110 kV STATION | Corderry [T122] | 110 kV | _ | MV | 1x63 MVA @ 20 kV | 63 | --> | 56.7 | 55.6 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 61.1 | 0 | 0 |  | --> |  | Transmission Source | CORDERRY |  | 54.204 | -8.1807
CORDUFF (932000) 220 kV STATION | Corduff [T121,T122] | 220 kV | _ | MV | 2x31.5 MVA @ 20 kV | 63 | --> | 47.25 | 41.3 | N/A, consult Eirgrid |  | --> | 38.9 | 14.9625 | 0.2 | 38.7 | 14.963 |  | --> |  | Transmission Source | CORDUFF |  | 53.4174 | -6.369
DUNMANWAY (676000) 110 kV STATION | Dunmanway [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 43.9 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 77.9 | 8.5 | 0 |  | --> |  | Transmission Source | DUNMANWAY |  | 51.7167 | -9.0773
COW CROSS (908000) 110 kV STATION | Cow Cross [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 8.8 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 27.9 | 8.2 | 0 |  | --> |  | Transmission Source | COW CROSS |  | 51.8555 | -8.3121
SINGLAND (521000) 110 kV STATION | Singland [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13.8 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 4 | 24.2 | 9.574 |  | --> |  | Transmission Source | SINGLAND |  | 52.6677 | -8.5792
CRANE (886000) 110 kV STATION | Crane [T122] | 110 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 18 | 4.4 | N/A, consult Eirgrid |  | --> | 19 | 0 | 12.3 | 9.4 | 0 |  | --> |  | Transmission Source | CRANE |  | 52.5377 | -6.502
CRANE (886000) 110 kV STATION | Crane [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 3.1 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 38.8 | 0 | 0 |  | --> |  | Transmission Source | CRANE |  | 52.5377 | -6.502
KILLOTERAN (911000) 110 kV STATION | Killoteran [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13.6 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 0.6 | 28.2 | 9.603 |  | --> |  | Transmission Source | KILLOTERAN |  | 52.2539 | -7.1523
DUNGARVAN (675000) 110 kV STATION | Dungarvan [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 64.4 | 0 | 0 |  | --> |  | Transmission Source | DUNGARVAN |  | 52.1109 | -7.6481
DUNFIRTH (771000) 110 kV STATION | Dunfirth [T122] | 110 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 15 | 3.5 | N/A, consult Eirgrid |  | --> | 13.3 | 0 | 28.3 | 0 | 0 |  | --> |  | Transmission Source | DUNFIRTH |  | 53.3838 | -6.815
KILBARRY (021000) 110 kV STATION | Kilbarry [T101,T43] | 110 kV | _ | MV | 1x15,1x20 MVA @ 10 kV | 35 | --> | 26.25 | 0 | N/A, consult Eirgrid |  | --> | 23.3 | 0 | 3.1 | 24.5 | 0 |  | --> |  | Transmission Source | KILBARRY |  | 51.926 | -8.4858
KILBARRY (021000) 110 kV STATION | Kilbarry [T142,T143] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 55.7 | 38.7 | 0 |  | --> |  | Transmission Source | KILBARRY |  | 51.926 | -8.4858
COW CROSS (908000) 110 kV STATION | Cow Cross [T102,T41] | 110 kV | _ | MV | 1x15,1x20 MVA @ 10 kV | 35 | --> | 26.25 | 19.7 | N/A, consult Eirgrid |  | --> | 18.5 | 9.5 | 6.4 | 12.1 | 9.5 |  | --> |  | N/A | N/A |  | 51.8555 | -8.3121
LISDRUM (624000) 110 kV STATION | Lisdrum [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 5.9 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 61.8 | 0 | 0 |  | --> |  | Transmission Source | LISDRUM |  | 54.2488 | -6.9279
GLENLARA (936000) 110 kV STATION | Glenlara [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.1 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 40.8 | 19.4 | 0 |  | --> |  | Transmission Source | GLENLARA |  | 52.2035 | -9.0207
CLOON (907000) 110 kV STATION | Cloon [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 10.8 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 36.2 | 9.1 | 0 |  | --> |  | Transmission Source | CLOON |  | 53.4879 | -8.8539
ENNIS (677000) 110 kV STATION | Ennis [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13.1 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 12.5 | 15.1 | 9.55 |  | --> |  | Transmission Source | ENNIS |  | 52.8555 | -8.9311
LISHEEN (792000) 110 kV STATION | Lisheen [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.4 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 39.6 | 20.5 | 0 |  | --> |  | Transmission Source | LISHEEN |  | 52.7447 | -7.6715
COLLEGE PARK (670000) 110 kV STATION | College Park [T101,T102,T103] | 110 kV | _ | MV | 3x20 MVA @ 10 kV | 60 | --> | 54 | 0 | N/A, consult Eirgrid |  | --> | 57 | 9.5 | 10 | 64.7 | 10.104 |  | --> |  | Transmission Source | COLLEGE PARK |  | 53.4148 | -6.3727
SORNE HILL (743000) 110 kV STATION | Sorne Hill [T122] | 110 kV | _ | MV | 1x31.5 MVA @ 20 kV | 31.5 | --> | 28.35 | 27.7 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 25.2 | 5 | 0 |  | --> |  | Transmission Source | SORNE HILL |  | 55.1231 | -7.361
COOMATAGGART (877000) 110 kV STATION | Coomataggart [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 55.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 42.6 | 17.5 | 0 |  | --> |  | Transmission Source | COOMATAGGART |  | 51.8805 | -9.324
SOMERSET (716000) 110 kV STATION | Somerset [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 2 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 29.8 | 6.8 | 0 |  | --> |  | Transmission Source | SOMERSET |  | 53.2595 | -8.2412
BALLYRAGGET (329000) 38 kV STATION | Ballyragget [T141] | 38 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 10.3 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 27.4 | 8.5 | 0 |  | --> |  | Transmission Source | BALLYRAGGET |  | 52.7962 | -7.3349
TULLABRACK (722000) 110 kV STATION | Tullabrack [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 14.4 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 43.7 | 0 | 0 |  | --> |  | Transmission Source | TULLABRACK |  | 52.6666 | -9.462
LIMERICK (688000) 110 kV STATION | Limerick [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 21.7 | 79.6 | 0 |  | --> |  | Transmission Source | LIMERICK |  | 52.6325 | -8.647
BALLYDINE (727000) 110 kV STATION | Ballydine [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 16.9 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 12.1 | 21 | 0 |  | --> |  | Transmission Source | BALLYDINE |  | 52.3562 | -7.5061
SLIGO (715000) 110 kV STATION | Sligo [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 27.1 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 40.1 | 55.8 | 0 |  | --> |  | Transmission Source | SLIGO |  | 54.2379 | -8.4592
IKERRIN (682000) 110 kV STATION | Ikerrin [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 52.3 | 0 | 0 |  | --> |  | Transmission Source | IKERRIN |  | 52.9228 | -7.7875
LIBERTY STREET (309000) 110 kV STATION | Liberty Street [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 7.9 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 1.3 | 28.4 | 9.667 |  | --> |  | Transmission Source | LIBERTY STREET |  | 51.9015 | -8.4693
COOLROE (131000) 110 kV STATION | Coolroe [T121,T122] | 110 kV | _ | MV | 2x20 MVA @ 20 kV | 40 | --> | 30 | 17.5 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 2.7 | 25.5 | 9.577 |  | --> |  | Transmission Source | COOLROE |  | 51.8881 | -8.631
BALLYLICKY (728000) 110 kV STATION | Ballylicky [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 42.2 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 76 | 0 | 0 |  | --> |  | Transmission Source | BALLYLICKY |  | 51.7191 | -9.4235
AGHADA (631000) 220 kV STATION | Aghada [T721] | 220 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 2.3 | N/A, consult Eirgrid |  | --> | 4.8 | 0 | 0.9 | 4.3 | 0 |  | --> |  |  | N/A |  | 51.8454 | -8.2168
SCREEB (366000) 110 kV STATION | Screeb [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 6.9 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 13.2 | 21.4 | 0 |  | --> |  | Transmission Source | SCREEB |  | 53.3894 | -9.5708
ARDNAGAPPARY (819000) 110 kV STATION | Ardnagappary [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 11.8 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 42 | 0 | 0 |  | --> |  | Transmission Source | ARDNAGAPPARY |  | 55.0608 | -8.2543
ARDNACRUSHA (990000) 110 kV STATION | Ardnacrusha [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 65.7 | 35 | 0 |  | --> |  | Transmission Source | ARDNACRUSHA |  | 52.716 | -8.6233
MIDLETON (775000) 110 kV STATION | Midleton [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 11.2 | 20.1 | 9.827 |  | --> |  | Transmission Source | MIDLETON |  | 51.9336 | -8.1835
MULLINGAR (693000) 110 kV STATION | Mullingar [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 3.4 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 56.3 | 0 | 0 |  | --> |  | Transmission Source | MULLINGAR |  | 53.5365 | -7.3663
KNOCKEARAGH (685000) 110 kV STATION | Knockearagh [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0.8 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 42.3 | 7.2 | 0 |  | --> |  | Transmission Source | KNOCKEARAGH |  | 52.08 | -9.4423
GORTAWEE (815000) 110 kV STATION | Gortawee [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 44.4 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 9.1 | 55.1 | 0 |  | --> |  | Transmission Source | GORTAWEE |  | 54.1214 | -7.5927
KILKENNY (683000) 110 kV STATION | Kilkenny [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 10.4 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 84.6 | 8.6 | 0 |  | --> |  | Transmission Source | KILKENNY |  | 52.6427 | -7.1662
ARKLOW (917000) 220 kV STATION | Arklow [T141,T142] | 220 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 53.6 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 99.4 | 0 | 0 |  | --> |  | Transmission Source | ARKLOW |  | 52.8171 | -6.1411
DRUMLINE (629000) 110 kV STATION | Drumline [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0.4 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 19.7 | 29.7 | 0 |  | --> |  | Transmission Source | DRUMLINE |  | 52.7309 | -8.8496
LANESBORO (686000) 110 kV STATION | Lanesboro [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 9.2 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 25.6 | 9.8 | 0 |  | --> |  | Transmission Source | LANESBORO |  | 53.6689 | -7.9718
MIDLETON (775000) 110 kV STATION | Midleton [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 30 | 10 | 0 |  | --> |  | Transmission Source | MIDLETON |  | 51.9336 | -8.1835
MULLINGAR (693000) 110 kV STATION | Mullingar [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 10.9 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 3.3 | 24.8 | 9.571 |  | --> |  | Transmission Source | MULLINGAR |  | 53.5365 | -7.3663
SALTHILL (161000) 110 kV STATION | Salthill [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 44.9 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 50.1 | 13.8 | 0 |  | --> |  | Transmission Source | SALTHILL |  | 53.2718 | -9.073
SALTHILL (161000) 110 kV STATION | Salthill [T101,T102] | 110 kV | _ | MV | 2x31.5 MVA @ 10 kV | 63 | --> | 47.25 | 11 | N/A, consult Eirgrid |  | --> | 38.9 | 14.9625 | 9.5 | 36.8 | 15.191 |  | --> |  | Transmission Source | SALTHILL |  | 53.2718 | -9.073
AHANE (900000) 110 kV STATION | Ahane [T102] | 110 kV | _ | MV | 1x15 MVA @ 10 kV | 15 | --> | 13.5 | 6.8 | N/A, consult Eirgrid |  | --> | 14.2 | 0 | 5.8 | 9.7 | 0 |  | --> |  | Transmission Source | AHANE |  | 52.668 | -8.4986
NENAGH (946000) 110 kV STATION | Nenagh [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 4.1 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 24.5 | 12.4 | 0 |  | --> |  | Transmission Source | NENAGH |  | 52.8664 | -8.1737
MARINA (794000) 110 kV STATION | Marina [T105,T106] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 4.7 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 1.7 | 26.5 | 9.579 |  | --> |  | Transmission Source | MARINA |  | 51.9025 | -8.4411
LETTERKENNY (687000) 110 kV STATION | Letterkenny [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 13.2 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 131.3 | 0 | 0 |  | --> |  | Transmission Source | LETTERKENNY |  | 54.9284 | -7.7024
NEWBRIDGE (695000) 110 kV STATION | Newbridge [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 34.4 | 15.3 | 0 |  | --> |  | Transmission Source | NEWBRIDGE |  | 53.1981 | -6.8437
DUNDALK (062000) 110 kV STATION | Dundalk [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 21 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 96.6 | 0 | 0 |  | --> |  | Transmission Source | DUNDALK |  | 54.0085 | -6.4194
DRYBRIDGE (064000) 110 kV STATION | Drybridge [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 80.6 | 16.3 | 0 |  | --> |  | Transmission Source | DRYBRIDGE |  | 53.7274 | -6.394
ATHY (927000) 110 kV STATION | Athy [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0.1 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 7.4 | 22 | 9.643 |  | --> |  | Transmission Source | ATHY |  | 52.9985 | -7.0167
ARIGNA (417000) 110 kV STATION | Arigna [T121] | 110 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 8.5 | N/A, consult Eirgrid |  | --> | 14.2 | 0 | 17.5 | 0 | 0 |  | --> |  | Transmission Source | ARIGNA |  | 54.0871 | -8.0882
ATHLONE (897000) 110 kV STATION | Athlone [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 7.6 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 83.4 | 15.5 | 0 |  | --> |  | Transmission Source | ATHLONE |  | 53.4256 | -7.9672
ARKLOW (917000) 220 kV STATION | Arklow [T101,T102] | 220 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 18.1 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 15.9 | 10.7 | 9.521 |  | --> |  | Transmission Source | ARKLOW |  | 52.8171 | -6.1411
WEXFORD (742000) 110 kV STATION | Wexford [T121,T122] | 110 kV | _ | MV | 2x20 MVA @ 20 kV | 40 | --> | 30 | 16.1 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 6.1 | 21.4 | 9.546 |  | --> |  | Transmission Source | WEXFORD |  | 52.3425 | -6.5476
WEXFORD (742000) 110 kV STATION | Wexford [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 33.6 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 70.3 | 22 | 0 |  | --> |  | Transmission Source | WEXFORD |  | 52.3425 | -6.5476
DALLOW (673000) 110 kV STATION | Dallow [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 6.4 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 32.1 | 4.4 | 0 |  | --> |  | Transmission Source | DALLOW |  | 53.1167 | -7.9381
DALTON (909000) 110 kV STATION | Dalton [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.5 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 47.5 | 12.6 | 0 |  | --> |  | Transmission Source | DALTON |  | 53.7163 | -8.9756
NAVAN (694000) 110 kV STATION | Navan [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 12.8 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 60.4 | 30.7 | 0 |  | --> |  | Transmission Source | NAVAN |  | 53.705 | -6.7109
DALTON (909000) 110 kV STATION | Dalton [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 20.5 | 17 | 0 |  | --> |  | Transmission Source | DALTON |  | 53.7163 | -8.9756
WATERFORD (808000) 110 kV STATION | Waterford [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 25.2 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 62.3 | 38.9 | 0 |  | --> |  | Transmission Source | WATERFORD |  | 52.2685 | -7.1278
SHANKILL (714000) 110 kV STATION | Shankill [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 13.8 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 84.7 | 8.3 | 0 |  | --> |  | Transmission Source | SHANKILL |  | 54.0044 | -7.3094
MACROOM (630000) 110 kV STATION | Macroom [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 16.1 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 55.3 | 0 | 0 |  | --> |  | Transmission Source | MACROOM |  | 51.8936 | -8.8878
CATHALEENS FALL (143000) 110 kV STATION | Cathaleens Fall [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 22.05 | 1.6 | N/A, consult Eirgrid |  | --> | 20.9 | 0 | 94.8 | 0 | 0 |  | --> |  | Transmission Source | CATHALEENS FALL |  | 54.4967 | -8.1841
TRABEG (701000) 110 kV STATION | Trabeg [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 5.5 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 5.4 | 23.5 | 9.612 |  | --> |  | Transmission Source | TRABEG |  | 51.8856 | -8.4621
TAWNAGHMORE (952000) 110 kV STATION | Tawnaghmore [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 26.8 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 30 | 0.1 | 0 |  | --> |  | Transmission Source | TAWNAGHMORE |  | 54.1991 | -9.229
GLENREE (894000) 110 kV STATION | Glenree [T121] | 110 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 18 | 17.7 | N/A, consult Eirgrid |  | --> | 19 | 0 | 17.2 | 2.2 | 0 |  | --> |  | Transmission Source | GLENREE |  | 54.1135 | -9.0022
GLENREE (894000) 110 kV STATION | Glenree [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 64.8 | 0 | 0 |  | --> |  | Transmission Source | GLENREE |  | 54.1135 | -9.0022
TRABEG (701000) 110 kV STATION | Trabeg [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 26.9 | 26.4 | 0 |  | --> |  | Transmission Source | TRABEG |  | 51.8856 | -8.4621
GALWAY 110KV (679000) 110 kV STATION | Galway 110kv [T102,T103] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 3.3 | 26.6 | 9.686 |  | --> |  | Transmission Source | GALWAY 110KV |  | 53.2951 | -9.0181
RATHKEALE (712000) 110 kV STATION | Rathkeale [T141,T142] | 110 kV | _ | 38 kV | 2x30 MVA @ 38 kV | 60 | --> | 42 | 12.7 | N/A, consult Eirgrid |  | --> | 37 | 0 | 71.5 | 0 | 0 |  | --> |  | Transmission Source | RATHKEALE |  | 52.5406 | -8.9745
BUTLERSTOWN (667000) 110 kV STATION | Butlerstown [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 68.7 | 0 | 0 |  | --> |  | Transmission Source | BUTLERSTOWN |  | 52.2225 | -7.1624
CASTLEVIEW (600000) 110 kV STATION | Castleview [T101,T102] | 110 kV | _ | MV | 2x31.5 MVA @ 10 kV | 63 | --> | 47.25 | 6.8 | N/A, consult Eirgrid |  | --> | 38.9 | 14.9625 | 19.9 | 29.4 | 15.486 |  | --> |  | Transmission Source | CASTLEVIEW |  | 51.8922 | -8.3586
BOOLTIAGH (887000) 110 kV STATION | Booltiagh [T143] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.4 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 64.1 | 0 | 0 |  | --> |  | Transmission Source | BOOLTIAGH |  | 52.7667 | -9.2556
BOOLTIAGH (887000) 110 kV STATION | Booltiagh [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 54.9 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 57.2 | 2.9 | 0 |  | --> |  | Transmission Source | BOOLTIAGH |  | 52.7667 | -9.2556
KILPADDOGE (921000) 220 kV STATION | Kilpaddoge [T122] | 220 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 18 | 17.4 | N/A, consult Eirgrid |  | --> | 19 | 0 | 18 | 1.3 | 0 |  | --> |  | Transmission Source | KILPADDOGE |  | 52.5867 | -9.3854
BOGGERAGH (572000) 110 kV STATION | Boggeragh [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 55.6 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 43.4 | 16.8 | 0 |  | --> |  | Transmission Source | BOGGERAGH |  | 52.0315 | -8.8926
TRIEN (720000) 110 kV STATION | Trien [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 14.8 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 54 | 0 | 0 |  | --> |  | Transmission Source | TRIEN |  | 52.4203 | -9.4318
ENNIS (677000) 110 kV STATION | Ennis [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 47.3 | 2.7 | 0 |  | --> |  | Transmission Source | ENNIS |  | 52.8555 | -8.9311
TRALEE (719000) 110 kV STATION | Tralee [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 28.6 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 79.3 | 10.6 | 0 |  | --> |  | Transmission Source | TRALEE |  | 52.2874 | -9.6776
MACETOWN (652000) 110 kV STATION | Macetown [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 7.4 | 25.4 | 10.088 |  | --> |  | Transmission Source | MACETOWN |  | 53.4109 | -6.409
THURLES (718000) 110 kV STATION | Thurles [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 13.7 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 54.3 | 0 | 0 |  | --> |  | Transmission Source | THURLES |  | 52.6972 | -7.7687
KILTEEL (684000) 110 kV STATION | Kilteel [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 45.5 | 5.1 | 0 |  | --> |  | Transmission Source | KILTEEL |  | 53.2569 | -6.53
CARRICK ON SHANNON (074000) 110 kV STATION | Carrick On Shannon [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 11.5 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 31.4 | 16.7 | 0 |  | --> |  | Transmission Source | CARRICK ON SHANNON |  | 53.9295 | -8.1261
GARVAGH (570000) 110 kV STATION | Garvagh [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 55.2 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 34 | 26.2 | 0 |  | --> |  | Transmission Source | GARVAGH |  | 54.1612 | -8.1779
THORNSBERRY (717000) 110 kV STATION | Thornsberry [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 65.1 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 38.5 | 43.2 | 0 |  | --> |  | Transmission Source | THORNSBERRY |  | 53.2917 | -7.4657
CARLOW (669000) 110 kV STATION | Carlow [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 22 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 105.5 | 0 | 0 |  | --> |  | Transmission Source | CARLOW |  | 52.8373 | -6.848
GLENLARA (936000) 110 kV STATION | Glenlara [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 38.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 54.3 | 10.8 | 0 |  | --> |  | Transmission Source | GLENLARA |  | 52.2035 | -9.0207
CARROWBEG (699000) 110 kV STATION | Carrowbeg [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 7.9 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 7.1 | 30.1 | 0 |  | --> |  | Transmission Source | CARROWBEG |  | 53.8048 | -9.5016
TRIEN (720000) 110 kV STATION | Trien [T143] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 55.8 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 46.3 | 13.8 | 0 |  | --> |  | Transmission Source | TRIEN |  | 52.4203 | -9.4318
TIPPERARY (806000) 110 kV STATION | Tipperary [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 2.8 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 29.1 | 8.1 | 0 |  | --> |  | Transmission Source | TIPPERARY |  | 52.4802 | -8.0759
TONROE (904000) 110 kV STATION | Tonroe [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 6.1 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 28.7 | 7.9 | 0 |  | --> |  | Transmission Source | TONROE |  | 53.9135 | -8.5866
MOY (774000) 110 kV STATION | Moy [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 13 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 28.4 | 20 | 0 |  | --> |  | Transmission Source | MOY |  | 54.1315 | -9.1748
CAHIR (668000) 110 kV STATION | Cahir [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 18.2 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 47.9 | 0 | 0 |  | --> |  | Transmission Source | CAHIR |  | 52.3824 | -7.8857
DOON (674000) 110 kV STATION | Doon [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 11.6 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 56.9 | 0 | 0 |  | --> |  | Transmission Source | DOON |  | 52.3931 | -7.6602
CASTLEBAR (520000) 110 kV STATION | Castlebar [T141,T142] | 110 kV | _ | 38 kV | 1x31.5,1x63 MVA @ 38 kV | 94.5 | --> | 66.15 | 25 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 61.3 | 0 | 0 |  | --> |  | Transmission Source | CASTLEBAR |  | 53.8701 | -9.2747
GALWAY 110KV (679000) 110 kV STATION | Galway 110kv [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 49.2 | 50.3 | 0 |  | --> |  | Transmission Source | GALWAY 110KV |  | 53.2951 | -9.0181
GARROW (992000) 110 kV STATION | Garrow [T121] | 110 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13.3 | N/A, consult Eirgrid |  | --> | 14.2 | 0 | 15 | 0 | 0 |  | --> |  | Transmission Source | GARROW |  | 52.0112 | -9.1445
BANDON (729000) 110 kV STATION | Bandon [T101,T42] | 110 kV | _ | MV | 1x10,1x20 MVA @ 10 kV | 30 | --> | 22.5 | 8.7 | N/A, consult Eirgrid |  | --> | 20 | 0 | 19.3 | 3.1 | 0 |  | --> |  | Transmission Source | BANDON |  | 51.7661 | -8.722
MALLOW (689000) 110 kV STATION | Mallow [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 18.1 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 32 | 16.6 | 0 |  | --> |  | Transmission Source | MALLOW |  | 52.1463 | -8.6155
BARRYMORE (905000) 110 kV STATION | Barrymore [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 67.8 | 0 | 0 |  | --> |  | Transmission Source | BARRYMORE |  | 52.0912 | -8.2595
BARNAHELY (772000) 110 kV STATION | Barnahely [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 20.5 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 22.7 | 24.4 | 0 |  | --> |  | Transmission Source | BARNAHELY |  | 51.8251 | -8.3485
BARNAHELY (772000) 110 kV STATION | Barnahely [T121,T122,T124] | 110 kV | _ | MV | 3x20 MVA @ 20 kV | 60 | --> | 54 | 18.2 | N/A, consult Eirgrid |  | --> | 57 | 9.5 | 13.3 | 58 | 9.811 |  | --> |  | Transmission Source | BARNAHELY |  | 51.8251 | -8.3485
CHARLEVILLE (456000) 110 kV STATION | Charleville [T142] | 110 kV | _ | 38 kV | 1x30 MVA @ 38 kV | 30 | --> | 27 | 7.9 | N/A, consult Eirgrid |  | --> | 28.5 | 0 | 44.6 | 0 | 0 |  | --> |  | Transmission Source | CHARLEVILLE |  | 52.325 | -8.7025
BANOGE (809000) 110 kV STATION | Banoge [T121,T122] | 110 kV | _ | MV | 2x20 MVA @ 20 kV | 40 | --> | 30 | 17.8 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 16.4 | 11.1 | 9.547 |  | --> |  | Transmission Source | BANOGE |  | 52.6528 | -6.2647
GRIFFINRATH (681000) 110 kV STATION | Griffinrath [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 96.3 | 2.6 | 0 |  | --> |  | Transmission Source | GRIFFINRATH |  | 53.3448 | -6.5619
BANDON (729000) 110 kV STATION | Bandon [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 3.2 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 39.7 | 11.5 | 0 |  | --> |  | Transmission Source | BANDON |  | 51.7661 | -8.722
GREAT ISLAND (680000) 220 kV STATION | Great Island [T141,T142] | 220 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 21.5 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 92.1 | 0 | 0 |  | --> |  | Transmission Source | GREAT ISLAND |  | 52.2837 | -6.9761
STRATFORD (913000) 110 kV STATION | Stratford [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0.6 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 37 | 0 | 0 |  | --> |  | Transmission Source | STRATFORD |  | 52.9896 | -6.6669
BALTRASNA (371000) 110 kV STATION | Baltrasna [T121,T122] | 110 kV | _ | MV | 2x20 MVA @ 20 kV | 40 | --> | 30 | 0 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 26.5 | 2.3 | 9.605 |  | --> |  | Transmission Source | BALTRASNA |  | 53.5535 | -6.4343
CLOGHBOOLA (875000) 110 kV STATION | Cloghboola [T122] | 110 kV | _ | MV | 1x63 MVA @ 20 kV | 63 | --> | 56.7 | 54.2 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 54.5 | 5.6 | 0 |  | --> |  | Transmission Source | CLOGHBOOLA |  | 52.3209 | -9.4472
CRORY (473000) 110 kV STATION | Crory [T121] | 110 kV | _ | MV | 1x63 MVA @ 20 kV | 63 | --> | 56.7 | 55.4 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 60.2 | 0 | 0 |  | --> |  | Transmission Source | CRORY |  | 52.569 | -6.5458
RICHMOND (713000) 110 kV STATION | Richmond [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 2.8 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 43.2 | 6 | 0 |  | --> |  | Transmission Source | RICHMOND |  | 53.7492 | -7.8419
MULLAGHARLIN (817000) 110 kV STATION | Mullagharlin [T121,T122] | 110 kV | _ | MV | 2x20 MVA @ 20 kV | 40 | --> | 30 | 19.8 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 0.8 | 27.1 | 9.562 |  | --> |  | Transmission Source | MULLAGHARLIN |  | 53.9808 | -6.4054
HARTNETTS CROSS (939000) 110 kV STATION | Hartnetts Cross [T121,T422] | 110 kV | _ | MV | 1x10,1x20 MVA @ 20 kV | 30 | --> | 22.5 | 18.8 | N/A, consult Eirgrid |  | --> | 12.4 | 9.5 | 4.8 | 8.2 | 9.507 |  | --> |  | Transmission Source | HARTNETTS CROSS |  | 51.9028 | -8.9308
REAMORE (197000) 110 kV STATION | Reamore [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.5 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 44.4 | 15.8 | 0 |  | --> |  | Transmission Source | REAMORE |  | 52.2973 | -9.5504
CAUTEEN (573000) 110 kV STATION | Cauteen [T144] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 54.6 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 52 | 8.1 | 0 |  | --> |  | Transmission Source | CAUTEEN |  | 52.5293 | -8.1839
BLAKE (120000) 110 kV STATION | Blake [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 20.1 | 17.3 | 0 |  | --> |  | Transmission Source | BLAKE |  | 53.2952 | -6.8636
FINGLAS (318000) 220 kV STATION | Finglas Urban 220/110 kV [T2103,T2104] | 220 kV | _ | 110 kV | 2x250 MVA @ 110 kV | 500 | --> | 350 | 87.1 | N/A, consult Eirgrid |  | --> | 308.8 | 0 | 30.4 | 325.8 | 0 |  | --> |  | Transmission Source | FINGLAS |  | 53.4075 | -6.3161
TRILLICK (721000) 110 kV STATION | Trillick [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 4.9 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 57.8 | 0 | 0 |  | --> |  | Transmission Source | TRILLICK |  | 55.1182 | -7.4248
CAUTEEN (573000) 110 kV STATION | Cauteen [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 54.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 60.7 | 0 | 0 |  | --> |  | Transmission Source | CAUTEEN |  | 52.5293 | -8.1839
TRILLICK (721000) 110 kV STATION | Trillick [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 28 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 30.9 | 0 | 0 |  | --> |  | Transmission Source | TRILLICK |  | 55.1182 | -7.4248
BINBANE (666000) 110 kV STATION | Binbane [T143] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.3 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 0 | 59.9 | 0 |  | --> |  | Transmission Source | BINBANE |  | 54.7253 | -8.2757
OUGHTRAGH (696000) 110 kV STATION | Oughtragh [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 25.1 | 11.7 | 0 |  | --> |  | Transmission Source | OUGHTRAGH |  | 52.1418 | -9.7044
CAUTEEN (573000) 110 kV STATION | Cauteen [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.2 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 66 | 0 | 0 |  | --> |  | Transmission Source | CAUTEEN |  | 52.5293 | -8.1839
CARRICKMINES (649000) 220 kV STATION | Carrickmines [T2101,T2103,T2104] | 220 kV | _ | 110 kV | 3x250 MVA @ 110 kV | 750 | --> | 675 | 348.6 | N/A, consult Eirgrid |  | --> | 712.5 | 0 | 81.5 | 710 | 0 |  | --> |  | Transmission Source | CARRICKMINES |  | 53.2549 | -6.1921
PORTLAOISE (201000) 110 kV STATION | Portlaoise [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 23.7 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 78.8 | 13.4 | 0 |  | --> |  | Transmission Source | PORTLAOISE |  | 53.022 | -7.3041
BELLACORICK (896000) 110 kV STATION | Bellacorick [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 51.8 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 46.4 | 14.6 | 0 |  | --> |  | Transmission Source | BELLACORICK |  | 54.1261 | -9.5683
BELLACORICK (896000) 110 kV STATION | Bellacorick [T122] | 110 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 7.6 | N/A, consult Eirgrid |  | --> | 9.5 | 0 | 10.6 | 0 | 0 |  | --> |  | Transmission Source | BELLACORICK |  | 54.1261 | -9.5683
POOLBEG (799000) 220 kV STATION | Poolbeg [TF3,TF4] | 220 kV | _ | 110 kV | 2x250 MVA @ 110 kV | 500 | --> | 350 | 57.1 | N/A, consult Eirgrid |  | --> | 308.8 | 0 | 93.1 | 281.1 | 0 |  | --> |  | Transmission Source | POOLBEG |  | 53.3438 | -6.1967
MONREAD (902000) 110 kV STATION | Monread [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 12.6 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 10.8 | 17.5 | 9.579 |  | --> |  | Transmission Source | MONREAD |  | 53.2479 | -6.6529
REAMORE (197000) 110 kV STATION | Reamore [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 45.1 | 15.6 | 0 |  | --> |  | Transmission Source | REAMORE |  | 52.2973 | -9.5504
CHARLEVILLE (456000) 110 kV STATION | Charleville [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 53.9 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 51.4 | 8.8 | 0 |  | --> |  | Transmission Source | CHARLEVILLE |  | 52.325 | -8.7025
BINBANE (666000) 110 kV STATION | Binbane [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 66.6 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 96.6 | 0 | 0 |  | --> |  | Transmission Source | BINBANE |  | 54.7253 | -8.2757
_ESB Networks Capacity Heat Map Publication. LV asset data from Aug 2025. Load data derived from revenue metering Jan 25, Generation and demand commitments up to 08 Oct 2025. |  | Report compiled 12/12/2025

## Disclaimer
Disclaimer
This capacity heatmap provides an indication of the available transformer capacity at substations. The map indicates transformer capacity only. It does not guarantee the same capacity is available in the upstream networks. The heatmap is a snapshot, representing a moment in time, of a continually changing network system. It cannot be relied upon in isolation to assess the viability of a connection to a premises. Whilst we use reasonable endeavours to ensure that the capacity map and related information is accurate, we do not warrant, and do not accept any responsibility or liability for, the accuracy or completeness of the content or for any consequence or loss which may arise from reliance on the capacity heatmap or related information. The data provided must be considered in conjunction with explanations in ‘Important details about the Heatmap’ section. The available capacity figures will be periodically updated, and you should check the webpage routinely for the latest version. The legal disclaimer terms and conditions for use of our website apply to the capacity heatmap and related information.
The legal disclaimer terms and conditions for use of our website apply to the capacity heatmap and related information.

## Notes & FAQs
What is the Available Capacity Heatmap?
At ESB Networks we are committed to improving the experience of our customers. As part of this commitment, we have developed our interactive Capacity Heatmap. It contains capacity information on all our 3-phase LV, MV and HV DSO substations. It provides an interface that enables the easy identification of potential transformer capacity in the vicinity of your site. An excel file is available to download from the download section on this page.
We envisage that the map will be used to inform initial discussion between ourselves and our customers. Although we have taken steps to ensure the accuracy of the map, it cannot replicate the level of accuracy provided by the detailed assessment carried out as part of the formal application process. Please read the accompanying notes and important details section to understand what the map does and does not provide.
If the Available Capacity Heatmap indicates that there is insufficient capacity to accommodate your development, please contact us to discuss the next steps. We will always work with customers to find solutions.
Generation customer queries should be directed to DSOgenerators@esb.ie.
Demand customer queries should be directed to innovationfeedback@esbnetworks.ie.
What can I learn from the map?
The Capacity Heatmap provides an indication of available transformer capacity, at substation level and at all voltage levels, for new demand and generation customers. It is a user-friendly and interactive map that shows how much demand or generation could be added into a substation without reinforcement. It empowers potential customers and helps them have a better understanding as to where connection is possible.
In the map HV substations are classified into three categories corresponding to the connection voltage i.e., 110kV, 38kV or Medium Voltage (MV).
The map also gives the location and available demand capacity for all 3 phase Medium Voltage to Low Voltage (MV/LV) substations.The LV data capacity is in the range of customers looking to connect demand less than 500kVA. This scale would be of most interest to small businesses, farming, and small community projects. If the indicated capacity meets your needs, then you can be reasonably assured no new substation development is required. However, site specific detail such as proximity and physical access could still be an overarching limiting factor.
Available capacity for LV generation is not specified because of additional considerations that are mainly site specific, see point No 5 below.
The pins on the map are colour coded by ranges of available capacity which can be separately filtered. Filtering can also be independently applied by voltage level.
How do I know which substation to review for my site?
We recommend using the Location Finder tool by clicking on the icon to the right of the map. Look for this symbol
Here you can type your place name, or Eircode and it will show the stations closest to the location. Please ensure you have selected the relevant connection voltages and available ranges in the filters section on the left or it may not return results.
For LV substations, use the map to locate your own site and then find the nearest LV substation to it. Typically, a substation must be within 300m or less to be suitable for connecting at LV otherwise a new substation must be provided nearer to you. The pop-up box also shows the parent HV substation that supplies the LV substation. Also check this for available capacity.
For MV connection (greater than or equal to 500kVA) locate the nearest LV station as in the previous paragraph and the parent capacity will also be shown.
Does the Capacity Available value mean I can connect the amount shown?
Not necessarily. There are many site-specific issues and detailed technical checks that must be completed to give that assurance and they can only be completed as part of an application. Below are some of the factors that influence the answer:
Am I the first to apply? All connection offers are provided on a first come first served basis so other customers may have applied ahead and used a proportion of the available capacity.
Proximity to the substation: typically for LV, you must be a maximum of 300m from the substation and much closer for the higher level of LV capacity. For 38kV and MV circuits, capacity is not assured, and new lines may need to be constructed or existing one upgraded.
HV substations are sometimes a parent supply to other downstream substations. In cases where the parent substation has limited capacity then all child substations will be curtailed by that limit. Furthermore, if just one child substation absorbs all the available capacity then that will result in no spare capacity for the other child stations. This form of interaction requires continual re-assessment to ensure no system overload occur.
A similar interaction can occur on circuits where apparently available capacity cannot be contracted because of customer increases on other circuits which share a common source with a capacity limit.
Generation, at all voltages, is particularly onerous due to the limited latitude to accommodate the associated voltage rise. This has an acute effect on the necessary proximity to a substation.
For ECP generation connections, the capacity available may differ depending on customers accepting or withdrawing their connection study offers during each batch of studies.
Capacity available is also influenced by disturbing load such as flicker and harmonic emissions.
The stated available capacity may exceed the maximum rating for an individual network component for example standard circuit connection capacity. In such cases, aconnection will be constrained by the network component and therefore will not be able to avail of the full value indicated.
How has the data been produced?
The data has been produced by an analysis of the available transformer capacity, existing loads, and contractual commitments to new customers. Detailed assessment aspects, necessary for connection offers, such as upstream circuit capacity and service contingency requirement are not included.
What are the available capacity figures based on?
Station capacity, as of Oct 2025.
Base load information comes from Special Load Readings, 2024/2025 which include 2024 Summer Valley load used in the Generation capacity preparation.
Demand calculation incorporates demand contracts and offers up to end Aug 2025
Generation calculations incorporates generation contracts and offers up to early Oct 2025.
How often is the Network Capacity Map updated?
As part of ESB Networks strategy, the objective is to update the map quarterly.
Are the substation locations accurate?
HV substation locations are only indicative. The exact locations of MV/LV substations are provided.
How long does a connection take?
In general, where HV substation capacity is adequate, MV connections up to a maximum of 10MVA will entail construction of overhead line or new underground cable network, associated civil works and minor station works only and typically do not require planning permission. These would not be expected to take longer than 6-9 months. However, any instances requiring significant station work such as the installation of a new transformer or MV switchgear will require increased time, and possibly planning permission or necessary permits and would typically be expected to take approximately 2-3 years.
LV connections alone are usually completed within 6 months of application.
Generation connection information: Enduring Connection Policy (ECP) (esbnetworks.ie)
What other important points should be kept in mind about the data in the map?
The map does not replace a full formal application in determining network capacity.
The map does not provide capacity figures for the final connection from HV substation to customer premises. Such connections will need to tap into the existing MV (10kV or 20kV) network. Capacity availability is subject to many variables and an assessment is necessary.
In some cases, the available capacity shown in the Demand Map may already be contracted to individual customers but is not currently being fully utilised.
The information provided in the Generation and Demand Maps does not guarantee the same capacity is available in the upstream DSO networks.
Any increased load on the Distribution System will impact on the upstream Transmission System and reinforcements may be required on the Transmission System in order to cater for these loads. This will be separately assessed by the TSO.
An individual connection cannot be greater than the capacity of an individual transformer. In the case of 38kV and MV, the available capacity shown is the total of all transformers in the substation at the respective voltage. Therefore, full capacity utilisation may, sometimes, only be possible with more than one connection. (Note, a single premises cannot have more than one connection).