## 1. Introduction
Generation Capacity Headroom Report 2025
Version: | 1.3
Date: | 29/01/2026
Overview: | This workbook is for indicative, informal purposes only.
All connections are subject to connection specific studies and the decision of ESB Networks' Planners.
The workbook provides a high level, indicative capacity analysis from the MV busbars at HV substations to the 110 kV busbars.
The indicative headroom capacity reported is for generation connections only.
For indicative demand capacity, please consult the companion Demand Capacity Headroom Report.
Capacity results are displayed in megawatts [MW].
Generation power factor = 0.95 lagging.
Non-Firm headroom capacity results are not included in this iteration of the Generation Workbooks.
All connected and contracted generators are deducted from the overall headroom generation capacity as of 2025 onwards.
Assumptions
The headroom capacity results presented in the workbooks are based on the various input data sources available at the time of processing. Some of the key assumptions are as follows: 1. Growth forecast scenarios were prepared in 2024 based on information available at the time. 2. 2024-25 Special Load Readings(SLR) HV station summer valley demand figures are used for calculating generation headroom capacity. 3. Freeze date for planned reinforcement projects, load transfers and other data-sets: August 2025. 4. New reinforcement projects identified or initiated since August 2025 are not included. These new projects could be to address new customer applications or new capacity constraints identified. They will appear in subsequent versions of workbooks. 5. Only contracted and connected distribution generators on record from July 2025 are included in this assessment. 6. Microgeneration, Mini-generation and Small Scale Generation as reported in September 2025 are included in this assessment. These generator categories have been applied to 38 kV/MV, 110 kV/MV and 110/38 kV substation generation capacity headroom calculations. No growth rates have been applied to these generator categories. 7. Existing and contracted BESS has been assumed to not import or export during the summer valley load period.
Purpose of the "2. Master Gen Capacity List" tab:
This tab provides a comprehensive list of projected generation capacity at all substations for the four load growth scenarios examined.
Purpose of the "3. Capacity Search" tab:
This tab gives a projection of the generation headroom capacity available at individual substations and the upstream limitations of their corresponding Bulk Supply Points (BSPs). Options that are available in the interface for the user:
→ Select their desired substation by name, or use a Geographical Search function to locate their closest substation.
→ Choose a voltage level, and the workbook will show the capacity available at that voltage level.
Load Growth Scenarios Studied:
The load growth percentages used in this iteration of the Generation Capacity Headroom Report are displayed below. These load growths are Based on the CRA 2025 report, and they are applied to the summer valley SLR 2024-2025 loads
Network Area | Conservative |  | Best View |  | Base Case |  | Aggressive
| 2025-2030 | 2031-2050 | 2025-2030 | 2031-2050 | 2025-2030 | 2031-2050 | 2025-2030 | 2031-2050
ARKLOW | 2.034% | 2.62% | 2.551% | 3.446% | 3.257% | 3.83% | 4.442% | 5.108%
ATHLONE | 1.536% | 2.485% | 2.389% | 3.486% | 3.381% | 3.76% | 5.191% | 4.147%
BALLINA | 0.8327% | 2.738% | 1.875% | 3.436% | 2.514% | 4.057% | 4.834% | 5.386%
BANDON | 2.539% | 2.489% | 2.683% | 3.356% | 3.684% | 3.365% | 5.095% | 3.427%
CASTLEBAR | 0.7263% | 2.837% | 1.693% | 3.475% | 2.435% | 4.196% | 4.942% | 5.577%
CAVAN | 1.969% | 2.702% | 2.529% | 3.691% | 3.151% | 4.059% | 4.9% | 4.898%
CLONMEL | 1.965% | 2.583% | 2.223% | 3.539% | 2.935% | 3.845% | 4.588% | 4.285%
CORK CITY | 2.543% | 2.489% | 2.686% | 3.355% | 3.688% | 3.364% | 5.102% | 3.423%
DROGHEDA | 2.33% | 3% | 2.751% | 3.757% | 3.88% | 4.432% | 5.266% | 5.647%
DUBLIN CENTRAL | 3.074% | 2.722% | 3.585% | 3.036% | 4.167% | 3.304% | 7.107% | 3.142%
DUBLIN NORTH | 3.809% | 2.139% | 4.207% | 2.453% | 4.628% | 2.758% | 5.692% | 2.449%
DUBLIN SOUTH | 3.06% | 2.324% | 3.543% | 2.719% | 3.987% | 3.046% | 5.819% | 2.869%
DUNDALK | 2.467% | 2.623% | 2.744% | 3.611% | 3.992% | 4.059% | 5.426% | 4.734%
DUNMANWAY | 2.537% | 2.489% | 2.682% | 3.356% | 3.682% | 3.365% | 5.091% | 3.429%
ENNIS | 1.96% | 2.596% | 2.154% | 3.673% | 3.431% | 3.972% | 6.032% | 4.218%
ENNISCORTHY | 1.35% | 3.158% | 2.376% | 3.432% | 2.921% | 3.771% | 4.589% | 5.236%
FERMOY | 2.527% | 2.493% | 2.67% | 3.357% | 3.647% | 3.389% | 5.065% | 3.474%
GALWAY | 1.882% | 2.538% | 2.363% | 3.575% | 3.002% | 3.905% | 4.72% | 4.481%
KILKENNY | 1.795% | 2.603% | 2.195% | 3.498% | 2.607% | 4.143% | 4.347% | 5.06%
KILLARNEY | 1.722% | 2.513% | 2.105% | 3.474% | 3.007% | 3.479% | 4.305% | 4.057%
KILLYBEGS | 1.068% | 2.459% | 2.282% | 3.433% | 2.617% | 4.04% | 4.006% | 4.712%
LETTERKENNY | 1.032% | 2.436% | 2.293% | 3.414% | 2.557% | 4.005% | 3.906% | 4.624%
LIMERICK | 2.198% | 2.443% | 2.253% | 3.311% | 3.103% | 3.803% | 5.037% | 4.146%
LONGFORD | 1.174% | 2.748% | 2.322% | 3.238% | 2.739% | 4.024% | 4.407% | 4.955%
MULLINGAR | 1.644% | 3.357% | 2.131% | 3.824% | 4.123% | 3.942% | 5.731% | 4.504%
NEWCASTLEWEST | 2.271% | 2.427% | 2.364% | 3.246% | 3.119% | 3.708% | 4.775% | 4.023%
PORTLAOISE | 1.965% | 2.734% | 2.411% | 3.483% | 2.95% | 4.104% | 4.664% | 5.305%
ROSCREA | 1.797% | 2.526% | 2.225% | 3.652% | 3.008% | 3.905% | 4.758% | 4.268%
SLIGO | 1.364% | 2.604% | 2.336% | 3.455% | 3.087% | 4.069% | 4.779% | 5.204%
THURLES | 1.873% | 2.498% | 2.271% | 3.597% | 3.041% | 3.831% | 4.782% | 4.051%
TRALEE | 1.368% | 2.556% | 2.425% | 3.291% | 2.721% | 3.535% | 4.263% | 4.311%
TUAM | 1.511% | 2.612% | 2.184% | 3.567% | 2.84% | 3.997% | 4.779% | 4.851%
TULLAMORE | 2.128% | 2.697% | 2.695% | 3.503% | 3.211% | 4.066% | 4.138% | 4.864%
WATERFORD | 2.086% | 2.654% | 2.304% | 3.376% | 2.716% | 3.905% | 4.305% | 4.683%
Capacity Search Sheet - User Guidelines
Notes: | Please wait for the workbook to finish calculating before acknowledging results.
The user can check the progress by watching the bottom corner of the screen.
The workbook must be opened in MS®Excel 365 desktop application, not the browser.
General Input Parameters:
Cell B4 | Set to "-" to enable geographical search. Otherwise enter selected substation for capacity results.
Cell D4 | Select desired connection voltage from those available in cell D3.
Cell E4 | Becomes visible if more than one connection configuration of the same connection voltage is available at the substation.
Cell will turn yellow and selection will become available for user input.
Note that this should be returned to 1 for majority of substations.
Cell Colouring:
Cells in green indicate available capacity.
Cells in red indicate that no capacity is available.
Geographical Search Mode:
It is difficult for a customer to know where their closest HV substation is located simply based on the substation name.
Therefore, a geographical search mode is provided. The user may enter the coordinates of their site.
The workbook will then find the closest substation to the site and display the capacity.
Cell H12: | Select desired geographical search mode - either Latitude/Longitude or Easting/Northing.
Cells H4 & I4: | Enter Longitude and Latitude Coordinates for desired connection point.
Cells H8 & I8: | Enter Easting and Northing Coordinates for desired connection point.
Cell I12: | If the closest substation found has no capacity, the user may increment this figure to select the next furthest substation from the user's coordinates.
Disclaimer:
Copyright @ ESB. All rights reserved. No part of this work may be modified, reproduced of copied in any form or by any means - graphic, electronic or
mechanical, including photocopying, recording taping or used for any purpose other than its designated purpose, without the written permission of ESB.
This document is only valid at time of printing, You must obtain the latest revision online. Results are to be interpreted as indicative values only.

## 2. Master Gen Capacity List
Sum of Firm-Capacity [MW] | [6 empty] | Years (Year)
Trafo Type | Substation | Connection Voltage | Connection number | Scenario | Transformer Layout Ruleset | Connection Method Identifier | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050 | Sparkline
110 - 38 kV | ARDNACRUSHA | 38 | 1 | Conservative [MW] |  |  | 53.7036 | 53.9539 | 54.2075 | 54.4664 | 54.7301 | 54.9985 | 53.7093 | 53.6373 | 53.9716 | 54.3119 | 54.6587 | 55.0116 | 55.3701 | 55.7361 | 56.1053 | 56.482 | 58.3454 | 60.21
|  |  |  | Best View [MW] |  |  | 53.7036 | 53.9736 | 54.2466 | 54.5264 | 54.8133 | 55.1033 | 53.9401 | 53.9985 | 54.4696 | 54.9524 | 55.4471 | 55.9507 | 56.467 | 56.9937 | 57.5315 | 58.0772 | 60.7845 | 63.4931
|  |  |  | Base Case [MW] |  |  | 53.7036 | 54.0721 | 54.4498 | 54.8386 | 55.2359 | 55.6422 | 54.5516 | 54.6837 | 55.2296 | 55.7918 | 56.3669 | 56.955 | 57.5545 | 58.1686 | 58.7934 | 59.428 | 62.5748 | 65.7232
|  |  |  | Aggressive [MW] |  |  | 53.7036 | 54.2955 | 54.9126 | 55.5544 | 56.2184 | 56.9041 | 55.9033 | 56.1202 | 56.7535 | 57.4029 | 58.0659 | 58.7413 | 59.43 | 60.1315 | 60.8442 | 61.5621 | 65.1375 | 68.7138
| ARDNAGAPPARY | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| ARKLOW | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.02311 | 0.077267 | 0.13529
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.29032 | 0.59703 | 2.0871 | 3.58
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.035656 | 0.43348 | 0.84776 | 1.2811 | 1.7326 | 2.2039 | 4.5077 | 6.8148
|  |  | 2 | Conservative [MW] |  |  | 0 | 0 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671
|  |  |  | Best View [MW] |  |  | 0 | 0 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671 | 3.3671
| ATHLONE | 38 | 1 | Conservative [MW] |  |  | 42.9391 | 43.2133 | 43.4901 | 43.7685 | 44.0513 | 44.3468 | 41.0173 | 35.3741 | 35.6962 | 36.0247 | 36.3612 | 36.7048 | 37.0607 | 37.4188 | 37.7839 | 38.1573 | 40.0021 | 41.8482
|  |  |  | Best View [MW] |  |  | 42.9391 | 43.368 | 43.8035 | 44.246 | 44.6965 | 45.1653 | 41.8918 | 36.154 | 36.6153 | 37.0904 | 37.5843 | 38.0862 | 38.6015 | 39.1306 | 39.6715 | 40.2258 | 42.9618 | 45.7001
|  |  |  | Base Case [MW] |  |  | 42.9391 | 43.5317 | 44.1378 | 44.757 | 45.3929 | 46.0569 | 42.7154 | 36.8142 | 37.3512 | 37.8994 | 38.4643 | 39.0452 | 39.6421 | 40.2556 | 40.8846 | 41.5302 | 44.714 | 47.9005
|  |  |  | Aggressive [MW] |  |  | 42.9391 | 43.8582 | 44.8094 | 45.7993 | 46.8224 | 47.8932 | 44.438 | 38.2347 | 38.8914 | 39.5701 | 40.2689 | 40.9904 | 41.732 | 42.4966 | 43.2801 | 44.0837 | 48.048 | 52.0157
| BALLYCUMMIN | 38 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 77.805 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 77.805 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 77.805 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 77.805 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226 | 89.2226
| BALLYDINE | 38 | 1 | Conservative [MW] |  |  | 9.0754 | 9.1244 | 9.1744 | 9.2251 | 9.2767 | 9.3383 | 9.4091 | 9.4815 | 9.5557 | 9.6313 | 9.7091 | 9.7881 | 9.8691 | 9.9519 | 10.037 | 10.1232 | 10.5514 | 10.9798
|  |  |  | Best View [MW] |  |  | 9.0754 | 9.1308 | 9.1872 | 9.2452 | 9.3039 | 9.3732 | 9.4712 | 9.5722 | 9.6765 | 9.7843 | 9.8949 | 10.0093 | 10.1268 | 10.2479 | 10.3727 | 10.5011 | 11.1335 | 11.7666
|  |  |  | Base Case [MW] |  |  | 9.0754 | 9.1487 | 9.2238 | 9.3009 | 9.38 | 9.471 | 9.5808 | 9.6945 | 9.8119 | 9.9331 | 10.0585 | 10.188 | 10.3213 | 10.4592 | 10.6015 | 10.748 | 11.4691 | 12.191
|  |  |  | Aggressive [MW] |  |  | 9.0754 | 9.1897 | 9.3088 | 9.4326 | 9.5614 | 9.7074 | 9.8386 | 9.9747 | 10.1158 | 10.262 | 10.4136 | 10.5704 | 10.7329 | 10.9005 | 11.074 | 11.253 | 12.1333 | 13.0146
| BALLYLICKEY | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| BALLYRAGGET | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| BANDON | 38 | 1 | Conservative [MW] |  |  | 6.5846 | 6.7563 | 6.9287 | 7.1064 | 7.2873 | 7.471 | 7.6548 | 7.8411 | 8.0301 | 8.2225 | 8.4168 | 8.6131 | 8.813 | 9.0125 | 9.2126 | 9.414 | 10.4175 | 11.4212
|  |  |  | Best View [MW] |  |  | 6.5846 | 6.7659 | 6.9487 | 7.1369 | 7.3279 | 7.5231 | 7.7711 | 8.0244 | 8.2829 | 8.5454 | 8.8124 | 9.0805 | 9.3496 | 9.6235 | 9.9026 | 10.1842 | 11.5858 | 12.9878
|  |  |  | Base Case [MW] |  |  | 6.5846 | 6.833 | 7.0863 | 7.3472 | 7.6156 | 7.8899 | 8.1456 | 8.4068 | 8.6728 | 8.942 | 9.2101 | 9.4815 | 9.7596 | 10.0405 | 10.3238 | 10.6084 | 12.028 | 13.4478
|  |  |  | Aggressive [MW] |  |  | 6.5846 | 6.9277 | 7.2807 | 7.6481 | 8.0272 | 8.418 | 8.689 | 8.9628 | 9.2365 | 9.5131 | 9.7968 | 10.083 | 10.3716 | 10.6615 | 10.9547 | 11.2501 | 12.7213 | 14.1929
| BARNAHELY_A | 38 | 1 | Conservative [MW] |  |  | 39.3751 | 39.4752 | 39.5752 | 39.6787 | 39.7856 | 39.2751 | 39.3849 | 39.4926 | 39.6081 | 39.7216 | 39.8421 | 39.9644 | 40.086 | 40.2132 | 40.342 | 40.4725 | 41.1205 | 41.7689
|  |  |  | Best View [MW] |  |  | 39.3751 | 39.4824 | 39.5879 | 39.6969 | 39.8085 | 39.3032 | 39.4529 | 39.6022 | 39.7618 | 39.9195 | 40.0867 | 40.2557 | 40.4334 | 40.6112 | 40.7976 | 40.9872 | 41.9267 | 42.8667
|  |  |  | Base Case [MW] |  |  | 39.3751 | 39.5201 | 39.6676 | 39.8212 | 39.9806 | 39.5226 | 39.6783 | 39.8366 | 40.0006 | 40.1664 | 40.3403 | 40.5196 | 40.703 | 40.8903 | 41.0846 | 41.2811 | 42.2579 | 43.235
|  |  |  | Aggressive [MW] |  |  | 39.3751 | 39.5567 | 39.7399 | 39.9351 | 40.1344 | 39.7265 | 39.9285 | 40.1417 | 40.3616 | 40.587 | 40.8212 | 41.067 | 41.3197 | 41.5776 | 41.8482 | 42.1292 | 43.5065 | 44.8856
| BARRYMORE | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| BELLACORRICK | 38 | 1 | Conservative [MW] |  |  | 8.833 | 8.8418 | 8.8506 | -0.0001 | -0.0001 | 34.8395 | 34.8679 | 34.8973 | 34.9281 | 34.9589 | 34.9911 | 35.0243 | 35.0578 | 35.0927 | 35.1277 | 35.1639 | 35.3417 | 35.5197
|  |  |  | Best View [MW] |  |  | 8.833 | 8.8526 | 8.8726 | -0.0001 | -0.0001 | 34.8946 | 34.9322 | 34.9718 | 35.0128 | 35.0541 | 35.0978 | 35.1419 | 35.1883 | 35.2362 | 35.2854 | 35.337 | 35.5886 | 35.8406
|  |  |  | Base Case [MW] |  |  | 8.833 | 8.8594 | 8.8864 | -0.0001 | -0.0001 | 34.9295 | 34.9759 | 35.0243 | 35.0744 | 35.1263 | 35.1792 | 35.2358 | 35.2942 | 35.355 | 35.4182 | 35.4844 | 35.8076 | 36.1312
|  |  |  | Aggressive [MW] |  |  | 8.833 | 8.8834 | 8.9368 | -0.0001 | -0.0001 | 35.0646 | 35.1327 | 35.205 | 35.28 | 35.3601 | 35.4453 | 35.5338 | 35.628 | 35.7257 | 35.8296 | 35.9392 | 36.4718 | 37.0054
|  |  | 2 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505 | 28.1505
| BELMAYNE | 38 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 84.4315 | 84.5513 | 84.6705 | 84.7891 | 84.9152 | 85.0407 | 85.1697 | 85.3005 | 85.4348 | 85.5724 | 85.7079 | 86.3912 | 87.074
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 84.5385 | 84.6762 | 84.8173 | 84.9588 | 85.1022 | 85.2515 | 85.4026 | 85.5582 | 85.7196 | 85.8813 | 86.0489 | 86.8711 | 87.6942
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 84.652 | 84.8076 | 84.9675 | 85.1318 | 85.3005 | 85.472 | 85.6478 | 85.8305 | 86.0159 | 86.2066 | 86.3999 | 87.3594 | 88.3194
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 84.946 | 85.0909 | 85.2377 | 85.3904 | 85.5475 | 85.7049 | 85.8641 | 86.0316 | 86.1995 | 86.3716 | 86.5479 | 87.4184 | 88.2896
| BINBANE | 38 | 1 | Conservative [MW] |  |  | 22.8599 | 22.9109 | 22.9616 | 23.0137 | 23.0661 | 23.1182 | 23.2406 | 23.3659 | 23.4946 | 23.6264 | 23.7607 | 23.8981 | 24.039 | 24.1831 | 24.331 | 24.4817 | 25.2279 | 25.9745
|  |  |  | Best View [MW] |  |  | 22.8599 | 22.968 | 23.0789 | 23.192 | 23.307 | 23.4245 | 23.6058 | 23.7929 | 23.9864 | 24.1855 | 24.3916 | 24.6043 | 24.8241 | 25.0486 | 25.2768 | 25.5118 | 26.6684 | 27.8262
|  |  |  | Base Case [MW] |  |  | 22.8599 | 22.9846 | 23.1118 | 23.2417 | 23.3747 | 23.5112 | 23.7275 | 23.9531 | 24.1858 | 24.429 | 24.6806 | 24.9408 | 25.206 | 25.4803 | 25.7647 | 26.0607 | 27.5097 | 28.9607
|  |  |  | Aggressive [MW] |  |  | 22.8599 | 23.0495 | 23.2471 | 23.4512 | 23.6634 | 23.8839 | 24.1532 | 24.4341 | 24.7273 | 25.0333 | 25.3448 | 25.6711 | 26.0105 | 26.3663 | 26.736 | 27.1324 | 29.0432 | 30.9584
|  |  | 2 | Conservative [MW] |  |  | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285
|  |  |  | Best View [MW] |  |  | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285
|  |  |  | Base Case [MW] |  |  | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285
|  |  |  | Aggressive [MW] |  |  | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285 | 28.7285
| BLACKROCK | 38 | 1 | Conservative [MW] |  |  | 83.583 | 83.9366 | 84.3017 | 84.6778 | 85.0616 | 85.4565 | 85.7639 | 85.497 | 85.8114 | 86.1367 | 86.4704 | 86.8046 | 87.1469 | 87.4949 | 87.8538 | 88.2106 | 90.0001 | 91.7892
|  |  |  | Best View [MW] |  |  | 83.583 | 83.9928 | 84.419 | 84.8543 | 85.3055 | 85.7689 | 86.1387 | 85.9309 | 86.3101 | 86.7013 | 87.1016 | 87.5066 | 87.9204 | 88.3415 | 88.774 | 89.2081 | 91.3742 | 93.5407
|  |  |  | Base Case [MW] |  |  | 83.583 | 84.0448 | 84.5212 | 85.0243 | 85.535 | 86.0628 | 86.4808 | 86.3209 | 86.7613 | 87.2068 | 87.6655 | 88.1296 | 88.6114 | 89.096 | 89.5852 | 90.0923 | 92.5802 | 95.0711
|  |  |  | Aggressive [MW] |  |  | 83.583 | 84.2575 | 84.971 | 85.7132 | 86.4875 | 87.3022 | 87.7245 | 87.572 | 88.01 | 88.4551 | 88.9148 | 89.3688 | 89.8426 | 90.3238 | 90.8118 | 91.3113 | 93.7782 | 96.2471
| BLAKE | 38 | 1 | Conservative [MW] |  |  | 20.3079 | 20.4183 | 20.5263 | 20.3446 | 20.0524 | 20.0993 | 20.08 | 20.2115 | 20.3553 | 20.5009 | 20.6502 | 20.8013 | 20.953 | 21.1091 | 21.2675 | 21.4314 | 22.2363 | 23.042
|  |  |  | Best View [MW] |  |  | 20.3079 | 20.4462 | 20.5818 | 20.4284 | 20.1667 | 20.2429 | 20.2624 | 20.4384 | 20.6291 | 20.8234 | 21.0205 | 21.2235 | 21.4341 | 21.6413 | 21.8501 | 22.0573 | 23.0976 | 24.1377
|  |  |  | Base Case [MW] |  |  | 20.3079 | 20.4723 | 20.6351 | 20.5084 | 20.277 | 20.3843 | 20.429 | 20.6393 | 20.8655 | 21.096 | 21.337 | 21.5796 | 21.8212 | 22.063 | 22.3044 | 22.5437 | 23.7458 | 24.9476
|  |  |  | Aggressive [MW] |  |  | 20.3079 | 20.5286 | 20.7515 | 20.6815 | 20.5178 | 20.6899 | 20.7724 | 21.0415 | 21.3322 | 21.6297 | 21.925 | 22.2215 | 22.5162 | 22.8082 | 23.0888 | 23.3535 | 24.7196 | 26.083
| BLUNDELSTOWN | 38 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 78.1268 | 78.1268 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 78.1268 | 78.1268 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 78.1268 | 78.1268 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 78.1268 | 78.1268 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856 | 79.0856
| BOGGERAGH | 38 | 1 | Conservative [MW] |  |  | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416
|  |  |  | Best View [MW] |  |  | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416
|  |  |  | Base Case [MW] |  |  | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416
|  |  |  | Aggressive [MW] |  |  | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416 | 15.8416
| BOOLTIAGH | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  | 2 | Conservative [MW] |  |  | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487
|  |  |  | Best View [MW] |  |  | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487
|  |  |  | Base Case [MW] |  |  | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487
|  |  |  | Aggressive [MW] |  |  | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487 | 4.1487
| BUTLERSTOWN | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | 35.6349 | 35.8844 | 36.1387 | 36.4675 | 36.8035 | 37.1473 | 37.4984 | 37.857 | 38.2235 | 38.5975 | 38.9791 | 39.3688 | 39.7663 | 41.7328 | 43.7007
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | 35.7125 | 35.9892 | 36.2716 | 36.6936 | 37.1275 | 37.5736 | 38.031 | 38.5028 | 38.9855 | 39.4806 | 39.9883 | 40.5096 | 41.0423 | 43.6754 | 46.3104
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | 35.8582 | 36.1883 | 36.5257 | 37.0214 | 37.5337 | 38.062 | 38.6069 | 39.1684 | 39.7469 | 40.3416 | 40.9531 | 41.5817 | 42.2287 | 45.4145 | 48.6034
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | 36.4298 | 36.9737 | 37.5359 | 38.1692 | 38.8261 | 39.507 | 40.211 | 40.9398 | 41.6933 | 42.4701 | 43.2713 | 44.0973 | 44.9461 | 49.1292 | 53.3161
| CAHIR | 38 | 1 | Conservative [MW] |  |  | 7.5628 | 7.6359 | 7.7071 | 7.782 | 7.8566 | 7.9309 | 6.9419 | 6.9789 | 7.08 | 7.1823 | 7.2846 | 7.3859 | 7.4864 | 7.5875 | 7.6884 | 7.7866 | 8.2848 | 8.7825
|  |  |  | Best View [MW] |  |  | 7.5628 | 7.6493 | 7.7373 | 7.8267 | 7.9187 | 8.0087 | 7.0624 | 7.1409 | 7.2838 | 7.4272 | 7.5707 | 7.7106 | 7.8516 | 7.9875 | 8.1204 | 8.2487 | 8.9023 | 9.5552
|  |  |  | Base Case [MW] |  |  | 7.5628 | 7.6753 | 7.7899 | 7.9076 | 8.0259 | 8.1428 | 7.2001 | 7.2769 | 7.4176 | 7.5581 | 7.6928 | 7.8257 | 7.9507 | 8.0681 | 8.1763 | 8.2736 | 8.7894 | 9.3033
|  |  |  | Aggressive [MW] |  |  | 7.5628 | 7.7289 | 7.898 | 8.0679 | 8.2355 | 8.4002 | 7.4653 | 7.5431 | 7.6834 | 7.8185 | 7.9445 | 8.0586 | 8.159 | 8.2443 | 8.3118 | 8.3553 | 8.6369 | 8.9144
| CARLOW | 38 | 1 | Conservative [MW] |  |  | 3.779 | 4.0376 | 4.3008 | 4.5689 | 4.8408 | 3.7851 | 2.8597 | 2.8066 | 3.2089 | 3.619 | 4.0372 | 4.4637 | 4.8978 | 5.3398 | 5.7898 | 6.2485 | 8.5188 | 10.7905
|  |  |  | Best View [MW] |  |  | 3.779 | 4.0985 | 4.4254 | 4.7579 | 5.0973 | 4.1097 | 3.3221 | 3.4127 | 3.9633 | 4.5286 | 5.1093 | 5.7036 | 6.3127 | 6.9394 | 7.5801 | 8.2359 | 11.4747 | 14.716
|  |  |  | Base Case [MW] |  |  | 3.779 | 4.1697 | 4.5703 | 4.9808 | 5.4003 | 4.4949 | 3.8035 | 3.9903 | 4.6456 | 5.3214 | 6.0148 | 6.7299 | 7.4669 | 8.2229 | 8.9928 | 9.7662 | 13.6237 | 17.4818
|  |  |  | Aggressive [MW] |  |  | 3.779 | 4.3818 | 5.0055 | 5.6533 | 6.3216 | 5.6728 | 5.185 | 5.5885 | 6.4715 | 7.3883 | 8.3368 | 9.3025 | 10.2805 | 11.2815 | 12.2999 | 13.3572 | 18.5398 | 23.7289
| CARRICK ON SHANNON | 38 | 1 | Conservative [MW] |  |  | 23.6296 | 23.7232 | 23.8175 | 23.9136 | 24.01 | 24.1077 | 24.3034 | 24.5037 | 24.7075 | 24.9159 | 25.1289 | 25.3462 | 25.5678 | 25.7945 | 26.0253 | 26.2601 | 27.4236 | 28.5877
|  |  |  | Best View [MW] |  |  | 23.6296 | 23.7942 | 23.9612 | 24.1322 | 24.3051 | 24.4828 | 24.7472 | 25.0185 | 25.2975 | 25.5839 | 25.8773 | 26.1793 | 26.489 | 26.805 | 27.1298 | 27.4623 | 29.1044 | 30.7477
|  |  |  | Base Case [MW] |  |  | 23.6296 | 23.8418 | 24.0603 | 24.2832 | 24.5122 | 24.7468 | 25.0697 | 25.4025 | 25.7468 | 26.1003 | 26.4661 | 26.8423 | 27.228 | 27.6253 | 28.0339 | 28.4518 | 30.5165 | 32.5828
|  |  |  | Aggressive [MW] |  |  | 23.6296 | 23.9599 | 24.3034 | 24.6608 | 25.0319 | 25.4163 | 25.8536 | 26.3072 | 26.7783 | 27.2656 | 27.77 | 28.2918 | 28.83 | 29.3812 | 29.9498 | 30.5293 | 33.3976 | 36.2678
| CARRICKMINES | 38 | 1 | Conservative [MW] |  |  | 81.9393 | 82.4097 | 82.8875 | 83.3806 | 83.8812 | 83.24 | 83.6359 | 84.0418 | 84.4526 | 84.8662 | 85.2919 | 85.7158 | 86.1465 | 86.5838 | 87.028 | 87.4741 | 89.6996 | 91.9254
|  |  |  | Best View [MW] |  |  | 81.9393 | 82.4781 | 83.0363 | 83.611 | 84.2001 | 83.6464 | 84.1171 | 84.5982 | 85.0901 | 85.5835 | 86.085 | 86.594 | 87.1149 | 87.6383 | 88.1712 | 88.7082 | 91.3824 | 94.0572
|  |  |  | Base Case [MW] |  |  | 81.9393 | 82.5513 | 83.1795 | 83.8261 | 84.4933 | 84.022 | 84.559 | 85.1054 | 85.6614 | 86.2237 | 86.7965 | 87.3819 | 87.9683 | 88.5663 | 89.178 | 89.7865 | 92.8376 | 95.8881
|  |  |  | Aggressive [MW] |  |  | 81.9393 | 82.8253 | 83.7568 | 84.7203 | 85.7227 | 85.6104 | 86.1377 | 86.6794 | 87.2244 | 87.7813 | 88.3409 | 88.9138 | 89.4859 | 90.0662 | 90.6492 | 91.2338 | 94.1525 | 97.0714
| CARROWBEG | 38 | 1 | Conservative [MW] |  |  | 26.5737 | 26.609 | 26.6459 | 26.6842 | 26.7213 | 26.7578 | 26.9043 | 27.0529 | 27.2019 | 27.354 | 27.5056 | 27.6607 | 27.8167 | 27.9727 | 28.1309 | 28.2899 | 29.0828 | 29.8758
|  |  |  | Best View [MW] |  |  | 26.5737 | 26.658 | 26.7466 | 26.8325 | 26.9199 | 27.0095 | 27.1916 | 27.3762 | 27.5633 | 27.7525 | 27.9422 | 28.1368 | 28.3316 | 28.5239 | 28.7176 | 28.9105 | 29.8772 | 30.8438
|  |  |  | Base Case [MW] |  |  | 26.5737 | 26.6952 | 26.8206 | 26.947 | 27.0742 | 27.2035 | 27.4261 | 27.6522 | 27.8807 | 28.1119 | 28.3458 | 28.5797 | 28.8131 | 29.0409 | 29.2679 | 29.4891 | 30.6104 | 31.7308
|  |  |  | Aggressive [MW] |  |  | 26.5737 | 26.8209 | 27.0748 | 27.3362 | 27.5995 | 27.8682 | 28.1726 | 28.4818 | 28.7895 | 29.0934 | 29.3892 | 29.6696 | 29.9327 | 30.1625 | 30.3521 | 30.484 | 31.2972 | 32.1007
| CASTLEBAR | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 40.7749 | 41.051 | 41.3331 | 41.6222 | 41.9187 | 42.2211 | 42.5305 | 42.8466 | 43.1704 | 43.5014 | 43.8403 | 45.5138 | 47.1887
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 41.2575 | 41.6116 | 41.9741 | 42.3474 | 42.7318 | 43.1265 | 43.5321 | 43.9483 | 44.3764 | 44.8146 | 45.2638 | 47.4805 | 49.6989
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 41.6263 | 42.0637 | 42.5162 | 42.9832 | 43.4666 | 43.9652 | 44.4796 | 45.0108 | 45.5571 | 46.1196 | 46.698 | 49.5477 | 52.4
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 42.9464 | 43.5853 | 44.252 | 44.9467 | 45.6683 | 46.4191 | 47.196 | 47.9978 | 48.8248 | 49.6768 | 50.5508 | 54.8622 | 59.1772
| CATHALEENS FALL | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| CAUTEEN | 38 | 1 | Conservative [MW] |  |  | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779
|  |  |  | Best View [MW] |  |  | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779
|  |  |  | Base Case [MW] |  |  | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779
|  |  |  | Aggressive [MW] |  |  | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779 | 5.8779
|  |  | 2 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  | 3 | Conservative [MW] |  |  | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574
|  |  |  | Best View [MW] |  |  | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574
|  |  |  | Base Case [MW] |  |  | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574
|  |  |  | Aggressive [MW] |  |  | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574 | 17.7574
|  |  | 4 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615 | 21.0615
| CHARLEVILLE | 38 | 1 | Conservative [MW] |  |  | 3.106 | 3.2255 | 3.3472 | 3.4708 | 3.597 | 3.725 | 3.8647 | 4.0067 | 4.1511 | 4.2982 | 4.4477 | 4.5997 | 4.7544 | 4.9117 | 5.0713 | 5.2337 | 6.0381 | 6.843
|  |  |  | Best View [MW] |  |  | 3.106 | 3.2305 | 3.3572 | 3.4863 | 3.6178 | 3.7518 | 3.9387 | 4.13 | 4.326 | 4.5265 | 4.7316 | 4.9409 | 5.1549 | 5.3731 | 5.5957 | 5.8222 | 6.9445 | 8.0673
|  |  |  | Base Case [MW] |  |  | 3.106 | 3.27 | 3.4382 | 3.6103 | 3.7867 | 3.967 | 4.1862 | 4.4116 | 4.6427 | 4.8795 | 5.1223 | 5.3704 | 5.6245 | 5.8838 | 6.1484 | 6.4174 | 7.7507 | 9.0848
|  |  |  | Aggressive [MW] |  |  | 3.106 | 3.3565 | 3.6167 | 3.8864 | 4.1657 | 4.4545 | 4.7064 | 4.9649 | 5.2303 | 5.5022 | 5.7805 | 6.065 | 6.3552 | 6.6507 | 6.9503 | 7.2533 | 8.7592 | 10.2657
|  |  | 2 | Conservative [MW] |  |  | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088
|  |  |  | Best View [MW] |  |  | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088
|  |  |  | Base Case [MW] |  |  | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088
|  |  |  | Aggressive [MW] |  |  | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088 | 10.6088
| CHERRYWOOD | 38 | 1 | Conservative [MW] |  |  | 77.0688 | 77.2056 | 77.3523 | 77.4957 | 77.6496 | 77.8073 | 77.9289 | 78.0576 | 78.182 | 78.3221 | 78.4465 | 78.5901 | 78.7421 | 78.897 | 78.997 | 79.1602 | 79.8075 | 80.4653
|  |  |  | Best View [MW] |  |  | 77.0688 | 77.2289 | 77.3969 | 77.5698 | 77.7516 | 77.9286 | 78.0854 | 78.2337 | 78.3822 | 78.5392 | 78.7053 | 78.9006 | 79.0528 | 79.2085 | 79.3028 | 79.4538 | 80.0575 | 80.6707
|  |  |  | Base Case [MW] |  |  | 77.0688 | 77.2489 | 77.4413 | 77.6368 | 77.8376 | 78.0538 | 78.2268 | 78.3947 | 78.5852 | 78.7432 | 78.921 | 79.1315 | 79.2733 | 79.4334 | 79.5794 | 79.7545 | 80.5525 | 81.3553
|  |  |  | Aggressive [MW] |  |  | 77.0688 | 77.3326 | 77.6117 | 77.912 | 78.224 | 78.56 | 78.758 | 78.9239 | 79.0712 | 79.2219 | 79.3656 | 79.5194 | 79.6703 | 79.8298 | 79.984 | 80.1515 | 80.9535 | 81.7578
| CLOON | 38 | 1 | Conservative [MW] |  |  | 12.9686 | 13.065 | 13.1573 | 13.2507 | 13.3454 | 13.4609 | 13.6434 | 13.8299 | 14.0197 | 14.2143 | 14.4125 | 14.6154 | 14.8225 | 15.0331 | 15.2487 | 15.4677 | 16.5537 | 17.6402
|  |  |  | Best View [MW] |  |  | 12.9686 | 13.1116 | 13.2517 | 13.3943 | 13.54 | 13.7067 | 13.9591 | 14.2188 | 14.4853 | 14.7596 | 15.0413 | 15.3304 | 15.6267 | 15.9316 | 16.2422 | 16.5614 | 18.1345 | 19.7091
|  |  |  | Base Case [MW] |  |  | 12.9686 | 13.1549 | 13.3406 | 13.5303 | 13.7242 | 13.9425 | 14.2351 | 14.5378 | 14.8498 | 15.1711 | 15.5024 | 15.8431 | 16.1936 | 16.5531 | 16.9224 | 17.3022 | 19.1732 | 21.0459
|  |  |  | Aggressive [MW] |  |  | 12.9686 | 13.2861 | 13.6109 | 13.9487 | 14.2993 | 14.6824 | 15.0712 | 15.4747 | 15.893 | 16.3254 | 16.7721 | 17.2345 | 17.7137 | 18.2063 | 18.7092 | 19.2212 | 21.7569 | 24.2942
| COOKSTOWN | 38 | 1 | Conservative [MW] |  |  | 81.797 | 82.1513 | 82.5155 | 82.8873 | 83.3285 | 83.7625 | 84.1009 | 84.4509 | 84.8095 | 85.1773 | 85.554 | 85.9167 | 86.2669 | 86.6224 | 86.981 | 87.3503 | 89.1685 | 90.9884
|  |  |  | Best View [MW] |  |  | 81.797 | 82.2098 | 82.6316 | 83.0704 | 83.5854 | 84.0994 | 84.5014 | 84.9188 | 85.3437 | 85.7771 | 86.1811 | 86.5865 | 87.0039 | 87.4322 | 87.865 | 88.304 | 90.4826 | 92.6621
|  |  |  | Base Case [MW] |  |  | 81.797 | 82.2623 | 82.744 | 83.2445 | 83.8485 | 84.4355 | 84.8955 | 85.3698 | 85.843 | 86.2914 | 86.7494 | 87.2154 | 87.6912 | 88.1791 | 88.6747 | 89.1817 | 91.6862 | 94.1927
|  |  |  | Aggressive [MW] |  |  | 81.797 | 82.5036 | 83.2526 | 84.0697 | 85.0137 | 85.9624 | 86.388 | 86.8206 | 87.2627 | 87.714 | 88.175 | 88.6426 | 89.1191 | 89.6022 | 90.0963 | 90.5968 | 93.082 | 95.5683
| COOMATAGGERT | 38 | 1 | Conservative [MW] |  |  | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721
|  |  |  | Best View [MW] |  |  | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721
|  |  |  | Base Case [MW] |  |  | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721
|  |  |  | Aggressive [MW] |  |  | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721 | 20.1721
| CORDAL | 38 | 1 | Conservative [MW] |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Best View [MW] |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Base Case [MW] |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Aggressive [MW] |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| COURTLOUGH | 38 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 79.4378 | 79.5093 | 79.5848 | 79.6586 | 79.7358 | 79.8148 | 79.8949 | 79.9756 | 80.0603 | 80.1439 | 80.2304 | 80.655 | 81.0801
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 79.5019 | 79.5868 | 79.6728 | 79.7623 | 79.8524 | 79.9453 | 80.0417 | 80.1387 | 80.2363 | 80.339 | 80.4423 | 80.9572 | 81.4722
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 79.572 | 79.6709 | 79.7698 | 79.8716 | 79.9762 | 80.0832 | 80.193 | 80.3074 | 80.4218 | 80.5408 | 80.6621 | 81.2624 | 81.8631
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 79.7549 | 79.845 | 79.9385 | 80.0326 | 80.1296 | 80.2277 | 80.3281 | 80.432 | 80.5382 | 80.6449 | 80.7545 | 81.2948 | 81.8356
| COW CROSS | 38 | 1 | Conservative [MW] |  |  | 18.324 | 18.3588 | 18.394 | 18.4297 | 18.4658 | 18.5271 | 18.5644 | 17.7848 | 17.8242 | 17.8638 | 17.9047 | 17.9468 | 17.9891 | 18.0327 | 18.0772 | 18.1229 | 18.3483 | 18.5739
|  |  |  | Best View [MW] |  |  | 18.324 | 18.3606 | 18.3978 | 18.4352 | 18.4748 | 18.5377 | 18.588 | 17.8222 | 17.8762 | 17.932 | 17.9884 | 18.0474 | 18.1078 | 18.1695 | 18.2336 | 18.2999 | 18.6254 | 18.9513
|  |  |  | Base Case [MW] |  |  | 18.324 | 18.3733 | 18.4244 | 18.4773 | 18.5317 | 18.6111 | 18.6643 | 17.9009 | 17.9579 | 18.0161 | 18.0761 | 18.1383 | 18.2018 | 18.2668 | 18.3346 | 18.4037 | 18.7457 | 19.088
|  |  |  | Aggressive [MW] |  |  | 18.324 | 18.3925 | 18.4646 | 18.5393 | 18.6182 | 18.7206 | 18.778 | 18.0217 | 18.0826 | 18.1467 | 18.2121 | 18.2794 | 18.3489 | 18.4202 | 18.4935 | 18.5694 | 18.9418 | 19.3147
| CRANE | 38 | 1 | Conservative [MW] |  |  | 15.496 | 15.549 | 15.6025 | 15.6561 | 15.7107 | 15.7658 | 15.8963 | 16.0291 | 16.1664 | 16.3059 | 16.4488 | 16.5951 | 16.7455 | 16.8987 | 17.0548 | 17.2145 | 18.0034 | 18.7929
|  |  |  | Best View [MW] |  |  | 15.496 | 15.5887 | 15.6837 | 15.7803 | 15.8784 | 15.9781 | 16.1253 | 16.2765 | 16.431 | 16.5899 | 16.7526 | 16.9187 | 17.0892 | 17.2635 | 17.4417 | 17.6229 | 18.5208 | 19.4191
|  |  |  | Base Case [MW] |  |  | 15.496 | 15.6102 | 15.7273 | 15.8463 | 15.9686 | 16.0941 | 16.2584 | 16.4283 | 16.6024 | 16.781 | 16.9649 | 17.1532 | 17.346 | 17.5433 | 17.7441 | 17.9491 | 18.963 | 19.9776
|  |  |  | Aggressive [MW] |  |  | 15.496 | 15.6754 | 15.8607 | 16.0529 | 16.2517 | 16.4574 | 16.6998 | 16.9513 | 17.2119 | 17.4813 | 17.7572 | 18.0412 | 18.3326 | 18.6303 | 18.9337 | 19.2397 | 20.7628 | 22.2864
| DALLOW | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.032292 | 0.23135 | 0.78218 | 1.3608
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.16947 | 0.39807 | 0.63546 | 0.8816 | 2.089 | 3.2978
| DALTON | 38 | 1 | Conservative [MW] |  |  | 17.5619 | 17.6369 | 17.712 | 17.7879 | 17.8638 | 17.9673 | 18.1353 | 18.3063 | 18.4788 | 18.6534 | 18.8308 | 19.0096 | 19.1904 | 19.3734 | 19.5568 | 19.7417 | 20.6621 | 21.5828
|  |  |  | Best View [MW] |  |  | 17.5619 | 17.6825 | 17.8051 | 17.9283 | 18.0536 | 18.2083 | 18.4333 | 18.6632 | 18.8958 | 19.1316 | 19.37 | 19.612 | 19.8539 | 20.0978 | 20.3424 | 20.5853 | 21.8044 | 23.0232
|  |  |  | Base Case [MW] |  |  | 17.5619 | 17.7238 | 17.8873 | 18.0537 | 18.2227 | 18.4253 | 18.6881 | 18.9554 | 19.2263 | 19.5011 | 19.7791 | 20.0574 | 20.3365 | 20.6141 | 20.8872 | 21.155 | 22.5081 | 23.8604
|  |  |  | Aggressive [MW] |  |  | 17.5619 | 17.8498 | 18.1444 | 18.4467 | 18.7558 | 19.1113 | 19.4526 | 19.7987 | 20.1456 | 20.493 | 20.8345 | 21.1689 | 21.4905 | 21.7929 | 22.0659 | 22.2993 | 23.5717 | 24.8375
|  |  | 2 | Conservative [MW] |  |  | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254
|  |  |  | Best View [MW] |  |  | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254
|  |  |  | Base Case [MW] |  |  | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254
|  |  |  | Aggressive [MW] |  |  | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254 | 20.3254
| DERRYIRON | 38 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85 | 59.85
| DONORE ROAD | 38 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 78.4697 | 67.1254 | 67.7337 | 67.9444 | 68.1582 | 68.373 | 68.5919 | 68.8131 | 69.0333 | 69.2573 | 69.4812 | 70.601 | 71.7207
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 78.4697 | 67.3211 | 67.9843 | 68.2526 | 68.5234 | 68.797 | 69.0751 | 69.353 | 69.6334 | 69.9146 | 70.1956 | 71.6011 | 73.0065
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 78.4697 | 67.7579 | 68.4768 | 68.8004 | 69.1252 | 69.454 | 69.7844 | 70.1132 | 70.4415 | 70.7622 | 71.0754 | 72.6612 | 74.2458
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 78.4697 | 68.3302 | 69.1466 | 69.5623 | 69.9804 | 70.3967 | 70.8023 | 71.1978 | 71.5709 | 71.9175 | 72.2244 | 73.8648 | 75.4985
| DOON | 38 | 1 | Conservative [MW] |  |  | 3.8807 | 4.0037 | 4.1282 | 4.2549 | 4.3832 | 4.5137 | 4.6875 | 4.8641 | 5.0444 | 5.2275 | 5.414 | 5.6035 | 5.7964 | 5.9923 | 6.1918 | 6.3934 | 7.3959 | 8.3987
|  |  |  | Best View [MW] |  |  | 3.8807 | 4.0193 | 4.1607 | 4.3043 | 4.4504 | 4.5991 | 4.8392 | 5.0849 | 5.3362 | 5.594 | 5.8576 | 6.1271 | 6.4017 | 6.6824 | 6.9678 | 7.2571 | 8.6931 | 10.1297
|  |  |  | Base Case [MW] |  |  | 3.8807 | 4.0639 | 4.2512 | 4.443 | 4.6386 | 4.8383 | 5.1054 | 5.3791 | 5.6602 | 5.9481 | 6.2423 | 6.5436 | 6.8507 | 7.1634 | 7.4814 | 7.8043 | 9.4057 | 11.008
|  |  |  | Aggressive [MW] |  |  | 3.8807 | 4.1663 | 4.4628 | 4.7688 | 5.0843 | 5.4102 | 5.724 | 6.0463 | 6.3762 | 6.715 | 7.0601 | 7.4124 | 7.771 | 8.135 | 8.5029 | 8.8748 | 10.7235 | 12.573
| DROMBEG | 38 | 1 | Conservative [MW] |  |  | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733
|  |  |  | Best View [MW] |  |  | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733
|  |  |  | Base Case [MW] |  |  | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733
|  |  |  | Aggressive [MW] |  |  | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733 | 6.4733
| DRUMLINE | 38 | 1 | Conservative [MW] |  |  | 31.6241 | 31.8312 | 32.0404 | 32.2533 | 32.4701 | 32.6885 | 32.9342 | 33.1856 | 33.4387 | 33.6951 | 33.9547 | 34.2191 | 34.4855 | 34.7557 | 35.0271 | 35.3016 | 36.6658 | 38.0305
|  |  |  | Best View [MW] |  |  | 31.6241 | 31.8363 | 32.0508 | 32.2689 | 32.4902 | 32.7151 | 33.0485 | 33.3907 | 33.737 | 34.0885 | 34.4479 | 34.811 | 35.1796 | 35.5517 | 35.9291 | 36.3091 | 38.2021 | 40.0955
|  |  |  | Base Case [MW] |  |  | 31.6241 | 31.9149 | 32.2135 | 32.5158 | 32.8256 | 33.1415 | 33.5333 | 33.9347 | 34.3426 | 34.7572 | 35.1792 | 35.6072 | 36.0406 | 36.4776 | 36.9176 | 37.358 | 39.5591 | 41.7602
|  |  |  | Aggressive [MW] |  |  | 31.6241 | 32.095 | 32.5824 | 33.0849 | 33.602 | 34.1345 | 34.5832 | 35.0381 | 35.5035 | 35.9724 | 36.4485 | 36.9267 | 37.4047 | 37.8836 | 38.3571 | 38.8206 | 41.1646 | 43.507
| DRYBRIDGE | 38 | 1 | Conservative [MW] |  |  | 35.1847 | 35.6107 | 36.0448 | 36.4847 | 36.7045 | 37.6835 | 50.4519 | 50.2096 | 50.5922 | 50.9821 | 51.3823 | 51.7914 | 52.2096 | 52.638 | 53.0753 | 53.5228 | 55.7329 | 57.9447
|  |  |  | Best View [MW] |  |  | 35.1847 | 35.6833 | 36.1911 | 36.7079 | 37.0053 | 38.0601 | 50.7991 | 50.6728 | 51.176 | 51.6948 | 52.2272 | 52.7771 | 53.3407 | 53.9197 | 54.516 | 55.1259 | 58.1393 | 61.1549
|  |  |  | Base Case [MW] |  |  | 35.1847 | 35.89 | 36.6131 | 37.3552 | 37.8822 | 39.1615 | 51.638 | 51.6222 | 52.2392 | 52.8796 | 53.5398 | 54.2216 | 54.9233 | 55.6447 | 56.3887 | 57.1528 | 60.9197 | 64.6899
|  |  |  | Aggressive [MW] |  |  | 35.1847 | 36.1397 | 37.1292 | 38.1512 | 38.967 | 40.5273 | 52.7382 | 52.9177 | 53.7407 | 54.5965 | 55.4851 | 56.4052 | 57.3573 | 58.3403 | 59.3511 | 60.3855 | 65.4946 | 70.6075
| DUNDALK | 38 | 1 | Conservative [MW] |  |  | 24.9382 | 25.2662 | 25.6014 | 25.9431 | 26.2911 | 26.6459 | 27.0457 | 27.4536 | 27.8705 | 28.2956 | 28.7282 | 29.1698 | 29.6202 | 30.0789 | 30.5464 | 31.0209 | 33.3747 | 35.7296
|  |  |  | Best View [MW] |  |  | 24.9382 | 25.3114 | 25.6924 | 26.0831 | 26.4812 | 26.8886 | 27.4447 | 28.0165 | 28.6036 | 29.2068 | 29.8263 | 30.4608 | 31.11 | 31.7707 | 32.4478 | 33.1398 | 36.5601 | 39.9828
|  |  |  | Base Case [MW] |  |  | 24.9382 | 25.4676 | 26.0153 | 26.5784 | 27.1603 | 27.7589 | 28.4088 | 29.0774 | 29.7661 | 30.4745 | 31.203 | 31.943 | 32.7046 | 33.4852 | 34.2855 | 35.1053 | 39.152 | 43.202
|  |  |  | Aggressive [MW] |  |  | 24.9382 | 25.6721 | 26.4375 | 27.2364 | 28.0676 | 28.9332 | 29.7362 | 30.5652 | 31.4181 | 32.2941 | 33.1969 | 34.1261 | 35.0809 | 36.0586 | 37.0527 | 38.0589 | 43.0578 | 48.0587
| DUNGARVAN | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 31.2509 | 31.5259 | 31.8594 | 32.2009 | 32.5505 | 32.9067 | 33.2707 | 33.6426 | 34.0226 | 34.4108 | 34.8064 | 35.21 | 37.2066 | 39.2045
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 31.3603 | 31.6651 | 32.1189 | 32.5854 | 33.0662 | 33.5605 | 34.0689 | 34.5922 | 35.1297 | 35.6818 | 36.248 | 36.8295 | 39.6961 | 42.5652
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 31.7355 | 32.1449 | 32.6485 | 33.1673 | 33.7024 | 34.2534 | 34.8217 | 35.4073 | 36.0084 | 36.6276 | 37.2632 | 37.9168 | 41.1369 | 44.36
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 32.5571 | 33.2057 | 33.7983 | 34.4106 | 35.0442 | 35.6983 | 36.3732 | 37.0697 | 37.7877 | 38.5262 | 39.2849 | 40.0652 | 43.9092 | 47.7568
| DUNMANWAY | 38 | 1 | Conservative [MW] |  |  | 9.1431 | 9.3529 | 9.5646 | 9.7875 | 10.0158 | 10.278 | 10.5133 | 10.7542 | 11.0006 | 11.2527 | 11.5104 | 11.7739 | 12.0435 | 12.3188 | 12.6002 | 12.8887 | 14.3124 | 15.7373
|  |  |  | Best View [MW] |  |  | 9.1431 | 9.3654 | 9.5897 | 9.8264 | 10.0675 | 10.3449 | 10.6641 | 10.993 | 11.3331 | 11.6831 | 12.0435 | 12.4143 | 12.7966 | 13.1901 | 13.5958 | 14.013 | 16.068 | 18.1251
|  |  |  | Base Case [MW] |  |  | 9.1431 | 9.4485 | 9.7622 | 10.0928 | 10.4333 | 10.8176 | 11.1521 | 11.4977 | 11.8535 | 12.2196 | 12.5975 | 12.986 | 13.3867 | 13.7988 | 14.2224 | 14.6612 | 16.8146 | 18.9705
|  |  |  | Aggressive [MW] |  |  | 9.1431 | 9.5644 | 10.0082 | 10.4752 | 10.9643 | 11.5117 | 11.8741 | 12.2479 | 12.6338 | 13.0314 | 13.4403 | 13.862 | 14.2962 | 14.7429 | 15.2019 | 15.674 | 17.9994 | 20.327
| EAST ATHLONE | 38 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 77.805 | 81.6883 | 87.3999 | 87.6167 | 87.8358 | 88.0601 | 88.2916 | 88.5262 | 88.763 | 89.0104 | 89.26 | 90.5021 | 91.7446
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 77.805 | 81.8957 | 87.9457 | 88.2625 | 88.5915 | 88.9306 | 89.2777 | 89.6373 | 90.0029 | 90.3834 | 90.7704 | 92.6882 | 94.607
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 77.805 | 82.1062 | 88.447 | 88.8088 | 89.1767 | 89.5587 | 89.954 | 90.3631 | 90.7793 | 91.2096 | 91.654 | 93.8384 | 96.0251
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 77.805 | 82.5072 | 89.3903 | 89.8152 | 90.2621 | 90.7174 | 91.193 | 91.6793 | 92.1839 | 92.702 | 93.2339 | 95.8564 | 98.4813
| EAST GALWAY | 38 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 73.9435 | 73.7567 | 73.9122 | 74.073 | 74.2369 | 74.4042 | 74.5761 | 74.7518 | 74.9312 | 75.1133 | 75.302 | 76.228 | 77.155
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 74.1739 | 74.0509 | 74.2768 | 74.5113 | 74.7505 | 74.9993 | 75.2558 | 75.5184 | 75.7917 | 76.0709 | 76.3602 | 77.7797 | 79.2009
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 74.4296 | 74.3365 | 74.5958 | 74.8627 | 75.1384 | 75.425 | 75.7206 | 76.026 | 76.3429 | 76.6701 | 77.0073 | 78.6664 | 80.3273
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 75.0396 | 75.0066 | 75.3332 | 75.6707 | 76.0246 | 76.39 | 76.7706 | 77.1654 | 77.5759 | 78.0007 | 78.442 | 80.6044 | 82.7695
| ENNIS | 38 | 1 | Conservative [MW] |  |  | 20.4386 | 20.6141 | 60.1009 | 60.2993 | 60.4991 | 60.7124 | 60.9936 | 61.2828 | 61.5768 | 61.8779 | 62.1851 | 62.4996 | 62.8214 | 63.1496 | 63.4837 | 63.8251 | 65.5128 | 67.2018
|  |  |  | Best View [MW] |  |  | 20.4386 | 20.6412 | 60.1598 | 60.389 | 60.6206 | 60.8681 | 61.271 | 61.6862 | 62.115 | 62.5572 | 63.0121 | 63.4803 | 63.9636 | 64.4598 | 64.9722 | 65.4968 | 68.0873 | 70.6799
|  |  |  | Base Case [MW] |  |  | 20.4386 | 20.7555 | 60.4149 | 60.7781 | 61.1548 | 61.5521 | 62.0093 | 62.484 | 62.9736 | 63.4796 | 64.0009 | 64.539 | 65.0933 | 65.6652 | 66.2571 | 66.8632 | 69.8558 | 72.8508
|  |  |  | Aggressive [MW] |  |  | 20.4386 | 20.9829 | 60.9327 | 61.5886 | 62.2764 | 63.0113 | 63.5524 | 64.1115 | 64.6906 | 65.2874 | 65.9046 | 66.5415 | 67.1998 | 67.8752 | 68.5733 | 69.2906 | 72.8257 | 76.3641
| FASSAROE | 38 | 1 | Conservative [MW] |  |  | 82.3955 | 82.8158 | 83.2452 | 83.6871 | 84.1293 | 84.5903 | 84.9434 | 85.2991 | 85.667 | 86.0373 | 86.4104 | 86.7931 | 87.1755 | 87.5677 | 87.9619 | 88.3558 | 90.3261 | 92.2963
|  |  |  | Best View [MW] |  |  | 82.3955 | 82.8842 | 83.3815 | 83.8927 | 84.4154 | 84.949 | 85.3685 | 85.796 | 86.23 | 86.6742 | 87.1216 | 87.5772 | 88.0378 | 88.5038 | 88.9767 | 89.4499 | 91.8152 | 94.1805
|  |  |  | Base Case [MW] |  |  | 82.3955 | 82.9425 | 83.5075 | 84.0809 | 84.6766 | 85.285 | 85.7591 | 86.2445 | 86.7436 | 87.2423 | 87.7543 | 88.2723 | 88.7984 | 89.3299 | 89.868 | 90.4085 | 93.1047 | 95.8013
|  |  |  | Aggressive [MW] |  |  | 82.3955 | 83.1949 | 84.019 | 84.8813 | 85.7723 | 86.6976 | 87.1673 | 87.6496 | 88.1378 | 88.6287 | 89.1273 | 89.6308 | 90.1427 | 90.6505 | 91.1679 | 91.6899 | 94.2877 | 96.8862
| FINGLAS | 38 | 1 | Conservative [MW] |  |  | 93.6782 | 94.2333 | 94.7996 | 95.3802 | 98.6768 | 98.5972 | 98.5611 | 98.6757 | 99.1712 | 99.6633 | 100.1731 | 100.6792 | 101.1915 | 101.71 | 102.2261 | 102.75 | 105.3488 | 107.9489
|  |  |  | Best View [MW] |  |  | 93.6782 | 94.3153 | 94.9715 | 95.6375 | 99.0176 | 99.1938 | 99.0648 | 99.2435 | 99.8042 | 100.3695 | 100.9393 | 101.5153 | 102.0976 | 102.6769 | 103.2611 | 103.8434 | 106.7599 | 109.6761
|  |  |  | Base Case [MW] |  |  | 93.6782 | 94.4158 | 95.1622 | 95.9324 | 99.4135 | 99.749 | 99.6231 | 99.8643 | 100.4823 | 101.1074 | 101.7416 | 102.3765 | 103.0135 | 103.649 | 104.2845 | 104.9185 | 108.0925 | 111.2663
|  |  |  | Aggressive [MW] |  |  | 93.6782 | 94.8459 | 96.0558 | 97.5166 | 101.252 | 102.1153 | 101.9861 | 102.223 | 102.8248 | 103.4286 | 104.0303 | 104.6292 | 105.2265 | 106.1004 | 106.9015 | 107.5077 | 111.0586 | 114.577
|  |  | 2 | Conservative [MW] |  |  | 74.5538 | 75.2379 | 75.9893 | 76.7171 | 77.467 | 78.2403 | 77.8329 | 74.6933 | 75.0795 | 75.4738 | 75.8749 | 76.2837 | 76.6957 | 77.1159 | 77.5398 | 77.9727 | 80.113 | 82.2548
|  |  |  | Best View [MW] |  |  | 74.5538 | 75.3094 | 76.1363 | 76.9479 | 77.7797 | 78.6427 | 78.3072 | 75.1572 | 75.61 | 76.0728 | 76.5422 | 77.0198 | 77.5064 | 78.0028 | 78.5029 | 79.0155 | 81.545 | 84.0766
|  |  |  | Base Case [MW] |  |  | 74.5538 | 75.3862 | 76.2941 | 77.186 | 78.1136 | 79.0697 | 78.8089 | 75.6456 | 76.1648 | 76.6957 | 77.2346 | 77.7854 | 78.3453 | 78.9182 | 79.4966 | 80.0915 | 83.022 | 85.9553
|  |  |  | Aggressive [MW] |  |  | 74.5538 | 75.5764 | 76.6903 | 77.8043 | 78.9633 | 80.1707 | 79.8633 | 76.5011 | 76.9777 | 77.4633 | 77.9565 | 78.4569 | 78.9651 | 79.4819 | 80.0043 | 80.6548 | 83.5658 | 86.4981
| FRANCIS STREET | 38 | 1 | Conservative [MW] |  |  | 84.8576 | 85.2661 | 85.6863 | 86.1118 | 89.0674 | 86.8763 | 87.2638 | 87.6662 | 88.0734 | 88.4872 | 88.907 | 89.3333 | 89.7667 | 90.2031 | 90.6462 | 91.0955 | 93.3256 | 95.5567
|  |  |  | Best View [MW] |  |  | 84.8576 | 85.3347 | 85.8258 | 86.327 | 89.3424 | 87.232 | 87.6781 | 88.1322 | 88.5936 | 89.0669 | 89.5429 | 90.027 | 90.5194 | 91.0172 | 91.5222 | 92.03 | 94.5617 | 97.0939
|  |  |  | Base Case [MW] |  |  | 84.8576 | 85.4105 | 85.9811 | 86.5694 | 89.6591 | 87.6502 | 88.1442 | 88.6485 | 89.1592 | 89.6827 | 90.2111 | 90.7478 | 91.2938 | 91.8439 | 92.4029 | 92.9688 | 95.7798 | 98.5919
|  |  |  | Aggressive [MW] |  |  | 84.8576 | 85.8003 | 86.7857 | 87.8215 | 91.3171 | 89.8305 | 90.3337 | 90.8496 | 91.3679 | 91.893 | 92.4249 | 92.9634 | 93.5042 | 94.0449 | 94.5939 | 95.1959 | 98.0648 | 100.9424
| GALWAY | 38 | 1 | Conservative [MW] |  |  | 87.3691 | 87.6903 | 88.01 | 88.337 | 88.6622 | 86.2831 | 86.7116 | 87.1459 | 87.5806 | 88.0259 | 88.4788 | 88.929 | 89.3914 | 89.8578 | 90.3308 | 90.805 | 93.1729 | 95.5409
|  |  |  | Best View [MW] |  |  | 87.3691 | 87.7834 | 88.2032 | 88.6248 | 89.0514 | 86.7127 | 87.3234 | 87.9423 | 88.5715 | 89.2128 | 89.8652 | 90.5255 | 91.1927 | 91.8659 | 92.5412 | 93.2166 | 96.5934 | 99.9703
|  |  |  | Base Case [MW] |  |  | 87.3691 | 87.8993 | 88.436 | 88.9818 | 89.5365 | 87.2791 | 87.9556 | 88.643 | 89.3406 | 90.0551 | 90.7776 | 91.5068 | 92.2391 | 92.9772 | 93.7088 | 94.4365 | 98.0855 | 101.7338
|  |  |  | Aggressive [MW] |  |  | 87.3691 | 88.2047 | 89.0605 | 89.9293 | 90.828 | 88.7633 | 89.5638 | 90.3846 | 91.2112 | 92.0491 | 92.8855 | 93.7198 | 94.5506 | 95.3651 | 96.1574 | 96.9201 | 100.8126 | 104.7001
| GARVAGH | 38 | 1 | Conservative [MW] |  |  | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247
|  |  |  | Best View [MW] |  |  | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247
|  |  |  | Base Case [MW] |  |  | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247
|  |  |  | Aggressive [MW] |  |  | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247 | 27.3247
| GLASMORE | 38 | 1 | Conservative [MW] |  |  | 63.587 | 63.1848 | 63.6976 | 63.5064 | 64.0259 | 72.7884 | 73.0347 | 73.2899 | 73.5451 | 73.802 | 74.0646 | 74.33 | 74.6021 | 74.8729 | 75.1541 | 75.4324 | 76.8315 | 78.2302
|  |  |  | Best View [MW] |  |  | 63.587 | 63.2365 | 63.8034 | 63.6649 | 64.245 | 73.0122 | 73.301 | 73.5941 | 73.8902 | 74.1938 | 74.5008 | 74.8111 | 75.1284 | 75.4536 | 75.7802 | 76.112 | 77.757 | 79.4029
|  |  |  | Base Case [MW] |  |  | 63.587 | 63.2908 | 63.9163 | 63.8326 | 64.476 | 73.2514 | 73.5757 | 73.9124 | 74.2528 | 74.5982 | 74.9551 | 75.3113 | 75.6786 | 76.0472 | 76.4299 | 76.8126 | 78.7261 | 80.6395
|  |  |  | Aggressive [MW] |  |  | 63.587 | 63.4303 | 64.2034 | 64.2629 | 65.0685 | 73.8652 | 74.164 | 74.4745 | 74.784 | 75.103 | 75.4235 | 75.7493 | 76.0804 | 76.4173 | 76.7578 | 77.1066 | 78.8285 | 80.5518
| GLENLARA | 38 | 1 | Conservative [MW] |  |  | 16.8328 | 16.9328 | 17.0233 | 17.115 | 17.2079 | 17.3022 | 17.442 | 17.5848 | 17.7306 | 17.8795 | 18.0309 | 18.1859 | 18.344 | 18.5067 | 18.6726 | 18.8421 | 19.68 | 20.5186
|  |  |  | Best View [MW] |  |  | 16.8328 | 16.9526 | 17.0632 | 17.1761 | 17.291 | 17.408 | 17.604 | 17.8057 | 18.0134 | 18.2268 | 18.4474 | 18.6752 | 18.9089 | 19.1492 | 19.3957 | 19.6487 | 20.8965 | 22.1453
|  |  |  | Base Case [MW] |  |  | 16.8328 | 16.9989 | 17.1586 | 17.3217 | 17.4897 | 17.6616 | 17.8653 | 18.0748 | 18.2901 | 18.5133 | 18.7433 | 18.9797 | 19.2218 | 19.4707 | 19.7261 | 19.9877 | 21.2791 | 22.5716
|  |  |  | Aggressive [MW] |  |  | 16.8328 | 17.0661 | 17.2961 | 17.5353 | 17.7829 | 18.0394 | 18.2894 | 18.5491 | 18.8182 | 19.0957 | 19.3817 | 19.6768 | 19.9803 | 20.2926 | 20.613 | 20.942 | 22.5639 | 24.1873
|  |  | 2 | Conservative [MW] |  |  | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132
|  |  |  | Best View [MW] |  |  | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132
|  |  |  | Base Case [MW] |  |  | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132
|  |  |  | Aggressive [MW] |  |  | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132 | 21.0132
| GLENREE | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| GORTAWEE | 38 | 1 | Conservative [MW] |  |  | 39.7625 | 39.8476 | 39.9338 | 40.0215 | 40.1112 | 40.2021 | 40.3297 | 40.4595 | 40.5925 | 40.7286 | 40.8677 | 41.011 | 41.1567 | 41.3053 | 41.4584 | 41.6141 | 42.3858 | 43.158
|  |  |  | Best View [MW] |  |  | 39.7625 | 39.8713 | 39.9829 | 40.0971 | 40.214 | 40.3332 | 40.5108 | 40.6936 | 40.8831 | 41.0786 | 41.2799 | 41.4869 | 41.7001 | 41.9203 | 42.1474 | 42.3805 | 43.5299 | 44.6803
|  |  |  | Base Case [MW] |  |  | 39.7625 | 39.8981 | 40.0379 | 40.1815 | 40.3288 | 40.4806 | 40.6816 | 40.8889 | 41.1038 | 41.3254 | 41.5548 | 41.7926 | 42.0368 | 42.2896 | 42.551 | 42.8194 | 44.1426 | 45.467
|  |  |  | Aggressive [MW] |  |  | 39.7625 | 39.9732 | 40.194 | 40.4236 | 40.6634 | 40.9127 | 41.1725 | 41.4428 | 41.7251 | 42.0176 | 42.3215 | 42.6375 | 42.9637 | 43.3022 | 43.6529 | 44.0158 | 45.798 | 47.5822
| GRANGE (DR) | 38 | 1 | Conservative [MW] |  |  | 51.9902 | 53.1334 | 53.6292 | 54.1196 | 54.6233 | 47.7382 | 47.9358 | 48.1438 | 48.3497 | 48.5591 | 48.7722 | 48.9898 | 49.2105 | 49.436 | 49.6657 | 49.9008 | 51.0619 | 52.2239
|  |  |  | Best View [MW] |  |  | 51.9902 | 53.1817 | 53.7285 | 54.2726 | 54.8354 | 47.9175 | 48.1476 | 48.3899 | 48.6316 | 48.8773 | 49.128 | 49.3848 | 49.6472 | 49.9154 | 50.1892 | 50.4675 | 51.847 | 53.2272
|  |  |  | Base Case [MW] |  |  | 51.9902 | 53.2328 | 53.834 | 54.4356 | 55.0597 | 48.1091 | 48.3729 | 48.6495 | 48.9276 | 49.2105 | 49.5009 | 49.7992 | 50.1037 | 50.415 | 50.7333 | 51.0587 | 52.6669 | 54.2763
|  |  |  | Aggressive [MW] |  |  | 51.9902 | 53.3597 | 54.1005 | 54.8526 | 55.6389 | 48.6043 | 48.8498 | 49.1074 | 49.3633 | 49.6238 | 49.8919 | 50.1645 | 50.4417 | 50.7239 | 51.0126 | 51.3079 | 52.7667 | 54.2266
| GRANGE CASTLE | 38 | 1 | Conservative [MW] |  |  | 93.1384 | 93.5377 | 93.9444 | 94.365 | 100.4708 | 100.3206 | 100.5599 | 100.8033 | 101.0508 | 101.3022 | 101.5542 | 101.8104 | 102.0703 | 102.3365 | 102.6005 | 102.871 | 104.2062 | 105.5424
|  |  |  | Best View [MW] |  |  | 93.1384 | 93.5837 | 94.037 | 94.5023 | 100.6473 | 100.5395 | 100.8233 | 101.1023 | 101.3914 | 101.6849 | 101.9825 | 102.2865 | 102.5887 | 102.9033 | 103.2156 | 103.5343 | 105.1108 | 106.6884
|  |  |  | Base Case [MW] |  |  | 93.1384 | 93.6232 | 94.1338 | 94.6506 | 100.8317 | 100.7734 | 101.0921 | 101.4123 | 101.7431 | 102.078 | 102.42 | 102.7628 | 103.1185 | 103.4689 | 103.8287 | 104.1888 | 105.9884 | 107.788
|  |  |  | Aggressive [MW] |  |  | 93.1384 | 93.7496 | 94.3902 | 95.0532 | 101.3422 | 101.4263 | 101.7174 | 102.0155 | 102.3204 | 102.6322 | 102.9476 | 103.2607 | 103.586 | 103.9058 | 104.2289 | 104.5547 | 106.1765 | 107.7987
| GREAT ISLAND | 38 | 1 | Conservative [MW] |  |  | 33.317 | 17.9505 | 18.0292 | 18.1091 | 55.7867 | 55.8737 | 56.0621 | 56.2574 | 56.4594 | 56.6669 | 56.8809 | 57.1008 | 57.3267 | 57.5591 | 57.7982 | 58.0423 | 59.2494 | 60.4573
|  |  |  | Best View [MW] |  |  | 33.317 | 18.0007 | 18.1312 | 18.2647 | 56.0107 | 56.158 | 56.3781 | 56.6056 | 56.8396 | 57.0817 | 57.3302 | 57.588 | 57.8514 | 58.124 | 58.404 | 58.6934 | 60.1152 | 61.5385
|  |  |  | Base Case [MW] |  |  | 33.317 | 18.0295 | 18.19 | 18.3544 | 56.1403 | 56.3262 | 56.5753 | 56.8331 | 57.1008 | 57.3765 | 57.6613 | 57.9565 | 58.2612 | 58.5751 | 58.8998 | 59.2297 | 60.8653 | 62.5017
|  |  |  | Aggressive [MW] |  |  | 33.317 | 18.1187 | 18.3744 | 18.6397 | 56.5631 | 56.8736 | 57.2396 | 57.6221 | 58.0226 | 58.4414 | 58.8778 | 59.328 | 59.8021 | 60.2975 | 60.8122 | 61.1317 | 63.2499 | 65.3355
| GRIFFINRATH | 38 | 1 | Conservative [MW] |  |  | 25.6536 | 26.2772 | 26.9179 | 27.5737 | 36.1512 | 48.334 | 47.8595 | 48.1562 | 48.4561 | 48.7624 | 49.0724 | 49.3858 | 49.7018 | 50.023 | 50.3479 | 50.6769 | 52.311 | 53.9459
|  |  |  | Best View [MW] |  |  | 25.6536 | 26.3478 | 27.0601 | 27.7917 | 36.4148 | 48.6068 | 48.1802 | 48.5274 | 48.8808 | 49.2377 | 49.6008 | 49.9695 | 50.342 | 50.7201 | 51.103 | 51.4894 | 53.4121 | 55.3353
|  |  |  | Base Case [MW] |  |  | 25.6536 | 26.4183 | 27.2066 | 28.018 | 36.6878 | 48.8866 | 48.5081 | 48.9044 | 49.3058 | 49.7146 | 50.1294 | 50.5511 | 50.9785 | 51.4095 | 51.8474 | 52.2906 | 54.4923 | 56.6949
|  |  |  | Aggressive [MW] |  |  | 25.6536 | 26.6169 | 27.6162 | 28.6518 | 37.4566 | 49.7082 | 49.3081 | 49.6777 | 50.0517 | 50.4298 | 50.8136 | 51.2018 | 51.5955 | 51.9912 | 52.3933 | 52.7984 | 54.8158 | 56.8337
| IKERRIN | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 8.5017 | 8.6452 | 8.7919 | 8.9414 | 9.0953 | 9.2521 | 9.4123 | 9.5757 | 9.7421 | 9.9119 | 10.0848 | 10.9408 | 11.7974
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 8.6202 | 8.831 | 9.0489 | 9.2738 | 9.5051 | 9.7436 | 9.9881 | 10.2398 | 10.498 | 10.7621 | 11.034 | 12.3728 | 13.7129
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 8.8449 | 9.0779 | 9.319 | 9.5681 | 9.8242 | 10.0876 | 10.3591 | 10.6381 | 10.9245 | 11.2184 | 11.5189 | 13.0037 | 14.4895
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 9.3699 | 9.6408 | 9.9209 | 10.2093 | 10.5072 | 10.814 | 11.1295 | 11.4526 | 11.7846 | 12.1248 | 12.473 | 14.1927 | 15.9136
| INCHICORE | 38 | 1 | Conservative [MW] |  |  | 89.7942 | 90.1709 | 90.5555 | 90.9554 | 94.019 | 93.6787 | 93.9364 | 94.1962 | 94.4602 | 94.7311 | 95.0011 | 95.2757 | 95.5566 | 95.8392 | 96.1258 | 96.4184 | 97.8655 | 99.3136
|  |  |  | Best View [MW] |  |  | 89.7942 | 90.2137 | 90.6499 | 91.0954 | 94.2003 | 93.9106 | 94.207 | 94.5106 | 94.8166 | 95.1274 | 95.4428 | 95.7606 | 96.0875 | 96.4163 | 96.7564 | 97.0939 | 98.7882 | 100.4821
|  |  |  | Base Case [MW] |  |  | 89.7942 | 90.2608 | 90.7457 | 91.2464 | 94.401 | 94.1672 | 94.504 | 94.844 | 95.1869 | 95.5422 | 95.8999 | 96.2652 | 96.6372 | 97.0118 | 97.3931 | 97.7832 | 99.7101 | 101.6385
|  |  |  | Aggressive [MW] |  |  | 89.7942 | 90.4146 | 91.065 | 91.7442 | 95.0569 | 95.0159 | 95.3347 | 95.6581 | 95.9836 | 96.3187 | 96.6576 | 96.9985 | 97.3461 | 97.7 | 98.0551 | 98.4142 | 100.1991 | 101.9847
|  |  | 2 | Conservative [MW] |  |  | 82.9908 | 83.533 | 84.083 | 84.6548 | 89.1163 | 89.3599 | 89.7236 | 90.1392 | 90.5155 | 90.9288 | 91.3396 | 91.7776 | 92.2076 | 92.6501 | 93.0988 | 93.5491 | 95.7964 | 98.0439
|  |  |  | Best View [MW] |  |  | 82.9908 | 83.6178 | 84.2714 | 84.9412 | 89.3363 | 89.6867 | 90.1331 | 90.5896 | 91.0417 | 91.5011 | 91.9807 | 92.4719 | 92.9691 | 93.4778 | 93.9887 | 94.5157 | 97.1079 | 99.7028
|  |  |  | Base Case [MW] |  |  | 82.9908 | 83.7155 | 84.4768 | 85.2793 | 89.6737 | 90.1235 | 90.6003 | 91.101 | 91.6066 | 92.1199 | 92.6525 | 93.1969 | 93.7581 | 94.326 | 94.9055 | 95.4882 | 98.3931 | 101.2985
|  |  |  | Aggressive [MW] |  |  | 82.9908 | 84.2304 | 85.5616 | 87.0192 | 91.3417 | 92.2662 | 92.7779 | 93.3009 | 93.8307 | 94.3722 | 94.9206 | 95.4843 | 96.0548 | 96.632 | 97.2267 | 97.8236 | 100.8023 | 103.7814
| KILBARRY | 38 | 1 | Conservative [MW] |  |  | 77.7185 | 78.0042 | 78.2955 | 76.4937 | 76.8272 | 77.165 | 76.919 | 71.5597 | 71.2109 | 71.459 | 71.7111 | 71.9683 | 72.2347 | 72.5017 | 72.779 | 73.0577 | 74.4473 | 75.8372
|  |  |  | Best View [MW] |  |  | 77.7185 | 78.027 | 78.342 | 76.5482 | 76.902 | 77.2616 | 77.1358 | 71.7927 | 71.5382 | 71.8792 | 72.2325 | 72.5957 | 72.9696 | 73.3509 | 73.7447 | 74.1475 | 76.1376 | 78.1291
|  |  |  | Base Case [MW] |  |  | 77.7185 | 78.1409 | 78.5752 | 76.9367 | 77.4308 | 77.9413 | 77.8342 | 72.2894 | 72.0461 | 72.4076 | 72.7735 | 73.1533 | 73.5425 | 73.942 | 74.3526 | 74.7762 | 76.8596 | 78.9452
|  |  |  | Aggressive [MW] |  |  | 77.7185 | 78.2998 | 78.9037 | 77.3401 | 77.9818 | 78.6505 | 78.669 | 72.9683 | 72.8132 | 73.2642 | 73.7273 | 74.2063 | 74.6962 | 75.2068 | 75.7296 | 76.2707 | 78.9274 | 81.5872
| KILKENNY | 38 | 1 | Conservative [MW] |  |  | 33.3736 | 33.6188 | 33.8686 | 34.1218 | 34.2516 | 34.4016 | 34.7767 | 35.16 | 35.5517 | 35.9514 | 36.3586 | 36.7748 | 37.1987 | 37.6301 | 38.0714 | 38.5199 | 40.7431 | 42.9675
|  |  |  | Best View [MW] |  |  | 33.3736 | 33.6696 | 33.9715 | 34.2794 | 34.4641 | 34.6711 | 35.1794 | 35.7023 | 36.2391 | 36.7908 | 37.3563 | 37.9369 | 38.5317 | 39.1408 | 39.7645 | 40.4024 | 43.5542 | 46.7083
|  |  |  | Base Case [MW] |  |  | 33.3736 | 33.7249 | 34.0842 | 34.4523 | 34.6978 | 34.968 | 35.5783 | 36.2082 | 36.8574 | 37.5277 | 38.2182 | 38.9273 | 39.6574 | 40.4079 | 41.1765 | 41.9653 | 45.8557 | 49.7494
|  |  |  | Aggressive [MW] |  |  | 33.3736 | 33.9549 | 34.5584 | 35.1824 | 35.6967 | 36.2486 | 37.0418 | 37.8632 | 38.7155 | 39.5966 | 40.5073 | 41.4466 | 42.4129 | 43.4045 | 44.4229 | 45.4617 | 50.601 | 55.7438
| KILTEEL | 38 | 1 | Conservative [MW] |  |  | 21.1128 | 21.3951 | 21.7691 | 22.0632 | 22.362 | 61.9064 | 57.6043 | 57.7905 | 57.9802 | 58.1747 | 58.372 | 58.5735 | 58.7803 | 58.9904 | 59.2046 | 59.4231 | 60.5042 | 61.586
|  |  |  | Best View [MW] |  |  | 21.1128 | 21.4397 | 21.8606 | 22.2013 | 22.5506 | 62.1887 | 57.826 | 58.0486 | 58.2771 | 58.5115 | 58.7507 | 58.9963 | 59.2468 | 59.5032 | 59.7665 | 60.0341 | 61.3606 | 62.6878
|  |  |  | Base Case [MW] |  |  | 21.1128 | 21.4803 | 21.9442 | 22.33 | 22.724 | 62.4536 | 58.0289 | 58.2851 | 58.547 | 58.8169 | 59.0928 | 59.3763 | 59.6675 | 59.9657 | 60.2715 | 60.5851 | 62.1321 | 63.6805
|  |  |  | Aggressive [MW] |  |  | 21.1128 | 21.648 | 22.2885 | 22.8604 | 23.4476 | 63.5739 | 58.7756 | 59.0356 | 59.301 | 59.5733 | 59.8519 | 60.1379 | 60.4306 | 60.7294 | 61.0362 | 61.3484 | 62.8949 | 64.4423
| KNOCKEARAGH | 38 | 1 | Conservative [MW] |  |  | 24.9825 | 25.1403 | 25.2997 | 25.4595 | 25.6217 | 24.9783 | 25.219 | 25.4635 | 25.7112 | 25.9598 | 26.213 | 26.4655 | 26.7207 | 26.9766 | 27.2345 | 27.4939 | 28.7868 | 30.08
|  |  |  | Best View [MW] |  |  | 24.9825 | 25.1759 | 25.3691 | 25.5665 | 25.7655 | 25.1604 | 25.4971 | 25.8376 | 26.1845 | 26.5329 | 26.8849 | 27.2388 | 27.5943 | 27.951 | 28.3051 | 28.6574 | 30.4237 | 32.1897
|  |  |  | Base Case [MW] |  |  | 24.9825 | 25.256 | 25.5357 | 25.8187 | 26.1055 | 25.5946 | 25.9375 | 26.2848 | 26.6347 | 26.9878 | 27.344 | 27.6998 | 28.0574 | 28.4114 | 28.7637 | 29.1095 | 30.8558 | 32.601
|  |  |  | Aggressive [MW] |  |  | 24.9825 | 25.3738 | 25.7744 | 26.1832 | 26.5994 | 26.2252 | 26.6329 | 27.0435 | 27.4573 | 27.8723 | 28.2864 | 28.6962 | 29.1005 | 29.4901 | 29.8641 | 30.2238 | 32.0602 | 33.8943
| LANESBOROUGH | 38 | 1 | Conservative [MW] |  |  | 16.7449 | 16.7857 | 16.8278 | 12.1406 | 12.1823 | 12.2244 | 12.3235 | 12.4252 | 12.5292 | 12.6349 | 12.7434 | 12.8536 | 12.9668 | 13.082 | 13.1995 | 13.3194 | 13.9124 | 14.5058
|  |  |  | Best View [MW] |  |  | 16.7449 | 16.8265 | 16.9091 | 12.2624 | 12.3474 | 12.4335 | 12.5557 | 12.6816 | 12.8103 | 12.9422 | 13.0773 | 13.2156 | 13.3572 | 13.5019 | 13.6502 | 13.801 | 14.5481 | 15.2957
|  |  |  | Base Case [MW] |  |  | 16.7449 | 16.8405 | 16.9392 | 12.3075 | 12.4082 | 12.5112 | 12.6656 | 12.8251 | 12.9893 | 13.1585 | 13.3323 | 13.5114 | 13.6955 | 13.8842 | 14.078 | 14.2767 | 15.2569 | 16.238
|  |  |  | Aggressive [MW] |  |  | 16.7449 | 16.8987 | 17.0588 | 12.4892 | 12.6577 | 12.8316 | 13.0341 | 13.2437 | 13.461 | 13.6854 | 13.9169 | 14.1563 | 14.4021 | 14.6554 | 14.9148 | 15.1795 | 16.489 | 17.7994
| LETTERKENNY | 38 | 1 | Conservative [MW] |  |  | 26.0762 | 26.2169 | 26.3676 | 26.5225 | 26.6807 | 26.8341 | 27.2031 | 27.5782 | 27.9617 | 28.3522 | 28.7503 | 29.1539 | 29.5652 | 29.9833 | 30.4163 | 30.8649 | 33.0664 | 35.2705
|  |  |  | Best View [MW] |  |  | 26.0762 | 26.3989 | 26.7482 | 27.1047 | 27.4684 | 27.7989 | 28.341 | 28.897 | 29.4667 | 30.0501 | 30.6637 | 31.2965 | 31.9442 | 32.6117 | 33.2975 | 33.9991 | 37.4649 | 40.9334
|  |  |  | Base Case [MW] |  |  | 26.0762 | 26.4367 | 26.829 | 27.2287 | 27.6356 | 28.006 | 28.6483 | 29.3082 | 29.987 | 30.703 | 31.4453 | 32.2085 | 33.0028 | 33.8166 | 34.6502 | 35.4961 | 39.6926 | 43.8911
|  |  |  | Aggressive [MW] |  |  | 26.0762 | 26.6389 | 27.2426 | 27.8654 | 28.5067 | 29.0844 | 29.8599 | 30.6783 | 31.5342 | 32.4195 | 33.3413 | 34.291 | 35.2583 | 36.2512 | 37.2641 | 38.2992 | 43.4156 | 48.5356
| LIMERICK | 38 | 1 | Conservative [MW] |  |  | 89.3493 | 89.6378 | 89.9458 | 90.2402 | 90.5431 | 90.8472 | 81.3824 | 81.7988 | 82.2148 | 82.6427 | 83.0764 | 83.5157 | 83.9569 | 84.4073 | 84.8674 | 85.3352 | 87.6535 | 89.9731
|  |  |  | Best View [MW] |  |  | 89.3493 | 89.6471 | 89.9662 | 90.2722 | 90.58 | 90.8935 | 81.5852 | 82.1478 | 82.7229 | 83.3133 | 83.9085 | 84.5176 | 85.1416 | 85.7771 | 86.4223 | 87.0821 | 90.3421 | 93.6045
|  |  |  | Base Case [MW] |  |  | 89.3493 | 89.7565 | 90.1867 | 90.6052 | 91.0379 | 91.473 | 82.3726 | 83.0349 | 83.7141 | 84.4057 | 85.1178 | 85.8458 | 86.5865 | 87.3392 | 88.1029 | 88.8744 | 92.7111 | 96.5491
|  |  |  | Aggressive [MW] |  |  | 89.3493 | 90.0028 | 90.6866 | 91.3785 | 92.0881 | 92.809 | 84.078 | 84.8452 | 85.6279 | 86.4311 | 87.2475 | 88.074 | 88.9148 | 89.763 | 90.6171 | 91.4709 | 95.7405 | 100.0102
| LISDRUM | 38 | 1 | Conservative [MW] |  |  | 7.5299 | 7.6682 | 7.8083 | 7.9513 | 8.1045 | 8.256 | 6.4042 | 6.6159 | 6.8325 | 7.0533 | 7.2791 | 7.5095 | 7.7443 | 7.9845 | 8.2292 | 8.4783 | 9.712 | 10.9464
|  |  |  | Best View [MW] |  |  | 7.5299 | 7.7069 | 7.8884 | 8.0735 | 8.2711 | 8.4682 | 6.6991 | 6.9971 | 7.3034 | 7.618 | 7.9425 | 8.2751 | 8.6162 | 8.9667 | 9.3258 | 9.6933 | 11.5086 | 13.3252
|  |  |  | Base Case [MW] |  |  | 7.5299 | 7.7505 | 7.9777 | 8.2104 | 8.4576 | 8.7071 | 6.9765 | 7.3126 | 7.6588 | 8.0161 | 8.3836 | 8.7622 | 9.1513 | 9.5506 | 9.9604 | 10.3792 | 12.4493 | 14.521
|  |  |  | Aggressive [MW] |  |  | 7.5299 | 7.8729 | 8.2301 | 8.6011 | 8.9976 | 9.4033 | 7.7703 | 8.2048 | 8.655 | 9.12 | 9.6004 | 10.0955 | 10.604 | 11.1256 | 11.6618 | 12.21 | 14.9191 | 17.6302
| LISHEEN | 38 | 1 | Conservative [MW] |  |  | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395
|  |  |  | Best View [MW] |  |  | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395
|  |  |  | Base Case [MW] |  |  | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395
|  |  |  | Aggressive [MW] |  |  | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395 | 21.2395
| MACROOM | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| MALLOW | 38 | 1 | Conservative [MW] |  |  | 27.8855 | 28.0301 | 28.1773 | 28.3281 | 28.4817 | 28.639 | 28.797 | 28.9589 | 29.1231 | 29.2921 | 29.4633 | 29.6392 | 29.819 | 30.0019 | 30.1878 | 30.3771 | 31.3147 | 32.2528
|  |  |  | Best View [MW] |  |  | 27.8855 | 28.0376 | 28.1935 | 28.3532 | 28.5168 | 28.6827 | 28.897 | 29.1173 | 29.345 | 29.5768 | 29.8162 | 30.0619 | 30.3147 | 30.5739 | 30.8396 | 31.1127 | 32.4584 | 33.8054
|  |  |  | Base Case [MW] |  |  | 27.8855 | 28.0935 | 28.3079 | 28.5286 | 28.7566 | 28.9923 | 29.2176 | 29.4491 | 29.6862 | 29.9317 | 30.1823 | 30.4394 | 30.705 | 30.9762 | 31.2565 | 31.5422 | 32.9562 | 34.3711
|  |  |  | Aggressive [MW] |  |  | 27.8855 | 28.1743 | 28.4748 | 28.7898 | 29.1173 | 29.4575 | 29.7018 | 29.9525 | 30.2116 | 30.4769 | 30.749 | 31.0281 | 31.3159 | 31.6103 | 31.9127 | 32.2209 | 33.7463 | 35.2726
| MARINA | 38 | 1 | Conservative [MW] |  |  | 0 | 89.6944 | 89.9969 | 90.3068 | 90.6241 | 90.9456 | 91.268 | 91.5946 | 91.928 | 92.2636 | 92.6083 | 92.9603 | 93.3141 | 93.6772 | 94.0417 | 94.4136 | 96.2532 | 98.0941
|  |  |  | Best View [MW] |  |  | 0 | 89.7104 | 90.0311 | 90.3601 | 90.6948 | 91.0359 | 91.4704 | 91.9177 | 92.3694 | 92.837 | 93.3132 | 93.7974 | 94.2972 | 94.8033 | 95.3208 | 95.8441 | 98.4451 | 101.047
|  |  |  | Base Case [MW] |  |  | 0 | 89.8284 | 90.2732 | 90.7272 | 91.2003 | 91.6798 | 92.1326 | 92.5936 | 93.0634 | 93.5453 | 94.0391 | 94.5427 | 95.0562 | 95.5775 | 96.11 | 96.6514 | 99.3344 | 102.019
|  |  |  | Aggressive [MW] |  |  | 0 | 89.9318 | 90.4872 | 91.0621 | 91.6567 | 92.2727 | 92.8639 | 93.4692 | 94.0922 | 94.7346 | 95.3904 | 96.063 | 96.7511 | 97.453 | 98.1633 | 98.8865 | 102.4682 | 106.052
| MCDERMOTT | 38 | 1 | Conservative [MW] |  |  | 84.3722 | 84.8981 | 85.4363 | 85.9986 | 86.5492 | 87.3305 | 87.7554 | 88.2004 | 88.6448 | 89.0821 | 89.5897 | 89.9091 | 90.2965 | 90.6321 | 90.9732 | 91.3349 | 93.0883 | 94.8452
|  |  |  | Best View [MW] |  |  | 84.3722 | 84.9631 | 85.57 | 86.2096 | 86.8471 | 87.716 | 88.2141 | 88.7177 | 89.2334 | 89.6819 | 90.112 | 90.5004 | 90.9218 | 91.3215 | 91.724 | 92.1504 | 94.2188 | 96.2911
|  |  |  | Base Case [MW] |  |  | 84.3722 | 85.0362 | 85.7216 | 86.4451 | 87.1696 | 88.1556 | 88.6969 | 89.3537 | 89.7991 | 90.2823 | 90.6813 | 91.118 | 91.5663 | 92.0389 | 92.5046 | 92.991 | 95.3678 | 97.748
|  |  |  | Aggressive [MW] |  |  | 84.3722 | 85.3034 | 86.2932 | 87.3403 | 88.4495 | 89.7702 | 90.1775 | 90.5876 | 90.9854 | 91.3775 | 91.7991 | 92.229 | 92.6664 | 93.1173 | 93.5655 | 94.0169 | 96.2655 | 98.5146
| MEATH HILL | 38 | 1 | Conservative [MW] |  |  | 18.8014 | 19.0017 | 19.2036 | 19.4083 | 19.6159 | 19.826 | 20.106 | 20.392 | 20.6816 | 20.9756 | 21.2737 | 21.5762 | 21.8824 | 22.1921 | 22.5038 | 22.8179 | 24.3822 | 25.9469
|  |  |  | Best View [MW] |  |  | 18.8014 | 19.0524 | 19.3074 | 19.5664 | 19.8298 | 20.0971 | 20.4859 | 20.8827 | 21.2888 | 21.7014 | 22.1199 | 22.5439 | 22.9715 | 23.4057 | 23.8423 | 24.2794 | 26.4635 | 28.6478
|  |  |  | Base Case [MW] |  |  | 18.8014 | 19.121 | 19.4467 | 19.7789 | 20.1187 | 20.4635 | 20.9015 | 21.3477 | 21.804 | 22.2668 | 22.7359 | 23.2113 | 23.6909 | 24.1736 | 24.6556 | 25.1362 | 27.543 | 29.9495
|  |  |  | Aggressive [MW] |  |  | 18.8014 | 19.2874 | 19.7871 | 20.3028 | 20.8316 | 21.3756 | 21.9223 | 22.4786 | 23.044 | 23.6168 | 24.1939 | 24.7697 | 25.3426 | 25.9075 | 26.4544 | 26.9766 | 29.6534 | 32.3261
| MIDLETON | 38 | 1 | Conservative [MW] |  |  | 16.9647 | 17.1139 | 17.2617 | 17.406 | 17.6943 | 73.9153 | 73.5507 | 73.9153 | 74.2903 | 74.6732 | 75.0647 | 75.4664 | 75.8784 | 76.3007 | 76.7322 | 77.1738 | 79.3547 | 81.5374
|  |  |  | Best View [MW] |  |  | 16.9647 | 17.1231 | 17.278 | 17.4293 | 17.7255 | 74.0164 | 73.7772 | 74.2758 | 74.7915 | 75.3242 | 75.8751 | 76.4408 | 77.0269 | 77.6333 | 78.2573 | 78.9009 | 82.0665 | 85.2355
|  |  |  | Base Case [MW] |  |  | 16.9647 | 17.1793 | 17.3876 | 17.5877 | 17.9313 | 74.7131 | 74.5022 | 75.03 | 75.5761 | 76.139 | 76.7203 | 77.3215 | 77.9407 | 78.5817 | 79.2424 | 79.9241 | 83.2765 | 86.6324
|  |  |  | Aggressive [MW] |  |  | 16.9647 | 17.2593 | 17.541 | 17.8031 | 18.2009 | 75.7745 | 75.611 | 76.1891 | 76.7878 | 77.4066 | 78.0443 | 78.7045 | 79.3851 | 80.0891 | 80.8186 | 81.5703 | 85.2698 | 88.973
| MILLTOWN (DR) | 38 | 1 | Conservative [MW] |  |  | 96.7425 | 97.2585 | 97.7817 | 98.3193 | 101.5565 | 95.259 | 93.0647 | 93.0409 | 93.4229 | 93.8093 | 94.1979 | 94.5972 | 95.0051 | 95.4185 | 95.8359 | 96.2638 | 98.3754 | 100.4887
|  |  |  | Best View [MW] |  |  | 96.7425 | 97.3416 | 97.9599 | 98.5867 | 101.9054 | 95.591 | 93.4601 | 93.4815 | 93.9098 | 94.3481 | 94.7933 | 95.25 | 95.7183 | 96.1885 | 96.6677 | 97.1601 | 99.5868 | 102.0158
|  |  |  | Base Case [MW] |  |  | 96.7425 | 97.4407 | 98.1529 | 98.8924 | 102.3015 | 95.9682 | 93.8688 | 93.9603 | 94.4353 | 94.9249 | 95.4221 | 95.9317 | 96.4533 | 96.9796 | 97.5154 | 98.0601 | 100.7597 | 103.4608
|  |  |  | Aggressive [MW] |  |  | 96.7425 | 97.9269 | 99.1617 | 100.4542 | 104.3746 | 97.9615 | 95.9195 | 96.0287 | 96.5241 | 97.0287 | 97.5397 | 98.0547 | 98.5824 | 99.1181 | 99.7194 | 100.1591 | 102.7886 | 105.3911
| MOY | 38 | 1 | Conservative [MW] |  |  | 31.31 | 31.376 | 31.4436 | 31.5108 | 31.5796 | 31.648 | 31.8724 | 32.1023 | 32.3383 | 32.5798 | 32.824 | 33.0748 | 33.3297 | 33.5887 | 33.853 | 34.1209 | 35.4509 | 36.7814
|  |  |  | Best View [MW] |  |  | 31.31 | 31.4602 | 31.6124 | 31.7648 | 31.9212 | 32.0811 | 32.3747 | 32.6785 | 32.9882 | 33.305 | 33.6304 | 33.9614 | 34.2999 | 34.647 | 34.9999 | 35.3592 | 37.1387 | 38.9193
|  |  |  | Base Case [MW] |  |  | 31.31 | 31.5108 | 31.7144 | 31.9242 | 32.1365 | 32.3533 | 32.7103 | 33.0761 | 33.453 | 33.8387 | 34.2358 | 34.6431 | 35.0595 | 35.4851 | 35.9184 | 36.3622 | 38.5533 | 40.7461
|  |  |  | Aggressive [MW] |  |  | 31.31 | 31.694 | 32.0948 | 32.5089 | 32.9377 | 33.3816 | 33.8912 | 34.4196 | 34.9629 | 35.5228 | 36.0997 | 36.6887 | 37.2888 | 37.895 | 38.5086 | 39.1231 | 42.1932 | 45.2635
| MULLINGAR | 38 | 1 | Conservative [MW] |  |  | 15.1087 | 15.2237 | 15.3392 | 15.4619 | 15.5796 | 54.8081 | 55.0726 | 55.3443 | 55.6267 | 55.9155 | 56.2161 | 56.5226 | 56.8397 | 57.1659 | 57.5014 | 57.8454 | 59.5428 | 61.2416
|  |  |  | Best View [MW] |  |  | 15.1087 | 15.2575 | 15.4071 | 15.5654 | 15.722 | 54.9984 | 55.3057 | 55.6251 | 55.9551 | 56.298 | 56.6509 | 57.0154 | 57.3929 | 57.7824 | 58.1839 | 58.6005 | 60.6432 | 62.6884
|  |  |  | Base Case [MW] |  |  | 15.1087 | 15.3949 | 15.688 | 16.0025 | 16.3214 | 55.8132 | 56.1606 | 56.5209 | 56.8922 | 57.2764 | 57.6744 | 58.0831 | 58.5112 | 58.9508 | 59.4052 | 59.8739 | 62.1792 | 64.4869
|  |  |  | Aggressive [MW] |  |  | 15.1087 | 15.5044 | 15.9194 | 16.3663 | 16.8258 | 56.5134 | 56.9388 | 57.379 | 57.8378 | 58.313 | 58.8075 | 59.3214 | 59.8548 | 60.4081 | 60.9784 | 61.5731 | 64.4817 | 67.3944
| NAVAN | 38 | 1 | Conservative [MW] |  |  | 52.2036 | 52.4616 | 52.7237 | 52.9908 | 53.2614 | 52.7938 | 51.8854 | 51.5236 | 51.9768 | 52.4391 | 52.9123 | 53.3958 | 53.8917 | 54.3967 | 54.9121 | 55.4384 | 58.0409 | 60.6451
|  |  |  | Best View [MW] |  |  | 52.2036 | 52.5181 | 52.8379 | 53.1646 | 53.4989 | 53.0964 | 52.2846 | 52.0254 | 52.5844 | 53.1571 | 53.7453 | 54.3491 | 54.9684 | 55.601 | 56.254 | 56.9174 | 60.2067 | 63.4977
|  |  |  | Base Case [MW] |  |  | 52.2036 | 52.7022 | 53.2169 | 53.7481 | 54.2944 | 54.1175 | 53.4064 | 53.2493 | 53.91 | 54.589 | 55.2874 | 56.0046 | 56.744 | 57.4812 | 58.231 | 58.9994 | 62.7916 | 66.5869
|  |  |  | Aggressive [MW] |  |  | 52.2036 | 52.8868 | 53.5987 | 54.3417 | 55.1147 | 55.1791 | 54.6516 | 54.6847 | 55.5411 | 56.4287 | 57.3283 | 58.2407 | 59.1848 | 60.1693 | 61.1718 | 62.187 | 67.2293 | 72.2737
| NENAGH | 38 | 1 | Conservative [MW] |  |  | 13.18 | 13.27 | 13.0276 | 13.1172 | 13.2064 | 13.2949 | 13.4173 | 13.5382 | 13.6553 | 13.7665 | 13.8738 | 13.9751 | 14.0702 | 14.1587 | 14.2398 | 14.3166 | 14.7119 | 15.1065
|  |  |  | Best View [MW] |  |  | 13.18 | 13.2915 | 13.07 | 13.1799 | 13.2898 | 13.3977 | 13.571 | 13.7356 | 13.8892 | 14.0324 | 14.1617 | 14.276 | 14.3772 | 14.4562 | 14.5063 | 14.5218 | 14.6916 | 14.8556
|  |  |  | Base Case [MW] |  |  | 13.18 | 13.3297 | 13.1464 | 13.2941 | 13.4394 | 13.5827 | 13.7564 | 13.9189 | 14.0688 | 14.201 | 14.3202 | 14.418 | 14.4865 | 14.521 | 14.5053 | 14.4222 | 14.1866 | 13.9397
|  |  |  | Aggressive [MW] |  |  | 13.18 | 13.4151 | 13.3138 | 13.5405 | 13.7539 | 13.9493 | 14.1086 | 14.2473 | 14.3694 | 14.4602 | 14.5133 | 14.5149 | 14.4467 | 14.2637 | 14.0054 | 13.6 | 11.9651 | 10.3057
| NEWBRIDGE | 38 | 1 | Conservative [MW] |  |  | 21.76 | 21.9565 | 22.1541 | 22.3553 | 22.5585 | 18.7254 | 18.9479 | 19.1742 | 19.4049 | 19.6397 | 19.8778 | 20.1195 | 20.3669 | 20.6168 | 20.8696 | 21.1271 | 22.402 | 23.6776
|  |  |  | Best View [MW] |  |  | 21.76 | 22.0082 | 22.2592 | 22.5153 | 22.7773 | 18.9565 | 19.251 | 19.552 | 19.8586 | 20.1728 | 20.4933 | 20.8193 | 21.1522 | 21.4899 | 21.8345 | 22.1823 | 23.9127 | 25.6436
|  |  |  | Base Case [MW] |  |  | 21.76 | 22.0548 | 22.3553 | 22.6628 | 22.9769 | 19.1705 | 19.5165 | 19.872 | 20.236 | 20.6086 | 20.9898 | 21.379 | 21.7747 | 22.1783 | 22.5861 | 23.0017 | 25.0587 | 27.1171
|  |  |  | Aggressive [MW] |  |  | 21.76 | 22.1392 | 22.5278 | 22.9295 | 23.3386 | 19.5591 | 19.9848 | 20.4231 | 20.8743 | 21.3351 | 21.8073 | 22.2885 | 22.7789 | 23.2743 | 23.7773 | 24.2776 | 26.7863 | 29.2946
| NEWBRIDGE EAST | 38 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 79.7615 | 84.5938 | 84.7658 | 84.9456 | 85.126 | 85.3093 | 85.4968 | 85.6906 | 85.8873 | 86.0867 | 86.2925 | 87.3044 | 88.3173
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 79.8277 | 84.8089 | 85.0233 | 85.2464 | 85.4756 | 85.7086 | 85.9476 | 86.1925 | 86.4469 | 86.7058 | 86.9679 | 88.2699 | 89.5724
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 79.8892 | 85.0042 | 85.2554 | 85.5137 | 85.779 | 86.0546 | 86.3382 | 86.6284 | 86.925 | 87.2327 | 87.5513 | 89.1151 | 90.6808
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 80.0016 | 85.5842 | 85.8604 | 86.1456 | 86.4446 | 86.7499 | 87.0637 | 87.3895 | 87.7223 | 88.069 | 88.4232 | 90.1743 | 91.9266
| OUGHTRAGH | 38 | 1 | Conservative [MW] |  |  | 9.0487 | 9.1455 | 9.2444 | 9.3438 | 9.4441 | 9.1284 | 9.2876 | 9.4492 | 9.612 | 9.7764 | 9.9415 | 10.1079 | 10.2751 | 10.4424 | 10.6102 | 10.7773 | 11.6148 | 12.4521
|  |  |  | Best View [MW] |  |  | 9.0487 | 9.1805 | 9.3153 | 9.4515 | 9.5889 | 9.3112 | 9.5294 | 9.7502 | 9.9728 | 10.1977 | 10.4232 | 10.649 | 10.8745 | 11.0988 | 11.3206 | 11.5374 | 12.6348 | 13.7313
|  |  |  | Base Case [MW] |  |  | 9.0487 | 9.2238 | 9.403 | 9.5847 | 9.7689 | 9.5399 | 9.7657 | 9.9931 | 10.2231 | 10.4542 | 10.6849 | 10.9148 | 11.1437 | 11.3696 | 11.5886 | 11.803 | 12.8872 | 13.9707
|  |  |  | Aggressive [MW] |  |  | 9.0487 | 9.3059 | 9.5701 | 9.8393 | 10.1131 | 9.9759 | 10.2466 | 10.5188 | 10.7903 | 11.0611 | 11.3282 | 11.5884 | 11.839 | 12.0787 | 12.3003 | 12.493 | 13.5335 | 14.5691
| PORTLAOISE | 38 | 1 | Conservative [MW] |  |  | 35.5608 | 35.8021 | 36.0476 | 36.6165 | 36.0457 | 35.961 | 32.3436 | 32.646 | 32.9452 | 33.2522 | 33.5648 | 33.8861 | 34.2139 | 34.5488 | 34.8884 | 35.235 | 36.9494 | 38.665
|  |  |  | Best View [MW] |  |  | 35.5608 | 35.8566 | 36.1609 | 36.7916 | 36.2821 | 36.2638 | 32.6633 | 33.056 | 33.4494 | 33.8546 | 34.2715 | 34.6993 | 35.134 | 35.5843 | 36.0474 | 36.5238 | 38.8702 | 41.2188
|  |  |  | Base Case [MW] |  |  | 35.5608 | 35.9266 | 36.3034 | 37.012 | 36.5837 | 36.6493 | 33.0216 | 33.4954 | 33.9731 | 34.4671 | 34.9732 | 35.4961 | 36.0376 | 36.5978 | 37.1749 | 37.769 | 40.6939 | 43.6217
|  |  |  | Aggressive [MW] |  |  | 35.5608 | 36.134 | 36.7312 | 37.6801 | 37.5034 | 37.8351 | 34.0943 | 34.745 | 35.4079 | 36.0972 | 36.8176 | 37.5658 | 38.343 | 39.1482 | 39.9835 | 40.852 | 45.1062 | 49.3658
| RATHKEALE | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| REAMORE | 38 | 1 | Conservative [MW] |  |  | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692
|  |  |  | Best View [MW] |  |  | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692
|  |  |  | Base Case [MW] |  |  | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692
|  |  |  | Aggressive [MW] |  |  | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692 | 17.8692
|  |  | 2 | Conservative [MW] |  |  | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636
|  |  |  | Best View [MW] |  |  | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636
|  |  |  | Base Case [MW] |  |  | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636
|  |  |  | Aggressive [MW] |  |  | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636 | 16.0636
| RICHMOND | 38 | 1 | Conservative [MW] |  |  | 28.2341 | 28.3354 | 28.4389 | 28.5419 | 28.646 | 28.7507 | 28.998 | 29.2493 | 29.5057 | 29.7669 | 30.0327 | 30.3028 | 30.5785 | 30.8575 | 31.1408 | 31.4261 | 32.8474 | 34.269
|  |  |  | Best View [MW] |  |  | 28.2341 | 28.435 | 28.638 | 28.8465 | 29.0571 | 29.2712 | 29.5723 | 29.8826 | 30.1971 | 30.5183 | 30.8451 | 31.179 | 31.5171 | 31.8604 | 32.2077 | 32.5594 | 34.3062 | 36.0537
|  |  |  | Base Case [MW] |  |  | 28.2341 | 28.47 | 28.712 | 28.957 | 29.2074 | 29.4632 | 29.8429 | 30.2339 | 30.6322 | 31.0409 | 31.4573 | 31.883 | 32.3138 | 32.7529 | 33.1941 | 33.6407 | 35.8592 | 38.0786
|  |  |  | Aggressive [MW] |  |  | 28.2341 | 28.6136 | 29.0044 | 29.4091 | 29.823 | 30.2495 | 30.7407 | 31.2468 | 31.7624 | 32.2914 | 32.8274 | 33.372 | 33.918 | 34.4662 | 35.0097 | 35.5436 | 38.2386 | 40.9321
| RINAWADE | 38 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 67.1119 | 67.2539 | 67.3984 | 67.5454 | 67.6962 | 67.8493 | 68.0034 | 68.1625 | 68.3223 | 68.4874 | 68.6535 | 69.4812 | 70.3091
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 67.2406 | 67.4054 | 67.5756 | 67.7477 | 67.9237 | 68.1027 | 68.2873 | 68.4734 | 68.6645 | 68.8582 | 69.0568 | 70.0367 | 71.0175
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 67.3779 | 67.5667 | 67.7609 | 67.959 | 68.1625 | 68.3693 | 68.5817 | 68.7981 | 69.0194 | 69.2449 | 69.4772 | 70.6207 | 71.7652
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 67.7333 | 67.9092 | 68.0886 | 68.2704 | 68.4564 | 68.6471 | 68.8399 | 69.0374 | 69.2394 | 69.4453 | 69.6562 | 70.6975 | 71.7396
| RINGSEND | 38 | 1 | Conservative [MW] |  |  | 93.8287 | 94.1653 | 94.4996 | 94.8518 | 95.2075 | 95.3677 | 95.6962 | 96.0363 | 96.3235 | 96.7751 | 97.1297 | 97.4876 | 97.8541 | 98.2267 | 98.6052 | 98.9942 | 100.9112 | 102.8299
|  |  |  | Best View [MW] |  |  | 93.8287 | 94.216 | 94.6138 | 95.0277 | 95.4466 | 95.6724 | 96.046 | 96.3992 | 96.8657 | 97.2617 | 97.6619 | 98.0795 | 98.4961 | 98.9241 | 99.3698 | 99.8297 | 102.0912 | 104.355
|  |  |  | Base Case [MW] |  |  | 93.8287 | 94.2839 | 94.7425 | 95.2246 | 95.722 | 96.026 | 96.3801 | 96.9074 | 97.3425 | 97.7821 | 98.2321 | 98.6922 | 99.1709 | 99.6613 | 100.1659 | 100.6748 | 103.2077 | 105.7413
|  |  |  | Aggressive [MW] |  |  | 93.8287 | 94.5922 | 95.4025 | 96.2567 | 97.1574 | 97.9173 | 98.3391 | 98.7755 | 99.2319 | 99.7049 | 100.1817 | 100.6725 | 101.164 | 101.6692 | 102.1877 | 102.6076 | 104.97 | 107.316
| SALTHILL | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.053647 | 0.17327 | 0.29557 | 0.42117 | 0.54885 | 1.1817 | 1.8149
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.11842 | 0.28932 | 0.46496 | 0.64662 | 0.83376 | 1.027 | 1.2253 | 2.2034 | 3.1822
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.1446 | 0.33179 | 0.52567 | 0.72632 | 0.93317 | 1.147 | 1.3678 | 1.5957 | 2.7163 | 3.8381
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.20071 | 0.41804 | 0.64411 | 0.8784 | 1.1211 | 1.3735 | 1.6357 | 1.9118 | 2.1981 | 2.495 | 3.9512 | 5.4092
| SCREEB | 38 | 1 | Conservative [MW] |  |  | 22.6847 | 22.7663 | 22.8469 | 22.9315 | 23.0148 | 23.1005 | 23.2178 | 23.3363 | 23.4594 | 23.5834 | 23.7093 | 23.8371 | 23.9668 | 24.0998 | 24.2338 | 24.3721 | 25.0521 | 25.7329
|  |  |  | Best View [MW] |  |  | 22.6847 | 22.7867 | 22.8897 | 22.9948 | 23.1023 | 23.2114 | 23.3787 | 23.5512 | 23.7269 | 23.9079 | 24.093 | 24.2821 | 24.4763 | 24.6728 | 24.8738 | 25.0777 | 26.0894 | 27.1016
|  |  |  | Base Case [MW] |  |  | 22.6847 | 22.8141 | 22.9454 | 23.081 | 23.2175 | 23.3584 | 23.5464 | 23.7381 | 23.9365 | 24.1397 | 24.3473 | 24.56 | 24.7764 | 24.998 | 25.2205 | 25.4492 | 26.5763 | 27.7044
|  |  |  | Aggressive [MW] |  |  | 22.6847 | 22.8869 | 23.0969 | 23.3124 | 23.5375 | 23.7703 | 23.9973 | 24.232 | 24.4721 | 24.7185 | 24.971 | 25.2261 | 25.4882 | 25.7549 | 26.0232 | 26.2926 | 27.6367 | 28.9809
| SHANKILL | 38 | 1 | Conservative [MW] |  |  | 49.2681 | 49.5201 | 49.7785 | 44.2983 | 44.5594 | 43.833 | 43.4758 | 43.1777 | 43.5854 | 44.0228 | 45.1893 | 45.6183 | 46.0555 | 46.5007 | 46.955 | 47.417 | 49.7065 | 51.9972
|  |  |  | Best View [MW] |  |  | 49.2681 | 49.6078 | 49.9576 | 44.5671 | 44.9242 | 44.2677 | 43.3887 | 43.9294 | 45.2643 | 45.8404 | 46.4302 | 47.0369 | 47.6553 | 48.2882 | 48.9319 | 49.5868 | 52.8314 | 56.078
|  |  |  | Base Case [MW] |  |  | 49.2681 | 49.6891 | 50.1215 | 44.8169 | 45.2607 | 44.0025 | 43.8872 | 45.2869 | 45.9317 | 46.5926 | 47.2733 | 47.9707 | 48.6824 | 49.4096 | 50.146 | 50.8917 | 54.5953 | 58.3004
|  |  |  | Aggressive [MW] |  |  | 49.2681 | 49.9247 | 50.6085 | 45.5525 | 46.0946 | 46.0653 | 46.1334 | 46.9407 | 47.7726 | 48.6285 | 49.5062 | 50.3947 | 51.2992 | 52.2023 | 53.1097 | 54.0207 | 58.5662 | 63.1123
| SLIGO | 38 | 1 | Conservative [MW] |  |  | 66.0837 | 66.2707 | 66.4572 | 66.6482 | 66.8393 | 67.0349 | 67.4075 | 67.7883 | 68.1758 | 68.571 | 68.9738 | 69.3811 | 69.7994 | 70.2214 | 70.653 | 71.0918 | 73.2666 | 75.4426
|  |  |  | Best View [MW] |  |  | 66.0837 | 66.4012 | 66.7256 | 67.0564 | 67.391 | 67.7325 | 68.2441 | 68.7696 | 69.3083 | 69.8581 | 70.4202 | 70.9958 | 71.5832 | 72.1801 | 72.7909 | 73.4083 | 76.4775 | 79.5479
|  |  |  | Base Case [MW] |  |  | 66.0837 | 66.5036 | 66.9348 | 67.3752 | 67.824 | 68.2854 | 68.9044 | 69.5396 | 70.194 | 70.8646 | 71.552 | 72.2556 | 72.9742 | 73.7025 | 74.4469 | 75.1984 | 78.9371 | 82.677
|  |  |  | Aggressive [MW] |  |  | 66.0837 | 66.7341 | 67.4061 | 68.1013 | 68.822 | 69.5672 | 70.4012 | 71.2655 | 72.155 | 73.0666 | 73.9983 | 74.9524 | 75.9079 | 76.8833 | 77.8681 | 78.8506 | 83.7693 | 88.6875
| SOMERSET | 38 | 1 | Conservative [MW] |  |  | 12.4561 | 12.5248 | 12.5941 | 12.6644 | 12.7355 | 20.1764 | 20.2356 | 20.2971 | 20.359 | 20.423 | 20.4885 | 20.5551 | 20.6228 | 20.6928 | 20.7639 | 20.8361 | 21.194 | 21.5521
|  |  |  | Best View [MW] |  |  | 12.4561 | 12.5587 | 12.6634 | 12.7694 | 12.8773 | 20.2592 | 20.3468 | 20.4369 | 20.5295 | 20.6246 | 20.724 | 20.8257 | 20.9304 | 21.0382 | 21.1499 | 21.2642 | 21.829 | 22.3942
|  |  |  | Base Case [MW] |  |  | 12.4561 | 12.5999 | 12.7477 | 12.8987 | 13.0534 | 20.3709 | 20.4684 | 20.5699 | 20.6736 | 20.7813 | 20.8931 | 21.0074 | 21.1264 | 21.2488 | 21.3756 | 21.5064 | 22.1498 | 22.7939
|  |  |  | Aggressive [MW] |  |  | 12.4561 | 12.6778 | 12.9078 | 13.1459 | 13.393 | 20.5999 | 20.7153 | 20.8351 | 20.9593 | 21.0888 | 21.2224 | 21.3595 | 21.5021 | 21.6503 | 21.8033 | 21.9609 | 22.7368 | 23.5134
| STRATFORD | 38 | 1 | Conservative [MW] |  |  | 23.5544 | 23.627 | 23.7022 | 23.7762 | 23.8532 | 23.9305 | 24.0402 | 24.1512 | 24.2649 | 24.3814 | 24.498 | 24.6189 | 24.7415 | 24.8678 | 24.9948 | 25.1228 | 25.76 | 26.3973
|  |  |  | Best View [MW] |  |  | 23.5544 | 23.6436 | 23.7359 | 23.8276 | 23.9223 | 24.0179 | 24.1598 | 24.3041 | 24.4525 | 24.6064 | 24.7607 | 24.9218 | 25.0838 | 25.251 | 25.4194 | 25.5934 | 26.4485 | 27.3045
|  |  |  | Base Case [MW] |  |  | 23.5544 | 23.6638 | 23.7761 | 23.8893 | 24.0066 | 24.1263 | 24.2956 | 24.4706 | 24.6499 | 24.8348 | 25.0242 | 25.2191 | 25.4178 | 25.6233 | 25.8295 | 26.0437 | 27.0932 | 28.144
|  |  |  | Aggressive [MW] |  |  | 23.5544 | 23.7272 | 23.9066 | 24.091 | 24.282 | 24.4795 | 24.7112 | 24.9522 | 25.2018 | 25.4572 | 25.7217 | 25.9915 | 26.2698 | 26.5519 | 26.8387 | 27.1267 | 28.5636 | 30.0006
| TAWNAGHMORE | 38 | 1 | Conservative [MW] |  |  | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766
|  |  |  | Best View [MW] |  |  | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766
|  |  |  | Base Case [MW] |  |  | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766
|  |  |  | Aggressive [MW] |  |  | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766 | 11.4766
| THORNSBERRY | 38 | 1 | Conservative [MW] |  |  | 57.1515 | 57.3457 | 57.5437 | 57.7455 | 57.952 | 58.1618 | 58.4324 | 58.7087 | 58.9928 | 59.2825 | 59.5793 | 59.8828 | 60.1935 | 60.5115 | 60.8365 | 61.1679 | 62.8077 | 64.4487
|  |  |  | Best View [MW] |  |  | 57.1515 | 57.3977 | 57.65 | 57.9079 | 58.1725 | 58.4424 | 58.8032 | 59.1737 | 59.5556 | 59.9491 | 60.3542 | 60.7709 | 61.2 | 61.6412 | 62.0953 | 62.5611 | 64.8589 | 67.1587
|  |  |  | Base Case [MW] |  |  | 57.1515 | 57.4442 | 57.7462 | 58.0566 | 58.376 | 58.7037 | 59.1306 | 59.5722 | 60.0285 | 60.5012 | 60.9906 | 61.4953 | 62.0165 | 62.5543 | 63.1096 | 63.6818 | 66.4978 | 69.3167
|  |  |  | Aggressive [MW] |  |  | 57.1515 | 57.5293 | 57.9202 | 58.3269 | 58.7475 | 59.1841 | 59.7137 | 60.2667 | 60.8411 | 61.4381 | 62.0595 | 62.7044 | 63.3729 | 64.0667 | 64.7851 | 65.5261 | 69.171 | 72.8196
| THURLES | 38 | 1 | Conservative [MW] |  |  | 2.247 | 2.371 | 2.9902 | 3.1036 | 3.2198 | 3.3369 | 3.1656 | 3.3268 | 3.4916 | 3.6597 | 3.8316 | 4.0067 | 4.1858 | 4.3683 | 4.5544 | 4.7441 | 5.6831 | 6.6226
|  |  |  | Best View [MW] |  |  | 2.247 | 2.3943 | 3.0377 | 3.1767 | 3.3185 | 3.4632 | 3.3634 | 3.6016 | 3.8466 | 4.099 | 4.3592 | 4.6269 | 4.902 | 5.1838 | 5.474 | 5.7757 | 7.2534 | 8.733
|  |  |  | Base Case [MW] |  |  | 2.247 | 2.4401 | 3.1303 | 3.3185 | 3.5117 | 3.7102 | 3.6319 | 3.8938 | 4.1643 | 4.4432 | 4.7308 | 5.0262 | 5.3306 | 5.6462 | 5.9726 | 6.3079 | 7.9605 | 9.6145
|  |  |  | Aggressive [MW] |  |  | 2.247 | 2.5431 | 3.3413 | 3.646 | 3.9613 | 4.2881 | 4.2427 | 4.5406 | 4.8474 | 5.1634 | 5.4895 | 5.8297 | 6.1806 | 6.5413 | 6.9125 | 7.2935 | 9.1721 | 11.0524
| TIPPERARY | 38 | 1 | Conservative [MW] |  |  | 19.4579 | 19.5532 | 19.6493 | 19.7469 | 19.8442 | 19.9431 | 20.0745 | 20.2067 | 20.3401 | 20.4738 | 20.6095 | 20.7441 | 20.8788 | 21.0143 | 21.1484 | 21.2813 | 21.9489 | 22.6163
|  |  |  | Best View [MW] |  |  | 19.4579 | 19.5734 | 19.6906 | 19.8087 | 19.9265 | 20.0462 | 20.2368 | 20.4276 | 20.6209 | 20.8145 | 21.0073 | 21.199 | 21.3895 | 21.5748 | 21.7566 | 21.9305 | 22.8212 | 23.7106
|  |  |  | Base Case [MW] |  |  | 19.4579 | 19.6129 | 19.7694 | 19.9274 | 20.087 | 20.2476 | 20.4526 | 20.6568 | 20.8637 | 21.0689 | 21.2726 | 21.4725 | 21.6678 | 21.8566 | 22.0359 | 22.2072 | 23.0851 | 23.9616
|  |  |  | Aggressive [MW] |  |  | 19.4579 | 19.7001 | 19.946 | 20.1956 | 20.4493 | 20.7049 | 20.922 | 21.1384 | 21.3525 | 21.5617 | 21.766 | 21.9605 | 22.1447 | 22.3172 | 22.4729 | 22.6076 | 23.337 | 24.0628
| TONROE | 38 | 1 | Conservative [MW] |  |  | 8.9327 | 8.9828 | 9.033 | 9.084 | 9.1351 | 24.9896 | 25.1168 | 25.2479 | 25.3818 | 25.5186 | 25.6586 | 25.8022 | 25.9488 | 26.0991 | 26.2528 | 26.4101 | 27.1869 | 27.9643
|  |  |  | Best View [MW] |  |  | 8.9327 | 9.0244 | 9.1181 | 9.213 | 9.3094 | 25.2308 | 25.4048 | 25.5833 | 25.7678 | 25.9576 | 26.1535 | 26.355 | 26.5628 | 26.7755 | 26.996 | 27.2214 | 28.3352 | 29.4498
|  |  |  | Base Case [MW] |  |  | 8.9327 | 9.0546 | 9.1791 | 9.3065 | 9.4362 | 25.4094 | 25.6198 | 25.8388 | 26.065 | 26.2999 | 26.5419 | 26.7936 | 27.0523 | 27.3209 | 27.5975 | 27.8839 | 29.2897 | 30.6972
|  |  |  | Aggressive [MW] |  |  | 8.9327 | 9.1344 | 9.3436 | 9.5598 | 9.7843 | 25.9067 | 26.2023 | 26.5127 | 26.8358 | 27.1727 | 27.5258 | 27.8924 | 28.2738 | 28.6714 | 29.084 | 29.5124 | 31.6121 | 33.7144
| TRABEG | 38 | 1 | Conservative [MW] |  |  | 43.2683 | 31.4014 | 31.4691 | 31.5398 | 31.4741 | 70.9377 | 71.0095 | 71.0852 | 71.1621 | 71.2404 | 71.3216 | 71.4023 | 71.4858 | 71.5731 | 71.6609 | 71.7502 | 72.1927 | 72.6354
|  |  |  | Best View [MW] |  |  | 43.2683 | 31.4062 | 31.477 | 31.5508 | 31.4899 | 70.9579 | 71.0569 | 71.1589 | 71.2653 | 71.3745 | 71.4858 | 71.6023 | 71.7206 | 71.8433 | 71.971 | 72.1023 | 72.7492 | 73.3967
|  |  |  | Base Case [MW] |  |  | 43.2683 | 31.4314 | 31.5303 | 31.6338 | 31.6037 | 71.1039 | 71.2091 | 71.3166 | 71.4269 | 71.5423 | 71.6592 | 71.7811 | 71.9069 | 72.0353 | 72.1673 | 72.3034 | 72.9729 | 73.6432
|  |  |  | Aggressive [MW] |  |  | 43.2683 | 31.4691 | 31.6072 | 31.7524 | 31.7683 | 71.3216 | 71.4353 | 71.5515 | 71.672 | 71.7948 | 71.9238 | 72.0548 | 72.19 | 72.3317 | 72.4738 | 72.6222 | 73.3475 | 74.0739
| TRALEE | 38 | 1 | Conservative [MW] |  |  | 23.608 | 23.7558 | 23.9063 | 24.0579 | 24.2111 | 24.7138 | 25.0061 | 25.3057 | 25.6121 | 25.9241 | 26.2442 | 26.5701 | 26.904 | 27.244 | 27.5924 | 27.9479 | 29.7064 | 31.466
|  |  |  | Best View [MW] |  |  | 23.608 | 23.8704 | 24.1383 | 24.4111 | 24.6896 | 25.3229 | 25.716 | 26.1217 | 26.538 | 26.9667 | 27.4066 | 27.8583 | 28.3222 | 28.798 | 29.287 | 29.7877 | 32.2601 | 34.7344
|  |  |  | Base Case [MW] |  |  | 23.608 | 23.9025 | 24.2031 | 24.5108 | 24.8268 | 25.4959 | 25.9255 | 26.3669 | 26.8218 | 27.2893 | 27.7714 | 28.2676 | 28.7772 | 29.3009 | 29.8395 | 30.3931 | 33.121 | 35.8515
|  |  |  | Aggressive [MW] |  |  | 23.608 | 24.0688 | 24.546 | 25.0406 | 25.5531 | 26.432 | 26.9887 | 27.5647 | 28.162 | 28.7787 | 29.4177 | 30.0781 | 30.7599 | 31.4626 | 32.1796 | 32.9176 | 36.5516 | 40.1891
| TRIEN | 38 | 1 | Conservative [MW] |  |  | 1.0163 | 1.1106 | 1.2064 | 1.3042 | 1.4035 | 41.9616 | 42.1205 | 42.2833 | 42.4504 | 42.6207 | 42.7949 | 42.9727 | 43.1552 | 43.342 | 43.533 | 43.7283 | 44.6935 | 45.6594
|  |  |  | Best View [MW] |  |  | 1.0163 | 1.1467 | 1.2799 | 1.4161 | 1.5545 | 42.1714 | 42.3863 | 42.607 | 42.8342 | 43.0683 | 43.3096 | 43.5578 | 43.8127 | 44.0754 | 44.3461 | 44.6241 | 45.9946 | 47.3664
|  |  |  | Base Case [MW] |  |  | 1.0163 | 1.1729 | 1.3339 | 1.4981 | 1.6668 | 42.327 | 42.5685 | 42.8181 | 43.0751 | 43.342 | 43.6159 | 43.8991 | 44.191 | 44.4928 | 44.8046 | 45.1251 | 46.7044 | 48.2852
|  |  |  | Aggressive [MW] |  |  | 1.0163 | 1.2592 | 1.5111 | 1.7728 | 2.044 | 42.8592 | 43.1597 | 43.4728 | 43.7969 | 44.1324 | 44.4805 | 44.8414 | 45.2155 | 45.6049 | 46.0079 | 46.4266 | 48.4782 | 50.5324
|  |  | 2 | Conservative [MW] |  |  | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458
|  |  |  | Best View [MW] |  |  | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458
|  |  |  | Base Case [MW] |  |  | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458
|  |  |  | Aggressive [MW] |  |  | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458 | 16.4458
| TRILLICK | 38 | 1 | Conservative [MW] |  |  | 12.521 | 12.5648 | 12.6089 | 12.6535 | 12.6982 | 12.7432 | 12.8509 | 12.9599 | 13.0709 | 13.1841 | 13.2991 | 13.4165 | 13.5354 | 13.6567 | 13.7792 | 13.9044 | 14.5232 | 15.1425
|  |  |  | Best View [MW] |  |  | 12.521 | 12.6182 | 12.7168 | 12.8173 | 12.9199 | 13.0238 | 13.181 | 13.342 | 13.507 | 13.676 | 13.8485 | 14.0241 | 14.2041 | 14.3875 | 14.5741 | 14.7645 | 15.7064 | 16.649
|  |  |  | Base Case [MW] |  |  | 12.521 | 12.6295 | 12.7399 | 12.8523 | 12.967 | 13.0837 | 13.2697 | 13.4609 | 13.6574 | 13.8589 | 14.0661 | 14.2777 | 14.4937 | 14.7148 | 14.9396 | 15.1677 | 16.2994 | 17.4316
|  |  |  | Aggressive [MW] |  |  | 12.521 | 12.6862 | 12.8561 | 13.0312 | 13.2111 | 13.3961 | 13.6209 | 13.8522 | 14.0903 | 14.3354 | 14.5863 | 14.8428 | 15.1041 | 15.3694 | 15.6382 | 15.9105 | 17.2625 | 18.6152
|  |  | 2 | Conservative [MW] |  |  | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544
|  |  |  | Best View [MW] |  |  | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544
|  |  |  | Base Case [MW] |  |  | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544
|  |  |  | Aggressive [MW] |  |  | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544 | 0.97544
| TULLABRACK | 38 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| WALTERSTOWN | 38 | 0 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 88.6363 | 88.6363 | 94.3088 | 94.4696 | 94.6255 | 94.7908 | 94.9558 | 95.1267 | 95.3013 | 95.4799 | 95.6625 | 96.5647 | 97.4676
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 88.6363 | 88.6363 | 94.4962 | 94.679 | 94.8697 | 95.0621 | 95.2618 | 95.4656 | 95.6746 | 95.889 | 96.1088 | 97.1935 | 98.2792
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 88.6363 | 88.6363 | 94.6946 | 94.9028 | 95.1206 | 95.3542 | 95.5833 | 95.8217 | 96.067 | 96.3193 | 96.579 | 97.8579 | 99.138
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 88.6363 | 88.6363 | 95.8791 | 95.2481 | 95.448 | 95.6593 | 95.8688 | 96.0877 | 96.3122 | 96.5425 | 96.7787 | 97.9438 | 99.1099
| WATERFORD | 38 | 1 | Conservative [MW] |  |  | 68.2682 | 83.43 | 83.7219 | 84.0139 | 84.3148 | 84.6245 | 85.0159 | 85.413 | 85.8129 | 86.2222 | 86.637 | 87.0606 | 87.4863 | 87.9171 | 88.3549 | 88.7968 | 90.9953 | 93.1944
|  |  |  | Best View [MW] |  |  | 68.2682 | 83.4608 | 83.782 | 84.1072 | 84.4374 | 84.7837 | 85.2824 | 85.7901 | 86.3096 | 86.8403 | 87.3773 | 87.9232 | 88.4794 | 89.0434 | 89.6111 | 90.1857 | 93.0403 | 95.896
|  |  |  | Base Case [MW] |  |  | 68.2682 | 83.5162 | 83.8962 | 84.2813 | 84.6725 | 85.0831 | 85.6677 | 86.2636 | 86.8743 | 87.4948 | 88.128 | 88.7761 | 89.428 | 90.0914 | 90.7611 | 91.4341 | 94.7904 | 98.1472
|  |  |  | Aggressive [MW] |  |  | 68.2682 | 83.7348 | 84.3391 | 84.96 | 85.6008 | 86.2666 | 86.9962 | 87.7418 | 88.5077 | 89.2854 | 90.0771 | 90.8763 | 91.6823 | 92.4936 | 93.3022 | 94.0855 | 98.0693 | 102.049
| WEST PORTLAOISE | 38 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 42.8503 | 42.9457 | 43.0477 | 43.1537 | 43.2576 | 43.3648 | 43.4745 | 43.5908 | 43.7048 | 43.8252 | 44.4103 | 44.9964
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 42.9629 | 43.0973 | 43.2392 | 43.3829 | 43.5301 | 43.6863 | 43.845 | 44.0038 | 44.1716 | 44.3482 | 45.2077 | 46.0687
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 43.1008 | 43.2579 | 43.4225 | 43.5953 | 43.7708 | 43.9529 | 44.1399 | 44.3326 | 44.5381 | 44.7426 | 45.768 | 46.7931
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 43.4763 | 43.688 | 43.9033 | 44.1292 | 44.3657 | 44.6109 | 44.8663 | 45.1326 | 45.4104 | 45.6977 | 47.1087 | 48.5213
| WEXFORD | 38 | 1 | Conservative [MW] |  |  | 34.6474 | 34.8048 | 34.9628 | 35.1231 | 35.2847 | 34.6051 | 34.9904 | 35.3853 | 35.7871 | 36.1982 | 36.6173 | 37.0444 | 37.4811 | 37.9247 | 38.3712 | 38.8216 | 41.0631 | 43.3053
|  |  |  | Best View [MW] |  |  | 34.6474 | 34.9236 | 35.2042 | 35.4901 | 35.7806 | 35.2342 | 35.6681 | 36.111 | 36.5637 | 37.028 | 37.5013 | 37.9839 | 38.4686 | 38.9581 | 39.4549 | 39.9574 | 42.4548 | 44.9532
|  |  |  | Base Case [MW] |  |  | 34.6474 | 34.9869 | 35.3332 | 35.6867 | 36.0479 | 35.5741 | 36.0592 | 36.5552 | 37.0643 | 37.585 | 38.1172 | 38.6489 | 39.1893 | 39.7378 | 40.3017 | 40.8823 | 43.7408 | 46.6021
|  |  |  | Aggressive [MW] |  |  | 34.6474 | 35.1793 | 35.7283 | 36.2958 | 36.8818 | 36.642 | 37.3487 | 38.0784 | 38.8132 | 39.5643 | 40.3395 | 41.1422 | 41.9558 | 42.7794 | 43.6062 | 44.4247 | 48.5394 | 52.6527
| WILTON | 38 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 78.4467 | 78.4467 | 84.2134 | 84.3489 | 84.4864 | 84.6243 | 84.7696 | 84.9193 | 85.0709 | 85.223 | 85.3808 | 86.1545 | 86.9291
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 78.4467 | 78.4467 | 84.3443 | 84.5271 | 84.7208 | 84.9168 | 85.1221 | 85.3297 | 85.5451 | 85.7666 | 85.9967 | 87.1243 | 88.2534
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 78.4467 | 78.4467 | 84.6216 | 84.8157 | 85.0137 | 85.2234 | 85.4354 | 85.655 | 85.8809 | 86.1113 | 86.3518 | 87.5275 | 88.7048
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 78.4467 | 78.4467 | 84.9844 | 85.2459 | 85.5155 | 85.7981 | 86.0911 | 86.3953 | 86.7107 | 87.0342 | 87.3749 | 89.0324 | 90.6928
110 kV - MV | ADAMSTOWN | 20 | 1 | Conservative [MW] |  |  | 26.536 | 26.6818 | 26.8356 | 26.9937 | 27.1545 | 27.3178 | 27.4139 | 27.5132 | 27.6114 | 27.7129 | 27.818 | 27.9214 | 28.0274 | 28.1365 | 28.2443 | 28.3539 | 28.8972 | 29.4408
|  |  |  | Best View [MW] |  |  | 26.536 | 26.6965 | 26.8669 | 27.0424 | 27.2214 | 27.4084 | 27.5193 | 27.6317 | 27.7497 | 27.8654 | 27.986 | 28.1123 | 28.2349 | 28.3623 | 28.4903 | 28.6219 | 29.2702 | 29.9192
|  |  |  | Base Case [MW] |  |  | 26.536 | 26.7138 | 26.9023 | 27.0926 | 27.2907 | 27.5016 | 27.6266 | 27.7593 | 27.892 | 28.028 | 28.1671 | 28.3054 | 28.45 | 28.5968 | 28.7496 | 28.8996 | 29.6572 | 30.4143
|  |  |  | Aggressive [MW] |  |  | 26.536 | 26.7557 | 26.9854 | 27.2266 | 27.4781 | 27.7412 | 27.858 | 27.9756 | 28.0987 | 28.223 | 28.3517 | 28.4809 | 28.6099 | 28.7431 | 28.8799 | 29.0156 | 29.6971 | 30.3784
| AHANE | 10 | 1 | Conservative [MW] |  |  | 4.5831 | 4.6112 | 4.6401 | 4.6695 | 4.6994 | 4.73 | 4.7646 | 4.8 | 4.8362 | 4.8732 | 4.9109 | 4.9494 | 4.9888 | 5.0291 | 5.0704 | 5.1122 | 5.32 | 5.5278
|  |  |  | Best View [MW] |  |  | 4.5831 | 4.612 | 4.6414 | 4.6717 | 4.7024 | 4.7338 | 4.7807 | 4.8291 | 4.8791 | 4.9303 | 4.9831 | 5.0376 | 5.0936 | 5.1511 | 5.2103 | 5.2713 | 5.5715 | 5.8721
|  |  |  | Base Case [MW] |  |  | 4.5831 | 4.623 | 4.6637 | 4.706 | 4.7493 | 4.7939 | 4.8497 | 4.9079 | 4.9676 | 5.0297 | 5.0937 | 5.1598 | 5.2282 | 5.2986 | 5.3714 | 5.4466 | 5.8161 | 6.1861
|  |  |  | Aggressive [MW] |  |  | 4.5831 | 4.6477 | 4.7153 | 4.7859 | 4.8598 | 4.9368 | 5.0034 | 5.0721 | 5.1433 | 5.2174 | 5.2937 | 5.3729 | 5.455 | 5.5397 | 5.6272 | 5.718 | 6.1633 | 6.609
| ARIGNA | 20 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| ARKLOW | 10 | 1 | Conservative [MW] |  |  | 9.1933 | 9.2349 | 9.2771 | 9.3198 | 9.3637 | 9.4087 | 9.4671 | 9.5274 | 9.5889 | 9.652 | 9.7166 | 9.7829 | 9.8511 | 9.9206 | 9.9919 | 10.0651 | 10.4262 | 10.7875
|  |  |  | Best View [MW] |  |  | 9.1933 | 9.2452 | 9.2981 | 9.3527 | 9.4087 | 9.4658 | 9.545 | 9.6263 | 9.7104 | 9.7977 | 9.8875 | 9.9805 | 10.076 | 10.1745 | 10.2764 | 10.3816 | 10.8987 | 11.4163
|  |  |  | Base Case [MW] |  |  | 9.1933 | 9.2597 | 9.3278 | 9.3984 | 9.471 | 9.5459 | 9.6367 | 9.7303 | 9.8278 | 9.9288 | 10.0335 | 10.1414 | 10.2534 | 10.3696 | 10.4896 | 10.6139 | 11.2241 | 11.835
|  |  |  | Aggressive [MW] |  |  | 9.1933 | 9.2836 | 9.378 | 9.4761 | 9.5781 | 9.685 | 9.8124 | 9.9463 | 10.0862 | 10.2332 | 10.3866 | 10.5476 | 10.7158 | 10.8921 | 11.076 | 11.2687 | 12.2085 | 13.1498
| ARTANE | 10 | 1 | Conservative [MW] |  |  | 25.1562 | 25.257 | 25.3629 | 25.4697 | 25.5846 | 25.6998 | 25.7676 | 25.8372 | 25.9079 | 25.9795 | 26.052 | 26.1255 | 26.2003 | 26.2756 | 26.3553 | 26.4364 | 26.8381 | 27.2401
|  |  |  | Best View [MW] |  |  | 25.1562 | 25.267 | 25.3848 | 25.5061 | 25.6294 | 25.7631 | 25.839 | 25.9229 | 26.0032 | 26.0874 | 26.1715 | 26.2595 | 26.3509 | 26.4381 | 26.5332 | 26.627 | 27.0995 | 27.5718
|  |  |  | Base Case [MW] |  |  | 25.1562 | 25.2795 | 25.4083 | 25.5421 | 25.6804 | 25.827 | 25.9176 | 26.0076 | 26.1045 | 26.2003 | 26.2989 | 26.3999 | 26.5036 | 26.6091 | 26.7168 | 26.8299 | 27.3808 | 27.9326
|  |  |  | Aggressive [MW] |  |  | 25.1562 | 25.3065 | 25.4689 | 25.6347 | 25.8104 | 25.9952 | 26.0799 | 26.1646 | 26.2531 | 26.3415 | 26.4337 | 26.5252 | 26.6201 | 26.7142 | 26.8111 | 26.9112 | 27.4032 | 27.8958
| ATHY | 10 | 1 | Conservative [MW] |  |  | 25.4551 | 25.5518 | 25.6477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Best View [MW] |  |  | 25.4551 | 25.5714 | 25.6925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Base Case [MW] |  |  | 25.4551 | 25.5974 | 25.7461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Aggressive [MW] |  |  | 25.4551 | 25.6825 | 25.9166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 43.7698 | 43.8768 | 43.9873 | 43.3592 | 43.5185 | 43.6811 | 43.8463 | 44.0138 | 44.187 | 44.3655 | 44.5454 | 44.7265 | 44.9157 | 45.8403 | 46.7661
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 43.8428 | 43.9765 | 44.1117 | 43.531 | 43.7359 | 43.9493 | 44.1665 | 44.3911 | 44.6219 | 44.8551 | 45.0964 | 45.3458 | 45.5985 | 46.8532 | 48.1084
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 43.9303 | 44.0948 | 44.2644 | 43.7239 | 43.9763 | 44.2314 | 44.4987 | 44.7695 | 45.0539 | 45.3433 | 45.6395 | 45.9454 | 46.2591 | 47.8067 | 49.3555
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 44.2132 | 44.4837 | 44.7669 | 44.3197 | 44.6653 | 45.0249 | 45.3988 | 45.7849 | 46.1833 | 46.5943 | 47.0172 | 47.4515 | 47.896 | 50.0913 | 52.2883
| BALLYBEG | 10 | 1 | Conservative [MW] |  |  | 6.6799 | 6.7548 | 6.831 | 6.9081 | 6.9871 | 7.0678 | 7.1726 | 7.2805 | 7.3906 | 7.5036 | 7.6188 | 7.7368 | 7.8572 | 7.9804 | 8.1065 | 8.235 | 8.8711 | 9.5075
|  |  |  | Best View [MW] |  |  | 6.6799 | 6.7737 | 6.8695 | 6.9677 | 7.0678 | 7.1706 | 7.3119 | 7.458 | 7.608 | 7.7625 | 7.9221 | 8.0859 | 8.2548 | 8.4282 | 8.6066 | 8.7897 | 9.6925 | 10.5961
|  |  |  | Base Case [MW] |  |  | 6.6799 | 6.7997 | 6.9227 | 7.0497 | 7.1798 | 7.3136 | 7.476 | 7.6434 | 7.8163 | 7.9951 | 8.1798 | 8.37 | 8.5668 | 8.7689 | 8.9781 | 9.1932 | 10.253 | 11.3139
|  |  |  | Aggressive [MW] |  |  | 6.6799 | 6.8432 | 7.0126 | 7.1887 | 7.372 | 7.5622 | 7.7887 | 8.0256 | 8.2726 | 8.5303 | 8.7987 | 9.0781 | 9.3686 | 9.6707 | 9.9843 | 10.3095 | 11.9045 | 13.5015
| BALTRASNA | 20 | 1 | Conservative [MW] |  |  | 10.0431 | 10.2065 | 10.3752 | 10.5496 | 10.7294 | 10.9146 | 11.023 | 11.1316 | 11.2436 | 11.3567 | 11.4721 | 11.5896 | 11.7083 | 11.8304 | 11.9533 | 12.0783 | 12.6978 | 13.3177
|  |  |  | Best View [MW] |  |  | 10.0431 | 10.2231 | 10.4104 | 10.6046 | 10.8054 | 11.012 | 11.1374 | 11.2649 | 11.3961 | 11.5283 | 11.664 | 11.8026 | 11.9437 | 12.0866 | 12.2327 | 12.3807 | 13.1158 | 13.8512
|  |  |  | Base Case [MW] |  |  | 10.0431 | 10.2417 | 10.4479 | 10.6626 | 10.8849 | 11.1161 | 11.2593 | 11.4058 | 11.556 | 11.7083 | 11.8648 | 12.0236 | 12.1865 | 12.3523 | 12.5222 | 12.6951 | 13.5516 | 14.4086
|  |  |  | Aggressive [MW] |  |  | 10.0431 | 10.287 | 10.5427 | 10.8113 | 11.0918 | 11.3852 | 11.5182 | 11.6525 | 11.7902 | 11.93 | 12.0729 | 12.2191 | 12.3671 | 12.517 | 12.671 | 12.8265 | 13.6 | 14.3737
| BANOGE | 20 | 1 | Conservative [MW] |  |  | 22.2533 | 22.371 | 22.4908 | 22.6106 | 22.734 | 22.8572 | 23.019 | 23.1823 | 23.3496 | 23.5184 | 23.6902 | 23.8654 | 24.0407 | 24.2208 | 24.4007 | 24.5846 | 25.4933 | 26.4028
|  |  |  | Best View [MW] |  |  | 22.2533 | 22.4012 | 22.5498 | 22.7033 | 22.857 | 23.0151 | 23.2292 | 23.4502 | 23.675 | 23.9031 | 24.1361 | 24.3708 | 24.6111 | 24.854 | 25.0978 | 25.3471 | 26.579 | 27.8118
|  |  |  | Base Case [MW] |  |  | 22.2533 | 22.4412 | 22.6342 | 22.8293 | 23.0285 | 23.2339 | 23.4769 | 23.7259 | 23.9828 | 24.2415 | 24.5056 | 24.7742 | 25.0456 | 25.3184 | 25.5963 | 25.873 | 27.2596 | 28.6461
|  |  |  | Aggressive [MW] |  |  | 22.2533 | 22.5083 | 22.7718 | 23.0424 | 23.3216 | 23.6056 | 23.9425 | 24.2847 | 24.6365 | 24.9952 | 25.3576 | 25.7251 | 26.097 | 26.4671 | 26.8321 | 27.191 | 29.0018 | 30.8115
| BARNAHELY_A | 20 | 1 | Conservative [MW] |  |  | 22.7529 | 22.9722 | 23.1894 | 23.41 | 23.6287 | 23.8474 | 24.0583 | 24.27 | 24.4795 | 24.6856 | 24.8898 | 25.0879 | 25.2814 | 25.4685 | 25.6476 | 25.8196 | 26.6986 | 27.5763
|  |  |  | Best View [MW] |  |  | 22.7529 | 22.9844 | 23.2141 | 23.4459 | 23.6768 | 23.9076 | 24.1919 | 24.4732 | 24.7515 | 25.0213 | 25.2814 | 25.5319 | 25.7647 | 25.9809 | 26.1744 | 26.3384 | 27.2371 | 28.1308
|  |  |  | Base Case [MW] |  |  | 22.7529 | 23.0693 | 23.3835 | 23.7 | 24.0144 | 24.3262 | 24.6054 | 24.8804 | 25.1474 | 25.4037 | 25.6473 | 25.8734 | 26.0801 | 26.2572 | 26.4067 | 26.5124 | 27.1577 | 27.7956
|  |  |  | Aggressive [MW] |  |  | 22.7529 | 23.1441 | 23.5349 | 23.9255 | 24.3111 | 24.6907 | 25.0345 | 25.3647 | 25.6733 | 25.953 | 26.1994 | 26.3966 | 26.5297 | 26.5797 | 26.5163 | 26.2981 | 25.6199 | 24.9159
| BARNAHELY_B | 20 | 1 | Conservative [MW] |  |  | 16.3861 | 16.4588 | 16.529 | 16.6033 | 16.6795 | 16.755 | 16.8316 | 16.9094 | 16.9887 | 17.0691 | 17.1505 | 17.2328 | 17.3178 | 17.4034 | 17.4888 | 17.579 | 18.0173 | 18.4565
|  |  |  | Best View [MW] |  |  | 16.3861 | 16.4628 | 16.5389 | 16.6162 | 16.6967 | 16.7761 | 16.8794 | 16.9861 | 17.0942 | 17.2032 | 17.3168 | 17.4323 | 17.5496 | 17.6701 | 17.7911 | 17.9168 | 18.5327 | 19.1493
|  |  |  | Base Case [MW] |  |  | 16.3861 | 16.4888 | 16.595 | 16.7043 | 16.814 | 16.9302 | 17.0363 | 17.1453 | 17.2573 | 17.3716 | 17.4897 | 17.6068 | 17.7292 | 17.854 | 17.9781 | 18.1057 | 18.7343 | 19.3636
|  |  |  | Aggressive [MW] |  |  | 16.3861 | 16.5145 | 16.6456 | 16.783 | 16.9232 | 17.0702 | 17.2102 | 17.3551 | 17.5009 | 17.6546 | 17.8096 | 17.9669 | 18.1304 | 18.296 | 18.4617 | 18.6333 | 19.4756 | 20.3189
| BARODA | 10 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965 | 26.1965
| BATTER LANE | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968
|  |  |  | Best View [MW] |  |  | 0 | 0 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968 | 39.7968
| BELLACORRICK | 20 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 2.8413 | 2.8515 | 2.8623 | 2.8732 | 2.8843 | 2.8958 | 2.9076 | 2.9197 | 2.9321 | 2.945 | 2.958 | 3.0227 | 3.0875
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 2.8611 | 2.8748 | 2.8889 | 2.9034 | 2.9185 | 2.934 | 2.9502 | 2.9668 | 2.9841 | 3.0018 | 3.0201 | 3.1101 | 3.2002
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 2.8737 | 2.8904 | 2.9076 | 2.9255 | 2.9442 | 2.9637 | 2.9837 | 3.0048 | 3.0267 | 3.0494 | 3.0729 | 3.1881 | 3.3035
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 2.9222 | 2.9467 | 2.9726 | 2.9999 | 3.0286 | 3.0588 | 3.0907 | 3.1242 | 3.1594 | 3.1965 | 3.2355 | 3.4253 | 3.6154
| BIRDHILL | 20 | 2 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 40.176 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 40.176 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 40.176 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 40.176 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897 | 40.4897
| BRACKLONE | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 24.7 | 24.7 | 26.5803 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866
|  |  |  | Best View [MW] |  |  | 0 | 0 | 24.7 | 24.7 | 26.5803 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 24.7 | 24.7 | 26.5803 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 24.7 | 24.7 | 26.5803 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866 | 27.1866
| CABRA | 10 | 1 | Conservative [MW] |  |  | 27.0201 | 27.143 | 27.2694 | 27.396 | 27.5265 | 27.6605 | 27.78 | 27.9044 | 28.0328 | 28.1616 | 28.2946 | 28.4262 | 28.562 | 28.7045 | 28.7894 | 28.8491 | 29.2149 | 29.5766
|  |  |  | Best View [MW] |  |  | 27.0201 | 27.1649 | 27.3101 | 27.4607 | 27.6116 | 27.7718 | 27.9121 | 28.0505 | 28.1958 | 28.3425 | 28.4948 | 28.6485 | 28.7692 | 28.8365 | 28.8966 | 28.9488 | 29.2308 | 29.5116
|  |  |  | Base Case [MW] |  |  | 27.0201 | 27.1849 | 27.3555 | 27.5307 | 27.7139 | 27.9014 | 28.0556 | 28.2098 | 28.3725 | 28.5384 | 28.7075 | 28.8007 | 28.865 | 28.93 | 28.9809 | 29.0281 | 29.2741 | 29.5195
|  |  |  | Aggressive [MW] |  |  | 27.0201 | 27.3008 | 27.5992 | 27.9075 | 28.2237 | 28.5838 | 28.7462 | 28.8521 | 28.9187 | 28.9802 | 29.0356 | 29.0823 | 29.1189 | 29.146 | 29.1621 | 29.1641 | 29.2118 | 29.2571
| CASTLEVIEW | 10 | 1 | Conservative [MW] |  |  | 42.3864 | 42.6349 | 42.8856 | 43.1389 | 43.3938 | 43.6532 | 42.7507 | 43.0103 | 43.2766 | 43.5417 | 43.8122 | 44.0834 | 44.3546 | 44.6287 | 44.9005 | 45.1769 | 46.5467 | 47.9173
|  |  |  | Best View [MW] |  |  | 42.3864 | 42.6472 | 42.9121 | 43.1806 | 43.4519 | 43.7263 | 42.9141 | 43.2667 | 43.6282 | 43.9886 | 44.3547 | 44.7193 | 45.0872 | 45.4564 | 45.8227 | 46.1892 | 48.0213 | 49.8534
|  |  |  | Base Case [MW] |  |  | 42.3864 | 42.7446 | 43.1099 | 43.4805 | 43.8554 | 44.2375 | 43.4371 | 43.7973 | 44.163 | 44.5286 | 44.8988 | 45.2676 | 45.6369 | 46.0045 | 46.3699 | 46.7304 | 48.546 | 50.3608
|  |  |  | Aggressive [MW] |  |  | 42.3864 | 42.8299 | 43.2835 | 43.7478 | 44.2231 | 44.7007 | 44.0073 | 44.4712 | 44.9402 | 45.4054 | 45.8742 | 46.3405 | 46.7963 | 47.2442 | 47.6714 | 48.0799 | 50.1724 | 52.2617
|  |  | 2 | Conservative [MW] |  |  | 0 | 0 | 0 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801 | 16.8801
| CENTRAL PARK | 10 | 1 | Conservative [MW] |  |  | 28.4862 | 28.6022 | 28.7219 | 28.8468 | 28.9712 | 29.1032 | 29.2011 | 29.3064 | 29.4106 | 29.517 | 29.6254 | 29.7321 | 29.8456 | 29.9605 | 30.0729 | 30.191 | 30.7663 | 31.3426
|  |  |  | Best View [MW] |  |  | 28.4862 | 28.6191 | 28.7617 | 28.9062 | 29.0515 | 29.2058 | 29.3242 | 29.4473 | 29.5712 | 29.699 | 29.8312 | 29.9624 | 30.0973 | 30.2354 | 30.3764 | 30.515 | 31.2144 | 31.9134
|  |  |  | Base Case [MW] |  |  | 28.4862 | 28.639 | 28.7952 | 28.9577 | 29.1269 | 29.3012 | 29.4366 | 29.5742 | 29.7186 | 29.8646 | 30.0125 | 30.1648 | 30.3226 | 30.4797 | 30.641 | 30.8062 | 31.6216 | 32.4377
|  |  |  | Aggressive [MW] |  |  | 28.4862 | 28.7067 | 28.94 | 29.1841 | 29.4417 | 29.705 | 29.842 | 29.9854 | 30.127 | 30.2705 | 30.4195 | 30.5701 | 30.7261 | 30.8818 | 31.0419 | 31.2059 | 32.0156 | 32.8259
| CHERRYWOOD | 10 | 1 | Conservative [MW] |  |  | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7
|  |  |  | Best View [MW] |  |  | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7
|  |  |  | Base Case [MW] |  |  | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7
|  |  |  | Aggressive [MW] |  |  | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7
| CITYWEST | 10 | 1 | Conservative [MW] |  |  | 31.8574 | 32.0482 | 32.2382 | 32.4309 | 32.6186 | 32.8129 | 32.9601 | 33.1091 | 33.2534 | 33.3983 | 33.5468 | 33.6881 | 33.8274 | 33.9671 | 34.1032 | 34.2328 | 34.8983 | 35.5627
|  |  |  | Best View [MW] |  |  | 31.8574 | 32.077 | 32.2966 | 32.5192 | 32.7406 | 32.9633 | 33.1345 | 33.3038 | 33.4749 | 33.6424 | 33.8084 | 33.968 | 34.1291 | 34.2798 | 34.428 | 34.5675 | 35.2881 | 36.0072
|  |  |  | Base Case [MW] |  |  | 31.8574 | 32.1042 | 32.352 | 32.6027 | 32.8505 | 33.0989 | 33.292 | 33.4808 | 33.668 | 33.8521 | 34.0305 | 34.2058 | 34.376 | 34.5329 | 34.6839 | 34.8202 | 35.5407 | 36.2588
|  |  |  | Aggressive [MW] |  |  | 31.8574 | 32.2147 | 32.5774 | 32.9353 | 33.2941 | 33.6509 | 33.8267 | 33.9967 | 34.1584 | 34.3209 | 34.4714 | 34.6174 | 34.7514 | 34.8753 | 34.9865 | 35.0812 | 35.5989 | 36.1138
| CLOGHBOOLA | 20 | 1 | Conservative [MW] |  |  | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718
|  |  |  | Best View [MW] |  |  | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718
|  |  |  | Base Case [MW] |  |  | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718
|  |  |  | Aggressive [MW] |  |  | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718 | 7.0718
| COLLEGE PARK | 10 | 1 | Conservative [MW] |  |  | 15.6998 | 15.7944 | 15.8728 | 15.9315 | 15.9634 | 15.9625 | 15.9438 | 15.9517 | 15.9219 | 15.8742 | 15.7962 | 15.6938 | 15.5677 | 15.4035 | 15.192 | 14.9228 | 13.7305 | 12.5286
|  |  |  | Best View [MW] |  |  | 15.6998 | 15.803 | 15.8875 | 15.9459 | 15.9668 | 15.9475 | 15.9075 | 15.5288 | 15.4344 | 15.3159 | 15.1551 | 14.9437 | 14.6624 | 14.2918 | 13.7811 | 13.0318 | 9.9214 | 6.7712
|  |  |  | Base Case [MW] |  |  | 15.6998 | 15.8112 | 15.8999 | 15.9547 | 15.966 | 15.9166 | 15.8472 | 15.8455 | 15.7243 | 15.5666 | 15.3475 | 15.0481 | 14.633 | 14.0409 | 13.1209 | 10.7808 | 2.8671 | -0.0001
|  |  |  | Aggressive [MW] |  |  | 15.6998 | 15.834 | 15.9303 | 15.9672 | 15.9243 | 15.7518 | 15.6226 | 15.6312 | 15.4606 | 15.2353 | 14.934 | 14.5342 | 13.9797 | 13.1483 | 11.4152 | 11.2429 | 6.2193 | 1.4558
|  | 20 | 1 | Conservative [MW] |  |  | 36.1341 | 36.6054 | 37.0994 | 37.5972 | 38.1138 | 38.7266 | 39.0363 | 39.3887 | 39.7089 | 40.0384 | 40.3676 | 40.7048 | 41.0412 | 41.384 | 41.7361 | 42.0947 | 43.8706 | 45.6475
|  |  |  | Best View [MW] |  |  | 36.1341 | 36.6601 | 37.1999 | 37.7564 | 38.3331 | 39.0021 | 39.3674 | 39.7697 | 40.1466 | 40.5236 | 40.91 | 41.303 | 41.7041 | 42.1117 | 42.5273 | 42.9477 | 45.0368 | 47.1267
|  |  |  | Base Case [MW] |  |  | 36.1341 | 36.711 | 37.3152 | 37.9292 | 38.5694 | 39.3184 | 39.7302 | 40.1887 | 40.6097 | 41.0473 | 41.4934 | 41.9445 | 42.4099 | 42.8719 | 43.3479 | 43.8364 | 46.2456 | 48.6568
|  |  |  | Aggressive [MW] |  |  | 36.1341 | 36.8445 | 37.5903 | 38.3589 | 39.1633 | 40.0872 | 40.4672 | 40.8978 | 41.2873 | 41.6939 | 42.0997 | 42.512 | 42.944 | 43.3729 | 43.8081 | 44.2514 | 46.4464 | 48.6427
| COOKSTOWN | 10 | 1 | Conservative [MW] |  |  | 29.5396 | 29.6907 | 29.8426 | 29.9988 | 30.1597 | 30.3199 | 30.4455 | 30.5752 | 30.7052 | 30.8342 | 30.9678 | 31.1041 | 31.2396 | 31.3822 | 31.5182 | 31.6609 | 32.3566 | 33.0534
|  |  |  | Best View [MW] |  |  | 29.5396 | 29.713 | 29.8914 | 30.0703 | 30.2577 | 30.4484 | 30.6005 | 30.7496 | 30.9038 | 31.0617 | 31.2201 | 31.3814 | 31.546 | 31.7126 | 31.8816 | 32.0515 | 32.8984 | 33.7456
|  |  |  | Base Case [MW] |  |  | 29.5396 | 29.7354 | 29.9367 | 30.1417 | 30.3506 | 30.5664 | 30.7397 | 30.911 | 31.0879 | 31.2655 | 31.4464 | 31.6316 | 31.8189 | 32.0081 | 32.1982 | 32.3929 | 33.354 | 34.316
|  |  |  | Aggressive [MW] |  |  | 29.5396 | 29.8233 | 30.1182 | 30.4229 | 30.7417 | 31.07 | 31.238 | 31.408 | 31.5833 | 31.7596 | 31.9354 | 32.1152 | 32.2973 | 32.4761 | 32.66 | 32.8453 | 33.768 | 34.691
| COOLROE | 20 | 1 | Conservative [MW] |  |  | 19.1879 | 19.2818 | 19.378 | 19.4757 | 19.576 | 19.6775 | 19.78 | 19.8849 | 19.9924 | 20.1011 | 20.212 | 20.3269 | 20.4427 | 20.5609 | 20.6828 | 20.8054 | 21.4167 | 22.0282
|  |  |  | Best View [MW] |  |  | 19.1879 | 19.2875 | 19.3883 | 19.4919 | 19.5979 | 19.7064 | 19.8461 | 19.9882 | 20.1352 | 20.2859 | 20.4412 | 20.6015 | 20.7667 | 20.9347 | 21.107 | 21.2855 | 22.1617 | 23.0388
|  |  |  | Base Case [MW] |  |  | 19.1879 | 19.3241 | 19.4642 | 19.6093 | 19.7584 | 19.9123 | 20.0582 | 20.2063 | 20.3609 | 20.5188 | 20.6814 | 20.8471 | 21.0191 | 21.1953 | 21.3756 | 21.5617 | 22.4767 | 23.3927
|  |  |  | Aggressive [MW] |  |  | 19.1879 | 19.3564 | 19.5326 | 19.7151 | 19.905 | 20.1025 | 20.2944 | 20.4934 | 20.6996 | 20.9126 | 21.1319 | 21.3608 | 21.5952 | 21.8385 | 22.0901 | 22.3495 | 23.6257 | 24.9032
| CORDERRY | 20 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  | 2 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| CORDUFF | 20 | 1 | Conservative [MW] |  |  | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629
|  |  |  | Best View [MW] |  |  | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629
|  |  |  | Base Case [MW] |  |  | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629
|  |  |  | Aggressive [MW] |  |  | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629 | 38.7629
| CRANE | 20 | 1 | Conservative [MW] |  |  | 8.6425 | 8.6785 | 8.7152 | 8.7523 | 8.7895 | 8.8273 | 8.9171 | 9.0085 | 9.1022 | 9.1986 | 9.2971 | 9.3982 | 9.5019 | 9.6076 | 9.7162 | 9.8271 | 10.3757 | 10.9246
|  |  |  | Best View [MW] |  |  | 8.6425 | 8.706 | 8.7712 | 8.8371 | 8.9046 | 8.9733 | 9.0746 | 9.1781 | 9.2849 | 9.3942 | 9.5066 | 9.6221 | 9.7398 | 9.8609 | 9.9847 | 10.1117 | 10.7382 | 11.3651
|  |  |  | Base Case [MW] |  |  | 8.6425 | 8.7206 | 8.8007 | 8.883 | 8.967 | 9.0527 | 9.1664 | 9.2828 | 9.4029 | 9.5266 | 9.6537 | 9.7842 | 9.9185 | 10.0557 | 10.1971 | 10.3416 | 11.0557 | 11.7704
|  |  |  | Aggressive [MW] |  |  | 8.6425 | 8.7651 | 8.8927 | 9.0245 | 9.1617 | 9.3031 | 9.4706 | 9.6445 | 9.8252 | 10.0123 | 10.2058 | 10.4066 | 10.6131 | 10.8258 | 11.0448 | 11.2693 | 12.377 | 13.4855
| CRORY | 20 | 1 | Conservative [MW] |  |  | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093
|  |  |  | Best View [MW] |  |  | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093
|  |  |  | Base Case [MW] |  |  | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093
|  |  |  | Aggressive [MW] |  |  | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093 | 1.4093
|  |  | 2 | Conservative [MW] |  |  | 0 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215
|  |  |  | Best View [MW] |  |  | 0 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215
|  |  |  | Base Case [MW] |  |  | 0 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215
|  |  |  | Aggressive [MW] |  |  | 0 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215 | 13.8215
| DUNFIRTH | 20 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 12.9193 | 13.3371 | 13.4472 | 13.5622 | 13.6806 | 13.803 | 13.9289 | 14.0589 | 14.1929 | 14.3314 | 14.4737 | 15.1752 | 15.8773
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 12.9972 | 13.433 | 13.5617 | 13.6968 | 13.8365 | 13.9815 | 14.1312 | 14.2865 | 14.4474 | 14.6136 | 14.7861 | 15.6317 | 16.4785
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 13.3316 | 13.7817 | 13.928 | 14.0803 | 14.2387 | 14.4023 | 14.5726 | 14.7487 | 14.9312 | 15.1208 | 15.3161 | 16.2773 | 17.2394
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 13.6192 | 14.0994 | 14.2808 | 14.4699 | 14.6664 | 14.8718 | 15.0859 | 15.3084 | 15.5394 | 15.7803 | 16.0309 | 17.2579 | 18.4865
| DUNSINK | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016
| EASTMONT | 10 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601
| ENNIS | 10 | 1 | Conservative [MW] |  |  | 17.6882 | 17.748 | 17.8079 | 17.8693 | 17.9319 | 17.9958 | 18.082 | 18.1693 | 18.2593 | 18.3506 | 18.4443 | 18.5408 | 18.6386 | 18.7402 | 18.8413 | 18.9466 | 19.462 | 19.9782
|  |  |  | Best View [MW] |  |  | 17.6882 | 17.754 | 17.8199 | 17.8884 | 17.957 | 18.0272 | 18.15 | 18.2769 | 18.4064 | 18.541 | 18.6792 | 18.8226 | 18.9711 | 19.1229 | 19.2796 | 19.441 | 20.2353 | 21.0304
|  |  |  | Base Case [MW] |  |  | 17.6882 | 17.7928 | 17.8991 | 18.0093 | 18.1234 | 18.2401 | 18.38 | 18.5249 | 18.6748 | 18.83 | 18.9898 | 19.1543 | 19.325 | 19.5017 | 19.6825 | 19.8704 | 20.7909 | 21.7126
|  |  |  | Aggressive [MW] |  |  | 17.6882 | 17.8707 | 18.0626 | 18.2653 | 18.4795 | 18.7039 | 18.8688 | 19.04 | 19.217 | 19.4001 | 19.5903 | 19.7857 | 19.9896 | 20.1982 | 20.4144 | 20.6381 | 21.7365 | 22.8362
| FERMOY | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176
| FORTUNESTOWN | 10 | 1 | Conservative [MW] |  |  | 27.7466 | 27.8693 | 27.9997 | 28.1295 | 28.2627 | 28.3988 | 28.5051 | 28.6146 | 28.7214 | 28.8349 | 28.9461 | 29.0634 | 29.1826 | 29.3025 | 29.4241 | 29.5462 | 30.1555 | 30.765
|  |  |  | Best View [MW] |  |  | 27.7466 | 27.8917 | 28.0375 | 28.1882 | 28.3467 | 28.5056 | 28.6333 | 28.7606 | 28.8923 | 29.0278 | 29.1621 | 29.3043 | 29.4447 | 29.5917 | 29.7404 | 29.8869 | 30.6252 | 31.3631
|  |  |  | Base Case [MW] |  |  | 27.7466 | 27.9088 | 28.0737 | 28.2478 | 28.4227 | 28.6059 | 28.7517 | 28.8989 | 29.0481 | 29.2027 | 29.3574 | 29.5207 | 29.6837 | 29.85 | 30.0184 | 30.1937 | 31.0518 | 31.911
|  |  |  | Aggressive [MW] |  |  | 27.7466 | 27.9821 | 28.2288 | 28.4874 | 28.7557 | 29.0325 | 29.179 | 29.3274 | 29.4769 | 29.6323 | 29.7876 | 29.9437 | 30.108 | 30.2711 | 30.4423 | 30.6106 | 31.4599 | 32.3086
| FOSTERSTOWN | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 39.4954 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 39.4954 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 39.4954 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 39.4954 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389 | 40.2389
| GALWAY | 10 | 1 | Conservative [MW] |  |  | 28.346 | 28.4428 | 28.5355 | 28.6313 | 28.727 | 28.827 | 28.9611 | 29.0994 | 29.2406 | 29.3809 | 29.5227 | 29.6715 | 29.8172 | 29.9642 | 30.1166 | 30.2694 | 31.0325 | 31.7956
|  |  |  | Best View [MW] |  |  | 28.346 | 28.4646 | 28.585 | 28.7061 | 28.8284 | 28.955 | 29.1465 | 29.3438 | 29.5466 | 29.7491 | 29.9598 | 30.1727 | 30.3868 | 30.6089 | 30.8295 | 31.0559 | 32.1723 | 33.2897
|  |  |  | Base Case [MW] |  |  | 28.346 | 28.4985 | 28.648 | 28.8025 | 28.9611 | 29.1239 | 29.3385 | 29.5591 | 29.7798 | 30.0129 | 30.2427 | 30.4816 | 30.7233 | 30.9704 | 31.2157 | 31.4671 | 32.7079 | 33.9497
|  |  |  | Aggressive [MW] |  |  | 28.346 | 28.5789 | 28.8221 | 29.0725 | 29.3285 | 29.5926 | 29.8513 | 30.1129 | 30.3838 | 30.6568 | 30.9389 | 31.2219 | 31.5073 | 31.7957 | 32.0829 | 32.3696 | 33.8045 | 35.2393
| GARROW | 20 | 1 | Conservative [MW] |  |  | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506
|  |  |  | Best View [MW] |  |  | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506
|  |  |  | Base Case [MW] |  |  | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506
|  |  |  | Aggressive [MW] |  |  | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506 | 4.7506
| GLENREE | 20 | 1 | Conservative [MW] |  |  | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162
|  |  |  | Best View [MW] |  |  | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162
|  |  |  | Base Case [MW] |  |  | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162
|  |  |  | Aggressive [MW] |  |  | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162 | 2.3162
| GRANGE CASTLE | 20 | 1 | Conservative [MW] |  |  | 13.4364 | 13.4408 | 13.4465 | 13.4521 | 13.4575 | 13.4645 | 13.4673 | 13.4717 | 13.4744 | 13.4786 | 13.4829 | 13.4869 | 13.491 | 13.4948 | 13.4987 | 13.5023 | 13.5212 | 13.54
|  |  |  | Best View [MW] |  |  | 13.4364 | 13.4418 | 13.4488 | 13.4536 | 13.4598 | 13.4677 | 13.4715 | 13.4752 | 13.4807 | 13.4842 | 13.4893 | 13.4942 | 13.4991 | 13.5038 | 13.5083 | 13.5128 | 13.5354 | 13.5579
|  |  |  | Base Case [MW] |  |  | 13.4364 | 13.4428 | 13.4491 | 13.4567 | 13.4638 | 13.4705 | 13.4754 | 13.4801 | 13.4848 | 13.491 | 13.4953 | 13.501 | 13.5068 | 13.5121 | 13.5175 | 13.5243 | 13.5544 | 13.5848
|  |  |  | Aggressive [MW] |  |  | 13.4364 | 13.4447 | 13.4525 | 13.4614 | 13.4698 | 13.4793 | 13.4846 | 13.4878 | 13.4929 | 13.4978 | 13.5025 | 13.5071 | 13.5134 | 13.5177 | 13.5235 | 13.5292 | 13.5579 | 13.5867
|  |  | 2 | Conservative [MW] |  |  | 34.7517 | 34.9636 | 35.1718 | 35.3572 | 35.5464 | 35.7127 | 35.7947 | 35.871 | 35.941 | 36.0037 | 36.0489 | 36.0823 | 36.1074 | 36.108 | 36.0957 | 36.0618 | 35.95 | 35.8345
|  |  |  | Best View [MW] |  |  | 34.7517 | 34.9861 | 35.2083 | 35.4184 | 35.6155 | 35.7915 | 35.877 | 35.9553 | 36.0202 | 36.0667 | 36.0987 | 36.1118 | 36.0956 | 36.0553 | 35.9694 | 35.85 | 35.3422 | 34.8288
|  |  |  | Base Case [MW] |  |  | 34.7517 | 35.0116 | 35.2524 | 35.4729 | 35.6879 | 35.8636 | 35.9499 | 36.0204 | 36.0776 | 36.1033 | 36.105 | 36.0825 | 36.0011 | 35.8772 | 35.7119 | 35.4827 | 34.5071 | 33.5208
|  |  |  | Aggressive [MW] |  |  | 34.7517 | 35.0685 | 35.3535 | 35.6205 | 35.8449 | 36.0151 | 36.0629 | 36.0965 | 36.1062 | 36.0996 | 36.0619 | 35.9804 | 35.8628 | 35.7177 | 35.5146 | 35.2562 | 34.1118 | 32.9581
| HAROLDS CROSS | 10 | 1 | Conservative [MW] |  |  | 29.1076 | 29.255 | 29.4074 | 29.5606 | 29.7144 | 29.8706 | 30.017 | 30.1612 | 30.3107 | 30.4615 | 30.6162 | 30.7715 | 30.9258 | 31.0875 | 31.2473 | 31.4095 | 32.2143 | 33.0196
|  |  |  | Best View [MW] |  |  | 29.1076 | 29.28 | 29.4538 | 29.6368 | 29.8186 | 30.0033 | 30.1659 | 30.3312 | 30.499 | 30.6729 | 30.8472 | 31.0215 | 31.1996 | 31.3806 | 31.5635 | 31.748 | 32.6664 | 33.585
|  |  |  | Base Case [MW] |  |  | 29.1076 | 29.3058 | 29.5127 | 29.7228 | 29.9383 | 30.1576 | 30.3377 | 30.522 | 30.7047 | 30.8983 | 31.0885 | 31.2833 | 31.4813 | 31.6813 | 31.8823 | 32.0872 | 33.1015 | 34.1164
|  |  |  | Aggressive [MW] |  |  | 29.1076 | 29.4449 | 29.8002 | 30.1682 | 30.5539 | 30.9484 | 31.1337 | 31.3205 | 31.5086 | 31.701 | 31.8926 | 32.0858 | 32.2801 | 32.4744 | 32.7063 | 33.0928 | 34.6129 | 36.1588
| HARTNETTS CROSS | 20 | 1 | Conservative [MW] |  |  | 13.6011 | 13.6183 | 13.635 | 13.6529 | 13.6721 | 13.6905 | 13.7088 | 13.7284 | 13.749 | 13.7689 | 13.7901 | 13.8104 | 13.8318 | 13.8543 | 13.8779 | 13.9004 | 14.0158 | 14.131
|  |  |  | Best View [MW] |  |  | 13.6011 | 13.6189 | 13.6379 | 13.6561 | 13.6755 | 13.6961 | 13.7217 | 13.7479 | 13.7747 | 13.804 | 13.8318 | 13.862 | 13.8926 | 13.9252 | 13.9581 | 13.9914 | 14.1571 | 14.3227
|  |  |  | Base Case [MW] |  |  | 13.6011 | 13.6262 | 13.6521 | 13.6784 | 13.7053 | 13.7342 | 13.7598 | 13.7878 | 13.8162 | 13.8471 | 13.8762 | 13.9078 | 13.9415 | 13.9735 | 14.0076 | 14.0438 | 14.219 | 14.3946
|  |  |  | Aggressive [MW] |  |  | 13.6011 | 13.6354 | 13.6711 | 13.708 | 13.7475 | 13.7899 | 13.8194 | 13.8492 | 13.8795 | 13.912 | 13.9445 | 13.9793 | 14.014 | 14.0507 | 14.0893 | 14.1277 | 14.32 | 14.5124
| HEUSTON SQUARE | 10 | 1 | Conservative [MW] |  |  | 28.3064 | 28.4144 | 28.5237 | 28.6383 | 28.7536 | 28.8736 | 28.9806 | 29.0893 | 29.2042 | 29.3202 | 29.4372 | 29.5552 | 29.6782 | 29.8052 | 29.933 | 30.0641 | 30.7109 | 31.3582
|  |  |  | Best View [MW] |  |  | 28.3064 | 28.4336 | 28.5599 | 28.6929 | 28.8326 | 28.9733 | 29.0945 | 29.2192 | 29.3486 | 29.4809 | 29.6165 | 29.755 | 29.8962 | 30.0389 | 30.1879 | 30.3376 | 31.0843 | 31.831
|  |  |  | Base Case [MW] |  |  | 28.3064 | 28.4523 | 28.6023 | 28.7599 | 28.9193 | 29.0892 | 29.2255 | 29.3635 | 29.5081 | 29.6542 | 29.8051 | 29.9606 | 30.12 | 30.2833 | 30.4497 | 30.6185 | 31.456 | 32.294
|  |  |  | Aggressive [MW] |  |  | 28.3064 | 28.5565 | 28.8189 | 29.095 | 29.3893 | 29.6981 | 29.8405 | 29.9892 | 30.1431 | 30.2977 | 30.4561 | 30.6181 | 30.7793 | 30.9477 | 31.122 | 31.2937 | 32.1591 | 33.0241
| KILLACLOYNE | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 24.7 | 25.3383 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 24.7 | 25.3383 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 24.7 | 25.3383 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 24.7 | 25.3383 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649 | 25.9649
| KILLOTERAN | 10 | 1 | Conservative [MW] |  |  | 28.7207 | 28.8066 | 28.8892 | 28.9756 | 29.0623 | 29.1534 | 29.2678 | 29.3879 | 29.5047 | 29.6309 | 29.753 | 29.8796 | 30.0112 | 30.1417 | 30.2759 | 30.4137 | 31.0933 | 31.7734
|  |  |  | Best View [MW] |  |  | 28.7207 | 28.8139 | 28.9069 | 29.0037 | 29.0991 | 29.1983 | 29.3479 | 29.4986 | 29.6535 | 29.8129 | 29.9799 | 30.1452 | 30.318 | 30.4919 | 30.6712 | 30.8552 | 31.7625 | 32.6706
|  |  |  | Base Case [MW] |  |  | 28.7207 | 28.8312 | 28.9428 | 29.0566 | 29.1715 | 29.2878 | 29.4646 | 29.6419 | 29.8229 | 30.0163 | 30.2074 | 30.4085 | 30.6143 | 30.824 | 31.04 | 31.2575 | 32.3408 | 33.4243
|  |  |  | Aggressive [MW] |  |  | 28.7207 | 28.8944 | 29.0722 | 29.2534 | 29.4462 | 29.6398 | 29.8627 | 30.0891 | 30.3268 | 30.5687 | 30.8181 | 31.0772 | 31.3398 | 31.6118 | 31.8905 | 32.1739 | 33.5786 | 34.984
| KILMORE | 10 | 1 | Conservative [MW] |  |  | 55.4821 | 55.9852 | 56.4943 | 57.0044 | 57.5098 | 58.0172 | 58.302 | 58.5826 | 58.8679 | 59.1456 | 59.42 | 59.6896 | 59.9527 | 60.2092 | 60.4603 | 60.701 | 61.9322 | 63.1617
|  |  |  | Best View [MW] |  |  | 55.4821 | 56.0408 | 56.5985 | 57.1578 | 57.7215 | 58.2728 | 58.6018 | 58.9201 | 59.2391 | 59.5496 | 59.8556 | 60.1542 | 60.4439 | 60.7157 | 60.984 | 61.2234 | 62.4975 | 63.7669
|  |  |  | Base Case [MW] |  |  | 55.4821 | 56.0951 | 56.7072 | 57.3248 | 57.9351 | 58.5463 | 58.907 | 59.2605 | 59.613 | 59.9496 | 60.2823 | 60.597 | 60.9017 | 61.177 | 61.4314 | 61.6693 | 62.9028 | 64.1335
|  |  |  | Aggressive [MW] |  |  | 55.4821 | 56.2291 | 56.9815 | 57.738 | 58.4801 | 59.2123 | 59.5228 | 59.8281 | 60.1277 | 60.4187 | 60.6919 | 60.957 | 61.2003 | 61.424 | 61.6346 | 61.8283 | 62.8418 | 63.8525
| KILNAP | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776 | 42.2776
| KILPADDOGE | 20 | 1 | Conservative [MW] |  |  | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834
|  |  |  | Best View [MW] |  |  | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834
|  |  |  | Base Case [MW] |  |  | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834
|  |  |  | Aggressive [MW] |  |  | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834 | 1.6834
| LIBERTY STREET | 10 | 1 | Conservative [MW] |  |  | 27.5114 | 27.5934 | 27.6797 | 27.7693 | 27.8584 | 27.4458 | 27.5375 | 27.6323 | 27.7267 | 27.8242 | 27.9244 | 28.0269 | 28.1325 | 28.2364 | 28.3425 | 28.4545 | 28.9986 | 29.5437
|  |  |  | Best View [MW] |  |  | 27.5114 | 27.6007 | 27.6898 | 27.7818 | 27.8766 | 27.4731 | 27.5956 | 27.7245 | 27.8569 | 27.992 | 28.1296 | 28.273 | 28.4173 | 28.5672 | 28.7212 | 28.8797 | 29.6603 | 30.4416
|  |  |  | Base Case [MW] |  |  | 27.5114 | 27.6319 | 27.7602 | 27.8867 | 28.0234 | 27.658 | 27.7864 | 27.9216 | 28.0594 | 28.1992 | 28.341 | 28.4917 | 28.6428 | 28.7984 | 28.9579 | 29.1207 | 29.9258 | 30.7315
|  |  |  | Aggressive [MW] |  |  | 27.5114 | 27.6614 | 27.8181 | 27.9837 | 28.1543 | 27.8286 | 27.9983 | 28.1756 | 28.3603 | 28.5479 | 28.7449 | 28.9424 | 29.1514 | 29.3632 | 29.5834 | 29.8076 | 30.918 | 32.029
| MACETOWN | 10 | 1 | Conservative [MW] |  |  | 29.5421 | 29.8165 | 30.0957 | 30.3767 | 30.6584 | 30.941 | 31.1067 | 31.6196 | 31.7731 | 31.9206 | 32.0737 | 32.2184 | 32.3663 | 32.5113 | 32.6513 | 32.7904 | 33.4881 | 34.1857
|  |  |  | Best View [MW] |  |  | 29.5421 | 29.8421 | 30.1512 | 30.4623 | 30.7763 | 31.0884 | 31.2718 | 31.7999 | 31.976 | 32.1429 | 32.3113 | 32.4808 | 32.6419 | 32.8009 | 32.9488 | 33.0958 | 33.8332 | 34.5705
|  |  |  | Base Case [MW] |  |  | 29.5421 | 29.8762 | 30.2132 | 30.5544 | 30.9 | 31.2423 | 31.4496 | 31.9871 | 32.1784 | 32.3681 | 32.5536 | 32.7278 | 32.9055 | 33.0666 | 33.2257 | 33.3677 | 34.1234 | 34.8763
|  |  |  | Aggressive [MW] |  |  | 29.5421 | 29.9514 | 30.3637 | 30.7869 | 31.205 | 31.6277 | 31.8061 | 32.2975 | 32.4654 | 32.6261 | 32.7845 | 32.933 | 33.0807 | 33.2206 | 33.3493 | 33.4717 | 34.1007 | 34.7286
| MARINA | 10 | 1 | Conservative [MW] |  |  | 27.5461 | 41.932 | 42.0293 | 42.1299 | 42.2338 | 42.3379 | 42.4441 | 42.5537 | 42.6626 | 42.774 | 42.8926 | 43.0097 | 43.1293 | 43.2512 | 43.3796 | 43.5056 | 44.1419 | 44.7778
|  |  |  | Best View [MW] |  |  | 27.5461 | 41.9383 | 42.0426 | 42.1488 | 42.2582 | 42.371 | 42.5121 | 42.6606 | 42.8124 | 42.9667 | 43.1308 | 43.2925 | 43.4638 | 43.6406 | 43.8215 | 44.0061 | 44.9193 | 45.8331
|  |  |  | Base Case [MW] |  |  | 27.5461 | 41.9744 | 42.1181 | 42.2676 | 42.4237 | 42.581 | 42.7328 | 42.8871 | 43.044 | 43.2065 | 43.3746 | 43.5516 | 43.7293 | 43.9117 | 44.102 | 44.2952 | 45.2534 | 46.2121
|  |  |  | Aggressive [MW] |  |  | 27.5461 | 42.009 | 42.1899 | 42.3793 | 42.5738 | 42.779 | 42.9757 | 43.1805 | 43.3966 | 43.6151 | 43.8471 | 44.0837 | 44.3319 | 44.5869 | 44.8516 | 45.1242 | 46.4663 | 47.8097
| MCDERMOTT | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 39.2234 | 39.5428 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 39.2234 | 39.5428 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 39.2234 | 39.5428 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 39.2234 | 39.5428 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601
| MIDLETON | 10 | 1 | Conservative [MW] |  |  | 22.326 | 22.4903 | 22.6566 | 22.8273 | 22.9999 | 23.1744 | 23.3522 | 23.529 | 23.7116 | 23.8947 | 24.0808 | 24.2694 | 24.4605 | 24.6531 | 24.8501 | 25.0477 | 26.0339 | 27.0202
|  |  |  | Best View [MW] |  |  | 22.326 | 22.499 | 22.6757 | 22.8564 | 23.0382 | 23.2255 | 23.4628 | 23.7057 | 23.9515 | 24.2042 | 24.4582 | 24.7173 | 24.981 | 25.2482 | 25.5177 | 25.7915 | 27.1491 | 28.5075
|  |  |  | Base Case [MW] |  |  | 22.326 | 22.5632 | 22.8043 | 23.0534 | 23.3079 | 23.5669 | 23.8144 | 24.0644 | 24.3207 | 24.58 | 24.8441 | 25.1116 | 25.3819 | 25.6565 | 25.9308 | 26.2097 | 27.592 | 28.9751
|  |  |  | Aggressive [MW] |  |  | 22.326 | 22.6547 | 22.9921 | 23.3434 | 23.7045 | 24.0755 | 24.3363 | 24.6044 | 24.8738 | 25.1484 | 25.427 | 25.7087 | 25.9919 | 26.2748 | 26.5613 | 26.847 | 28.2775 | 29.708
| MILLTOWN (DR) | 10 | 1 | Conservative [MW] |  |  | 27.6259 | 27.7876 | 27.9496 | 28.1148 | 28.2068 | 28.1453 | 28.2698 | 28.4339 | 28.5899 | 28.7501 | 28.9099 | 29.0765 | 29.2413 | 29.4075 | 29.5748 | 29.7466 | 30.5938 | 31.4417
|  |  |  | Best View [MW] |  |  | 27.6259 | 27.8118 | 28.0043 | 28.1961 | 28.3223 | 28.2848 | 28.4336 | 28.615 | 28.7933 | 28.9717 | 29.1537 | 29.3422 | 29.5283 | 29.7198 | 29.9111 | 30.1019 | 31.0571 | 32.0123
|  |  |  | Base Case [MW] |  |  | 27.6259 | 27.8432 | 28.0657 | 28.293 | 28.449 | 28.4496 | 28.6121 | 28.8125 | 29.0098 | 29.2073 | 29.4121 | 29.6147 | 29.8228 | 30.0343 | 30.2446 | 30.456 | 31.5101 | 32.5643
|  |  |  | Aggressive [MW] |  |  | 27.6259 | 27.9936 | 28.376 | 28.7743 | 29.1175 | 29.2849 | 29.4527 | 29.6526 | 29.8522 | 30.05 | 30.2527 | 30.4552 | 30.66 | 30.8614 | 31.0664 | 31.2685 | 32.2866 | 33.3042
| MISERY HILL | 10 | 1 | Conservative [MW] |  |  | 30.2686 | 30.4237 | 30.5788 | 30.7381 | 30.9053 | 31.0692 | 31.2175 | 31.3709 | 31.525 | 31.6829 | 31.8404 | 32.0054 | 32.1684 | 32.3334 | 32.4999 | 32.6673 | 33.502 | 34.3368
|  |  |  | Best View [MW] |  |  | 30.2686 | 30.4494 | 30.6301 | 30.8186 | 31.0099 | 31.2057 | 31.375 | 31.5505 | 31.7224 | 31.9035 | 32.0839 | 32.2672 | 32.4486 | 32.6356 | 32.8274 | 33.0183 | 33.9753 | 34.9321
|  |  |  | Base Case [MW] |  |  | 30.2686 | 30.4795 | 30.6933 | 30.9125 | 31.1354 | 31.3636 | 31.5518 | 31.7415 | 31.9374 | 32.1342 | 32.3343 | 32.5366 | 32.7407 | 32.9448 | 33.1526 | 33.3615 | 34.4028 | 35.4444
|  |  |  | Aggressive [MW] |  |  | 30.2686 | 30.623 | 30.9903 | 31.3774 | 31.7769 | 32.1913 | 32.3833 | 32.5756 | 32.7667 | 32.9654 | 33.1607 | 33.3608 | 33.5592 | 33.7593 | 33.955 | 34.1496 | 35.1255 | 36.1013
| MONREAD | 10 | 1 | Conservative [MW] |  |  | 27.0792 | 27.2154 | 27.3543 | 27.4996 | 27.6463 | 27.7986 | 27.9141 | 28.0309 | 28.1537 | 28.2728 | 28.3967 | 28.5253 | 28.65 | 28.7831 | 28.9114 | 29.0436 | 29.6943 | 30.3456
|  |  |  | Best View [MW] |  |  | 27.0792 | 27.2357 | 27.3998 | 27.5667 | 27.7394 | 27.9134 | 28.0551 | 28.1954 | 28.3381 | 28.4868 | 28.6326 | 28.7837 | 28.9354 | 29.0921 | 29.2526 | 29.4121 | 30.2121 | 31.0119
|  |  |  | Base Case [MW] |  |  | 27.0792 | 27.2555 | 27.4402 | 27.6319 | 27.8257 | 28.0245 | 28.1817 | 28.3429 | 28.5076 | 28.675 | 28.8449 | 29.016 | 29.1931 | 29.3698 | 29.5509 | 29.7349 | 30.6472 | 31.5599
|  |  |  | Aggressive [MW] |  |  | 27.0792 | 27.3382 | 27.6109 | 27.894 | 28.185 | 28.4933 | 28.6476 | 28.8108 | 28.9728 | 29.1378 | 29.305 | 29.4744 | 29.6449 | 29.8204 | 29.9949 | 30.1738 | 31.0564 | 31.9397
| MULLAGHARLIN | 20 | 1 | Conservative [MW] |  |  | 41.9826 | 42.0636 | 42.1525 | 42.2384 | 42.3277 | 42.4211 | 42.521 | 42.6203 | 42.7261 | 42.8313 | 42.9437 | 43.0547 | 43.1683 | 43.2883 | 43.4068 | 43.5317 | 44.1392 | 44.7477
|  |  |  | Best View [MW] |  |  | 41.9826 | 42.0759 | 42.1687 | 42.2687 | 42.3681 | 42.4702 | 42.6109 | 42.7551 | 42.902 | 43.0547 | 43.2133 | 43.3776 | 43.5429 | 43.717 | 43.8952 | 44.0806 | 44.9886 | 45.8977
|  |  |  | Base Case [MW] |  |  | 41.9826 | 42.1175 | 42.2585 | 42.4014 | 42.5542 | 42.7129 | 42.8749 | 43.045 | 43.2226 | 43.4068 | 43.5975 | 43.7932 | 43.9978 | 44.2111 | 44.4267 | 44.6533 | 45.7571 | 46.8627
|  |  |  | Aggressive [MW] |  |  | 41.9826 | 42.1641 | 42.3604 | 42.5616 | 42.7753 | 42.9968 | 43.2033 | 43.4157 | 43.6379 | 43.8683 | 44.1091 | 44.361 | 44.6207 | 44.8921 | 45.174 | 45.4638 | 46.8918 | 48.3211
| MULLINGAR | 10 | 1 | Conservative [MW] |  |  | 22.5661 | 22.6244 | 22.6824 | 22.7419 | 22.801 | 22.8614 | 22.9882 | 23.1164 | 23.2505 | 23.3858 | 23.5266 | 23.6705 | 23.8195 | 23.971 | 24.1273 | 24.2879 | 25.0796 | 25.872
|  |  |  | Best View [MW] |  |  | 22.5661 | 22.642 | 22.7173 | 22.7937 | 22.8734 | 22.952 | 23.0978 | 23.2487 | 23.4042 | 23.5662 | 23.7303 | 23.9006 | 24.0764 | 24.258 | 24.4448 | 24.6359 | 25.5799 | 26.5247
|  |  |  | Base Case [MW] |  |  | 22.5661 | 22.7097 | 22.8605 | 23.014 | 23.174 | 23.3381 | 23.5016 | 23.669 | 23.8447 | 24.0236 | 24.2076 | 24.399 | 24.5946 | 24.7964 | 25.0042 | 25.2172 | 26.2682 | 27.3201
|  |  |  | Aggressive [MW] |  |  | 22.5661 | 22.7664 | 22.977 | 23.1947 | 23.4255 | 23.6663 | 23.8649 | 24.0718 | 24.2841 | 24.5035 | 24.732 | 24.9665 | 25.2081 | 25.4586 | 25.7148 | 25.9799 | 27.2816 | 28.5849
| NEW KILLINICK | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428 | 39.5428
| NEW MAYFIELD-RIVERSTOWN STATION | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 37.8926 | 38.3737 | 38.3737 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 37.8926 | 38.3737 | 38.3737 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 37.8926 | 38.3737 | 38.3737 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 37.8926 | 38.3737 | 38.3737 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503 | 38.8503
| NEW MONAGHAN | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339 | 41.0339
| NORTH CITY JUNCTION | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.2234 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.2234 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.2234 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.2234 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016 | 39.7016
| NORTH EAST CASHEL | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 24.7 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 24.7 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 24.7 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 24.7 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312 | 25.7312
| NORTH QUAYS | 10 | 1 | Conservative [MW] |  |  | 30.7267 | 30.8986 | 31.0722 | 31.2508 | 31.429 | 31.6077 | 31.772 | 31.9382 | 32.1061 | 32.2795 | 32.4481 | 32.6211 | 32.7976 | 32.9717 | 33.1474 | 33.318 | 34.1844 | 35.0499
|  |  |  | Best View [MW] |  |  | 30.7267 | 30.9251 | 31.1277 | 31.334 | 31.5471 | 31.7621 | 31.9434 | 32.1318 | 32.3206 | 32.5148 | 32.708 | 32.8997 | 33.0971 | 33.2886 | 33.4855 | 33.6796 | 34.6574 | 35.6347
|  |  |  | Base Case [MW] |  |  | 30.7267 | 30.9587 | 31.1957 | 31.4366 | 31.6802 | 31.9337 | 32.1394 | 32.3418 | 32.5495 | 32.761 | 32.9751 | 33.1843 | 33.3976 | 33.6087 | 33.8204 | 34.0303 | 35.0844 | 36.1382
|  |  |  | Aggressive [MW] |  |  | 30.7267 | 31.1208 | 31.5242 | 31.944 | 32.3775 | 32.8225 | 33.0248 | 33.2238 | 33.4267 | 33.63 | 33.8274 | 34.0265 | 34.2259 | 34.4187 | 34.6066 | 34.7928 | 35.7285 | 36.664
| NUTLEY LANE | 10 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 45.8014 | 47.286 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 45.8014 | 47.286 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6794 | 47.6814 | 47.6836
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 45.8014 | 47.286 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6786 | 47.6794 | 47.6794 | 47.6817 | 47.6839
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 45.8006 | 47.286 | 47.6786 | 47.6786 | 47.6786 | 47.6794 | 47.6794 | 47.6794 | 47.6794 | 47.6794 | 47.6794 | 47.6794 | 47.6794
| PELLETSTOWN | 10 | 1 | Conservative [MW] |  |  | 25.7346 | 25.8704 | 26.0124 | 26.1594 | 26.3105 | 26.4623 | 26.5531 | 26.6431 | 26.7375 | 26.8309 | 26.9282 | 27.025 | 27.125 | 27.2239 | 27.3261 | 27.427 | 27.935 | 28.4427
|  |  |  | Best View [MW] |  |  | 25.7346 | 25.8883 | 26.0414 | 26.2051 | 26.3701 | 26.5459 | 26.6504 | 26.7576 | 26.8627 | 26.974 | 27.0874 | 27.2028 | 27.3191 | 27.4367 | 27.5556 | 27.6794 | 28.2854 | 28.8922
|  |  |  | Base Case [MW] |  |  | 25.7346 | 25.9001 | 26.0751 | 26.2529 | 26.4378 | 26.6328 | 26.7514 | 26.874 | 26.9975 | 27.1213 | 27.2532 | 27.3842 | 27.5194 | 27.6573 | 27.7934 | 27.9367 | 28.6341 | 29.3327
|  |  |  | Aggressive [MW] |  |  | 25.7346 | 25.9378 | 26.1536 | 26.3763 | 26.608 | 26.8561 | 26.9643 | 27.0746 | 27.1906 | 27.308 | 27.423 | 27.5431 | 27.6681 | 27.7894 | 27.9151 | 28.0455 | 28.685 | 29.3252
| PEMBROKE | 10 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 42.8251 | 43.1251 | 43.4196 | 43.4196 | 43.4196 | 43.4196 | 43.4196 | 43.4196 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 42.8251 | 43.1251 | 43.4196 | 43.4196 | 43.4196 | 43.4196 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 42.8251 | 43.1251 | 43.4196 | 43.4196 | 43.4196 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 42.8251 | 43.1251 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189 | 43.4189
| POPPINTREE | 10 | 1 | Conservative [MW] |  |  | 19.6301 | 19.849 | 20.0741 | 20.3042 | 20.5399 | 20.7829 | 20.9221 | 21.0623 | 21.2053 | 21.3507 | 21.4964 | 21.6427 | 21.7927 | 21.9428 | 22.0944 | 22.2473 | 23.0084 | 23.7698
|  |  |  | Best View [MW] |  |  | 19.6301 | 19.8723 | 20.1215 | 20.376 | 20.6398 | 20.9087 | 21.0698 | 21.2343 | 21.4004 | 21.5676 | 21.7378 | 21.9086 | 22.082 | 22.2573 | 22.4342 | 22.6124 | 23.4999 | 24.3876
|  |  |  | Base Case [MW] |  |  | 19.6301 | 19.8955 | 20.1697 | 20.4526 | 20.7431 | 21.042 | 21.2257 | 21.4115 | 21.6015 | 21.793 | 21.9857 | 22.1808 | 22.3787 | 22.5781 | 22.7796 | 22.9819 | 23.9914 | 25.001
|  |  |  | Aggressive [MW] |  |  | 19.6301 | 19.9561 | 20.2953 | 20.6469 | 21.0107 | 21.3859 | 21.5539 | 21.7226 | 21.8941 | 22.0681 | 22.2422 | 22.4181 | 22.5951 | 22.7724 | 22.9542 | 23.1347 | 24.0406 | 24.9463
|  | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 29.1919 | 29.1919 | 29.1919 | 29.1919 | 29.1919 | 29.1919 | 29.1919 | 29.1925 | 29.1925 | 29.1925 | 29.1932 | 29.1946 | 29.1962
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 29.1919 | 29.1919 | 29.1919 | 29.1919 | 29.1919 | 29.1925 | 29.1925 | 29.1925 | 29.1932 | 29.1932 | 29.1932 | 29.1932 | 29.1932
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 29.1919 | 29.1925 | 29.1919 | 29.1919 | 29.1925 | 29.1925 | 29.1925 | 29.1932 | 29.1932 | 29.1938 | 29.1938 | 29.1955 | 29.1971
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 29.1925 | 29.1925 | 29.1925 | 29.1925 | 29.1925 | 29.1932 | 29.1932 | 29.1932 | 29.1938 | 29.1938 | 29.1944 | 29.1959 | 29.1975
| POTTERY ROAD | 10 | 1 | Conservative [MW] |  |  | 28.4936 | 28.6404 | 28.7922 | 28.949 | 29.1057 | 29.2666 | 29.3954 | 29.5203 | 29.6493 | 29.7779 | 29.9105 | 30.1059 | 30.325 | 30.5426 | 30.7681 | 31.0018 | 32.1484 | 33.2963
|  |  |  | Best View [MW] |  |  | 28.4936 | 28.6638 | 28.8428 | 29.023 | 29.2068 | 29.394 | 29.5419 | 29.695 | 29.8488 | 30.0419 | 30.2927 | 30.5497 | 30.8117 | 31.0844 | 31.3615 | 31.6491 | 33.0592 | 34.4711
|  |  |  | Base Case [MW] |  |  | 28.4936 | 28.6868 | 28.885 | 29.0876 | 29.298 | 29.5152 | 29.6806 | 29.8523 | 30.0788 | 30.3618 | 30.6537 | 30.9483 | 31.2552 | 31.5753 | 31.8969 | 32.237 | 33.8881 | 35.5424
|  |  |  | Aggressive [MW] |  |  | 28.4936 | 28.7766 | 29.0679 | 29.3722 | 29.6871 | 30.0507 | 30.3195 | 30.5906 | 30.8735 | 31.1614 | 31.4526 | 31.7577 | 32.0718 | 32.3891 | 32.7197 | 33.0577 | 34.728 | 36.3995
| RINGSEND | 10 | 1 | Conservative [MW] |  |  | 29.8539 | 29.9956 | 30.143 | 30.2924 | 30.4425 | 30.6002 | 30.7382 | 30.8829 | 31.0304 | 31.1746 | 31.329 | 31.4797 | 31.6393 | 31.7943 | 31.9573 | 32.1193 | 32.9321 | 33.7446
|  |  |  | Best View [MW] |  |  | 29.8539 | 30.0193 | 30.1911 | 30.3637 | 30.5463 | 30.727 | 30.8883 | 31.0492 | 31.2179 | 31.3848 | 31.5573 | 31.7315 | 31.911 | 32.0899 | 32.2724 | 32.4578 | 33.3769 | 34.2966
|  |  |  | Base Case [MW] |  |  | 29.8539 | 30.0481 | 30.2476 | 30.4516 | 30.6624 | 30.8787 | 31.0563 | 31.2347 | 31.4174 | 31.6075 | 31.7959 | 31.99 | 32.1889 | 32.3878 | 32.5948 | 32.7985 | 33.8259 | 34.8528
|  |  |  | Aggressive [MW] |  |  | 29.8539 | 30.181 | 30.5254 | 30.89 | 31.2644 | 31.6608 | 31.8429 | 32.0289 | 32.2167 | 32.4065 | 32.6014 | 32.7964 | 32.9939 | 33.1929 | 33.3934 | 33.5931 | 34.594 | 35.5947
| SALTHILL | 10 | 1 | Conservative [MW] |  |  | 41.4085 | 41.5449 | 41.6792 | 41.8197 | 41.9631 | 42.1032 | 42.2998 | 42.4968 | 42.7009 | 42.9043 | 43.1155 | 43.3292 | 43.5443 | 43.7651 | 43.987 | 44.2134 | 45.3333 | 46.4541
|  |  |  | Best View [MW] |  |  | 41.4085 | 41.5794 | 41.7529 | 41.9247 | 42.1032 | 42.2883 | 42.5663 | 42.8517 | 43.1442 | 43.446 | 43.7515 | 44.0637 | 44.3848 | 44.7098 | 45.0407 | 45.3806 | 47.0562 | 48.7332
|  |  |  | Base Case [MW] |  |  | 41.4085 | 41.6231 | 41.8422 | 42.071 | 42.299 | 42.5353 | 42.8479 | 43.1652 | 43.4954 | 43.8275 | 44.1723 | 44.524 | 44.8808 | 45.2472 | 45.6179 | 45.9945 | 47.8618 | 49.73
|  |  |  | Aggressive [MW] |  |  | 41.4085 | 41.7454 | 42.0949 | 42.4566 | 42.8342 | 43.219 | 43.5949 | 43.9824 | 44.3777 | 44.7869 | 45.2028 | 45.6255 | 46.0591 | 46.4952 | 46.9409 | 47.3838 | 49.6057 | 51.8272
| SINGLAND | 10 | 1 | Conservative [MW] |  |  | 26.1586 | 26.2341 | 26.311 | 26.3924 | 26.4741 | 26.5562 | 26.6491 | 26.7448 | 26.8444 | 26.9426 | 27.044 | 27.1477 | 27.2546 | 27.3589 | 27.4705 | 27.5837 | 28.1455 | 28.7076
|  |  |  | Best View [MW] |  |  | 26.1586 | 26.2347 | 26.3158 | 26.3972 | 26.4831 | 26.5647 | 26.6949 | 26.824 | 26.9603 | 27.099 | 27.2402 | 27.3825 | 27.5312 | 27.6841 | 27.842 | 27.9997 | 28.7889 | 29.5781
|  |  |  | Base Case [MW] |  |  | 26.1586 | 26.2646 | 26.376 | 26.4932 | 26.6105 | 26.7285 | 26.8825 | 27.0357 | 27.1968 | 27.3604 | 27.5307 | 27.7063 | 27.8866 | 28.071 | 28.2628 | 28.4571 | 29.4221 | 30.3874
|  |  |  | Aggressive [MW] |  |  | 26.1586 | 26.3333 | 26.5181 | 26.7085 | 26.9076 | 27.113 | 27.2911 | 27.4767 | 27.6659 | 27.857 | 28.0618 | 28.2662 | 28.478 | 28.6964 | 28.9191 | 29.1498 | 30.2821 | 31.4157
| SORNE HILL | 20 | 1 | Conservative [MW] |  |  | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112
|  |  |  | Best View [MW] |  |  | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112
|  |  |  | Base Case [MW] |  |  | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112
|  |  |  | Aggressive [MW] |  |  | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112 | 5.8112
|  |  | 2 | Conservative [MW] |  |  | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316
|  |  |  | Best View [MW] |  |  | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316
|  |  |  | Base Case [MW] |  |  | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316
|  |  |  | Aggressive [MW] |  |  | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316 | 31.2316
| SOUTH EAST CARLOW | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.5428 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.5428 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.5428 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.5428 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601 | 39.8601
| SOUTH NAVAN | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.5428 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.5428 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.5428 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9025 | 39.5428 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176 | 40.176
| STEEVENS LANE | 10 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 38.9025 | 50.146 | 50.146 | 50.146 | 50.146 | 50.145 | 50.145 | 50.145 | 50.1441 | 50.1441 | 50.1441 | 50.1431 | 50.1409 | 50.1385
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 38.9025 | 50.146 | 50.146 | 50.146 | 50.145 | 50.145 | 50.145 | 50.1441 | 50.1441 | 50.1441 | 50.1431 | 50.1431 | 50.1406 | 50.1382
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 38.9025 | 50.146 | 50.146 | 50.145 | 50.145 | 50.145 | 50.1441 | 50.1441 | 50.1431 | 50.1431 | 50.1431 | 50.1431 | 50.1431 | 50.1431
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 38.9025 | 50.1441 | 50.1441 | 50.1441 | 50.1431 | 50.1431 | 50.1431 | 50.1431 | 50.1431 | 50.1431 | 50.1431 | 50.1441 | 50.1463 | 50.1487
| STEPHENSTOWN | 10 | 1 | Conservative [MW] |  |  | 24.3745 | 24.5016 | 24.6275 | 25.4396 | 25.5966 | 25.7569 | 25.852 | 25.9473 | 26.0417 | 26.1392 | 26.2399 | 26.3438 | 26.4466 | 26.5483 | 26.6567 | 26.7633 | 27.3013 | 27.839
|  |  |  | Best View [MW] |  |  | 24.3745 | 24.514 | 24.6553 | 25.4834 | 25.6608 | 25.8417 | 25.9493 | 26.0631 | 26.1747 | 26.2915 | 26.4059 | 26.5259 | 26.6461 | 26.7718 | 26.8981 | 27.0244 | 27.6558 | 28.2872
|  |  |  | Base Case [MW] |  |  | 24.3745 | 24.5255 | 24.6837 | 25.538 | 25.7316 | 25.9304 | 26.0575 | 26.1849 | 26.312 | 26.4472 | 26.5813 | 26.7186 | 26.8589 | 27.0011 | 27.1456 | 27.2917 | 28.018 | 28.7446
|  |  |  | Aggressive [MW] |  |  | 24.3745 | 24.5599 | 24.7528 | 25.666 | 25.9089 | 26.1651 | 26.2787 | 26.3985 | 26.5154 | 26.6374 | 26.7599 | 26.8831 | 27.0106 | 27.1423 | 27.27 | 27.4051 | 28.0608 | 28.7178
| TANEY | 10 | 1 | Conservative [MW] |  |  | 26.2898 | 26.3509 | 26.4126 | 26.4794 | 26.5424 | 26.6104 | 26.6624 | 26.7163 | 26.7719 | 26.8294 | 26.8845 | 26.9451 | 27.0033 | 27.0631 | 27.1282 | 27.191 | 27.5112 | 27.8309
|  |  |  | Best View [MW] |  |  | 26.2898 | 26.3633 | 26.4322 | 26.5091 | 26.5852 | 26.6649 | 26.7273 | 26.7908 | 26.8593 | 26.9244 | 26.9941 | 27.0647 | 27.1398 | 27.215 | 27.2908 | 27.3665 | 27.7452 | 28.1239
|  |  |  | Base Case [MW] |  |  | 26.2898 | 26.3689 | 26.4507 | 26.5347 | 26.6247 | 26.7131 | 26.7843 | 26.8591 | 26.9345 | 27.0138 | 27.0923 | 27.1748 | 27.2608 | 27.3498 | 27.4378 | 27.5288 | 27.9758 | 28.4234
|  |  |  | Aggressive [MW] |  |  | 26.2898 | 26.4057 | 26.5257 | 26.6539 | 26.7889 | 26.9302 | 27.0013 | 27.0768 | 27.1563 | 27.2319 | 27.315 | 27.398 | 27.4846 | 27.5701 | 27.6596 | 27.7516 | 28.2047 | 28.6582
| TRABEG | 10 | 1 | Conservative [MW] |  |  | 26.5321 | 26.6448 | 26.7548 | 26.8718 | 26.9903 | 27.1103 | 27.2293 | 27.3534 | 27.4795 | 27.6064 | 27.7339 | 27.8665 | 28.0035 | 28.141 | 28.2784 | 28.4239 | 29.1298 | 29.8371
|  |  |  | Best View [MW] |  |  | 26.5321 | 26.6488 | 26.7672 | 26.8908 | 27.0153 | 27.145 | 27.308 | 27.4755 | 27.6464 | 27.8204 | 28.0008 | 28.188 | 28.3762 | 28.5697 | 28.7665 | 28.9722 | 29.9769 | 30.9831
|  |  |  | Base Case [MW] |  |  | 26.5321 | 26.6907 | 26.8574 | 27.027 | 27.2039 | 27.3869 | 27.5552 | 27.7269 | 27.9061 | 28.091 | 28.2781 | 28.47 | 28.6666 | 28.8669 | 29.0742 | 29.2836 | 30.325 | 31.3668
|  |  |  | Aggressive [MW] |  |  | 26.5321 | 26.7332 | 26.9396 | 27.1536 | 27.3744 | 27.6056 | 27.8293 | 28.0587 | 28.2979 | 28.5449 | 28.794 | 29.0575 | 29.3238 | 29.5956 | 29.8765 | 30.1687 | 31.5996 | 33.0324
| TRINITY | 10 | 1 | Conservative [MW] |  |  | 30.2346 | 30.3896 | 30.5454 | 30.7053 | 30.864 | 31.0298 | 31.1795 | 31.33 | 31.4856 | 31.6412 | 31.801 | 31.9645 | 32.1261 | 32.2949 | 32.4616 | 32.6331 | 33.4778 | 34.3233
|  |  |  | Best View [MW] |  |  | 30.2346 | 30.4122 | 30.5941 | 30.784 | 30.9724 | 31.1671 | 31.3385 | 31.5078 | 31.6827 | 31.8623 | 32.0419 | 32.2259 | 32.412 | 32.6046 | 32.7935 | 32.9878 | 33.9449 | 34.9029
|  |  |  | Base Case [MW] |  |  | 30.2346 | 30.4435 | 30.6544 | 30.8717 | 31.0974 | 31.3265 | 31.5137 | 31.703 | 31.8982 | 32.095 | 32.2959 | 32.5004 | 32.7069 | 32.9144 | 33.1252 | 33.3346 | 34.3851 | 35.4354
|  |  |  | Aggressive [MW] |  |  | 30.2346 | 30.5864 | 30.9521 | 31.3346 | 31.7362 | 32.1497 | 32.3424 | 32.5363 | 32.7345 | 32.9312 | 33.134 | 33.3332 | 33.5378 | 33.7411 | 33.9452 | 34.1502 | 35.173 | 36.1959
| WEST PORTLAOISE | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043 | 38.9043
| WEXFORD | 20 | 1 | Conservative [MW] |  |  | 24.1841 | 24.2215 | 24.2624 | 24.3022 | 24.3406 | 24.3825 | 24.4798 | 24.5796 | 24.6813 | 24.7854 | 24.895 | 25.0064 | 25.1191 | 25.2367 | 25.3597 | 25.4827 | 26.0978 | 26.7128
|  |  |  | Best View [MW] |  |  | 24.1841 | 24.251 | 24.3234 | 24.3928 | 24.4667 | 24.5416 | 24.6505 | 24.7644 | 24.8831 | 25.0022 | 25.1255 | 25.2527 | 25.3877 | 25.5212 | 25.662 | 25.8053 | 26.515 | 27.2251
|  |  |  | Base Case [MW] |  |  | 24.1841 | 24.2684 | 24.3521 | 24.4434 | 24.5341 | 24.6278 | 24.7519 | 24.8789 | 25.0133 | 25.15 | 25.2892 | 25.4379 | 25.5875 | 25.7421 | 25.9011 | 26.0681 | 26.8819 | 27.697
|  |  |  | Aggressive [MW] |  |  | 24.1841 | 24.3144 | 24.4537 | 24.5974 | 24.745 | 24.904 | 25.085 | 25.2797 | 25.4827 | 25.6929 | 25.9136 | 26.143 | 26.3835 | 26.6292 | 26.8912 | 27.1591 | 28.483 | 29.8079
| WOLFE TONE STREET | 10 | 1 | Conservative [MW] |  |  | 30.986 | 31.1609 | 31.3431 | 31.5279 | 31.7132 | 31.906 | 32.0762 | 31.6673 | 31.8494 | 32.0297 | 32.2159 | 32.4043 | 32.5924 | 32.7856 | 32.9779 | 33.1736 | 34.1431 | 35.1131
|  |  |  | Best View [MW] |  |  | 30.986 | 31.1909 | 31.4022 | 31.6184 | 31.8394 | 32.0641 | 32.2612 | 31.8744 | 32.0787 | 32.2858 | 32.4941 | 32.7074 | 32.9205 | 33.1413 | 33.3599 | 33.5841 | 34.6902 | 35.7973
|  |  |  | Base Case [MW] |  |  | 30.986 | 31.224 | 31.4696 | 31.7222 | 31.9789 | 32.2494 | 32.4652 | 32.0992 | 32.3278 | 32.5539 | 32.785 | 33.0249 | 33.2628 | 33.5031 | 33.748 | 33.9961 | 35.2279 | 36.4604
|  |  |  | Aggressive [MW] |  |  | 30.986 | 31.3888 | 31.8135 | 32.2605 | 32.7215 | 33.2027 | 33.4239 | 33.0649 | 33.2949 | 33.5241 | 33.7569 | 33.9915 | 34.2306 | 34.4638 | 34.703 | 34.9426 | 36.1396 | 37.3367
| YELLOWMEADOWS | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182 | 40.0182
38 kV - MV | ABBEYFEALE | 10 | 1 | Conservative [MW] |  |  | 3.973 | 3.989 | 4.0061 | 4.0243 | 4.0416 | 4.0599 | 4.0806 | 4.1002 | 4.1205 | 4.1417 | 4.1616 | 4.1842 | 4.2054 | 4.2273 | 4.2498 | 4.2728 | 4.3865 | 4.5003
|  |  |  | Best View [MW] |  |  | 3.973 | 3.9896 | 4.0091 | 4.0258 | 4.0454 | 4.0641 | 4.0905 | 4.1169 | 4.1451 | 4.1731 | 4.2027 | 4.2319 | 4.2605 | 4.2926 | 4.3218 | 4.3541 | 4.5074 | 4.6611
|  |  |  | Base Case [MW] |  |  | 3.973 | 3.9962 | 4.0198 | 4.0437 | 4.0697 | 4.094 | 4.1258 | 4.1568 | 4.1887 | 4.2216 | 4.2573 | 4.2914 | 4.3259 | 4.3628 | 4.3995 | 4.4361 | 4.6193 | 4.8026
|  |  |  | Aggressive [MW] |  |  | 3.973 | 4.0092 | 4.0457 | 4.0841 | 4.1221 | 4.1634 | 4.1987 | 4.2342 | 4.2719 | 4.3094 | 4.3486 | 4.387 | 4.4289 | 4.4694 | 4.5104 | 4.554 | 4.765 | 4.9764
|  | 20 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.024776 | 0.060048 | 0.095918 | 0.1324 | 0.16946 | 0.20724 | 0.24552 | 0.28453 | 0.32389 | 0.51976 | 0.71568
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.0082345 | 0.054974 | 0.10268 | 0.15159 | 0.20164 | 0.2527 | 0.30463 | 0.35766 | 0.41162 | 0.46677 | 0.73936 | 1.0122
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.015111 | 0.068633 | 0.12353 | 0.17987 | 0.23764 | 0.29684 | 0.35721 | 0.41884 | 0.48185 | 0.54608 | 0.6116 | 0.93574 | 1.2601
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.062068 | 0.13408 | 0.19539 | 0.25848 | 0.323 | 0.38908 | 0.45668 | 0.52579 | 0.59628 | 0.66815 | 0.7427 | 0.82017 | 1.1997 | 1.5798
| ABBEYLAND | 10 | 1 | Conservative [MW] |  |  | 12.3906 | 12.4364 | 12.4839 | 12.5332 | 12.5845 | 12.6371 | 12.7033 | 11.9782 | 12.0484 | 12.1219 | 12.1952 | 12.2715 | 12.3507 | 12.4292 | 12.5103 | 12.5937 | 13.0046 | 13.4159
|  |  |  | Best View [MW] |  |  | 12.3906 | 12.4448 | 12.5038 | 12.5598 | 12.6206 | 12.6819 | 12.7687 | 12.0624 | 12.1523 | 12.2465 | 12.345 | 12.4439 | 12.5464 | 12.6489 | 12.7575 | 12.8687 | 13.4177 | 13.9672
|  |  |  | Base Case [MW] |  |  | 12.3906 | 12.4669 | 12.5491 | 12.633 | 12.7183 | 12.8087 | 12.9149 | 12.2297 | 12.344 | 12.463 | 12.5829 | 12.7067 | 12.8372 | 12.9701 | 13.1084 | 13.2479 | 13.9424 | 14.6371
|  |  |  | Aggressive [MW] |  |  | 12.3906 | 12.4954 | 12.6091 | 12.723 | 12.844 | 12.972 | 13.1107 | 12.4684 | 12.6239 | 12.7836 | 12.9499 | 13.1251 | 13.3037 | 13.4917 | 13.683 | 13.8833 | 14.8608 | 15.8399
| ABBEYLEIX | 20 | 1 | Conservative [MW] |  |  | 3.2927 | 3.3056 | 3.3182 | 3.3306 | 3.3427 | 3.3559 | 3.3746 | 3.394 | 3.4128 | 3.4324 | 3.4526 | 3.4736 | 3.4952 | 3.516 | 3.5373 | 3.5607 | 3.6724 | 3.7844
|  |  |  | Best View [MW] |  |  | 3.2927 | 3.3084 | 3.3237 | 3.3387 | 3.3545 | 3.3713 | 3.3953 | 3.4196 | 3.4457 | 3.4706 | 3.4971 | 3.5251 | 3.5533 | 3.5814 | 3.6108 | 3.6416 | 3.7919 | 3.9424
|  |  |  | Base Case [MW] |  |  | 3.2927 | 3.312 | 3.3307 | 3.3489 | 3.3691 | 3.39 | 3.4184 | 3.4481 | 3.479 | 3.511 | 3.5426 | 3.5765 | 3.6112 | 3.6466 | 3.6825 | 3.7203 | 3.9041 | 4.0882
|  |  |  | Aggressive [MW] |  |  | 3.2927 | 3.3223 | 3.3518 | 3.3837 | 3.4167 | 3.4492 | 3.4897 | 3.5301 | 3.5731 | 3.6186 | 3.6646 | 3.7123 | 3.7615 | 3.8118 | 3.8642 | 3.9184 | 4.1849 | 4.4516
| ACADEMY STREET | 10 | 1 | Conservative [MW] |  |  | 8.2016 | 8.2372 | 8.2728 | 8.3083 | 8.3461 | 8.3836 | 8.431 | 8.4809 | 8.5308 | 8.5828 | 8.6367 | 8.6902 | 8.7426 | 8.7989 | 8.8539 | 8.9121 | 9.1944 | 9.4772
|  |  |  | Best View [MW] |  |  | 8.2016 | 8.2441 | 8.2858 | 8.3288 | 8.3729 | 8.4157 | 8.4771 | 8.5405 | 8.6057 | 8.6722 | 8.7396 | 8.8098 | 8.8777 | 8.9498 | 9.0211 | 9.0957 | 9.4598 | 9.8244
|  |  |  | Base Case [MW] |  |  | 8.2016 | 8.2609 | 8.3208 | 8.3809 | 8.4432 | 8.5073 | 8.5837 | 8.6609 | 8.7404 | 8.8218 | 8.9041 | 8.9894 | 9.0737 | 9.1612 | 9.2482 | 9.3364 | 9.7744 | 10.2126
|  |  |  | Aggressive [MW] |  |  | 8.2016 | 8.2816 | 8.3614 | 8.4469 | 8.5352 | 8.6254 | 8.7243 | 8.8269 | 8.9321 | 9.0383 | 9.1479 | 9.2589 | 9.3698 | 9.4836 | 9.5938 | 9.7047 | 10.2573 | 10.8101
|  | 20 | 1 | Conservative [MW] |  |  | 5.0991 | 5.1445 | 5.1901 | 5.2361 | 5.2822 | 5.3284 | 4.6714 | 4.7475 | 4.8245 | 4.9022 | 4.9804 | 5.0591 | 5.1381 | 5.2172 | 5.2962 | 5.3745 | 5.768 | 6.1614
|  |  |  | Best View [MW] |  |  | 5.0991 | 5.1526 | 5.2065 | 5.2608 | 5.3153 | 5.3699 | 4.7432 | 4.8393 | 4.9364 | 5.0344 | 5.1328 | 5.2315 | 5.3299 | 5.4272 | 5.523 | 5.6166 | 6.0907 | 6.5644
|  |  |  | Base Case [MW] |  |  | 5.0991 | 5.1743 | 5.2502 | 5.3266 | 5.4034 | 5.4801 | 4.903 | 5.0178 | 5.1336 | 5.2496 | 5.3649 | 5.4786 | 5.5897 | 5.697 | 5.7988 | 5.8929 | 6.384 | 6.8738
|  |  |  | Aggressive [MW] |  |  | 5.0991 | 5.2006 | 5.3034 | 5.4069 | 5.5102 | 5.6118 | 5.11 | 5.2568 | 5.4025 | 5.5452 | 5.6826 | 5.8115 | 5.9275 | 6.0259 | 6.0986 | 6.134 | 6.4104 | 6.6806
| ACHILL | 20 | 1 | Conservative [MW] |  |  | 4.1098 | 4.117 | 4.1218 | 4.1265 | 4.1334 | 4.1378 | 4.1588 | 4.1827 | 4.2048 | 4.2272 | 4.2502 | 4.2758 | 4.2992 | 4.3252 | 4.3489 | 4.375 | 4.4989 | 4.6233
|  |  |  | Best View [MW] |  |  | 4.1098 | 4.1221 | 4.1359 | 4.1493 | 4.1621 | 4.1742 | 4.2021 | 4.2319 | 4.2589 | 4.2898 | 4.3198 | 4.3511 | 4.3813 | 4.4149 | 4.447 | 4.4798 | 4.6418 | 4.804
|  |  |  | Base Case [MW] |  |  | 4.1098 | 4.1289 | 4.1469 | 4.1658 | 4.1857 | 4.2044 | 4.2394 | 4.2747 | 4.3102 | 4.3457 | 4.3855 | 4.4247 | 4.4629 | 4.5047 | 4.5448 | 4.5876 | 4.7942 | 5.0013
|  |  |  | Aggressive [MW] |  |  | 4.1098 | 4.1466 | 4.1852 | 4.2255 | 4.2646 | 4.307 | 4.3573 | 4.4082 | 4.4587 | 4.5132 | 4.5683 | 4.6252 | 4.6808 | 4.7389 | 4.7959 | 4.8555 | 5.1467 | 5.4382
| AGHAGAD | 10 | 1 | Conservative [MW] |  |  | 5.8287 | 5.8406 | 5.8483 | 5.8597 | 5.8669 | 5.8779 | 5.8967 | 5.9189 | 5.94 | 5.9601 | 5.9792 | 6.0014 | 6.0224 | 6.0464 | 6.0693 | 6.0951 | 6.2164 | 6.3382
|  |  |  | Best View [MW] |  |  | 5.8287 | 5.8452 | 5.8609 | 5.8799 | 5.8982 | 5.9158 | 5.9416 | 5.9699 | 5.9962 | 6.0289 | 6.0597 | 6.0884 | 6.1232 | 6.1557 | 6.1901 | 6.2219 | 6.388 | 6.5536
|  |  |  | Base Case [MW] |  |  | 5.8287 | 5.8523 | 5.8746 | 5.8957 | 5.9195 | 5.942 | 5.9776 | 6.0107 | 6.0451 | 6.0809 | 6.1179 | 6.1602 | 6.1992 | 6.2389 | 6.2834 | 6.3285 | 6.5523 | 6.7761
|  |  |  | Aggressive [MW] |  |  | 5.8287 | 5.8643 | 5.8969 | 5.9346 | 5.973 | 6.0123 | 6.0575 | 6.1021 | 6.1545 | 6.2056 | 6.2598 | 6.3121 | 6.3707 | 6.431 | 6.4971 | 6.564 | 6.8964 | 7.2289
| AGHAMORE | 10 | 1 | Conservative [MW] |  |  | 3.906 | 3.9151 | 3.924 | 3.9326 | 3.941 | 3.9491 | 3.9708 | 3.9911 | 4.0119 | 4.0357 | 4.0578 | 4.0804 | 4.1034 | 4.1268 | 4.1504 | 4.1767 | 4.3012 | 4.4262
|  |  |  | Best View [MW] |  |  | 3.906 | 3.9225 | 3.9401 | 3.9568 | 3.9746 | 3.9935 | 4.0182 | 4.0452 | 4.0721 | 4.0986 | 4.1271 | 4.1552 | 4.1827 | 4.2142 | 4.2424 | 4.2745 | 4.4244 | 4.575
|  |  |  | Base Case [MW] |  |  | 3.906 | 3.9266 | 3.9457 | 3.9679 | 3.9885 | 4.0099 | 4.0422 | 4.0731 | 4.107 | 4.1437 | 4.1785 | 4.2155 | 4.2524 | 4.2911 | 4.3291 | 4.3683 | 4.5611 | 4.754
|  |  |  | Aggressive [MW] |  |  | 3.906 | 3.9384 | 3.9716 | 4.0054 | 4.0397 | 4.0763 | 4.1166 | 4.16 | 4.2034 | 4.2491 | 4.2964 | 4.3449 | 4.3939 | 4.4454 | 4.4961 | 4.5475 | 4.8026 | 5.0579
| ARDFINNAN | 10 | 1 | Conservative [MW] |  |  | 0.74646 | 0.74846 | 0.75055 | 0.75268 | 0.75482 | 0.757 | 0.76 | 0.763 | 0.76614 | 0.76923 | 0.77255 | 0.77587 | 0.77924 | 0.78274 | 0.78634 | 0.79004 | 0.80825 | 0.82648
|  |  |  | Best View [MW] |  |  | 0.74646 | 0.74877 | 0.75109 | 0.7535 | 0.75595 | 0.75845 | 0.76254 | 0.76677 | 0.77114 | 0.77569 | 0.78033 | 0.78521 | 0.79022 | 0.79536 | 0.8007 | 0.80626 | 0.83348 | 0.86074
|  |  |  | Base Case [MW] |  |  | 0.74646 | 0.7495 | 0.75263 | 0.75582 | 0.75913 | 0.76254 | 0.76714 | 0.77191 | 0.77683 | 0.78192 | 0.78725 | 0.79277 | 0.79851 | 0.80444 | 0.81061 | 0.817 | 0.84835 | 0.87974
|  |  |  | Aggressive [MW] |  |  | 0.74646 | 0.75118 | 0.75613 | 0.76136 | 0.76673 | 0.77237 | 0.77796 | 0.78375 | 0.78971 | 0.79596 | 0.80248 | 0.80928 | 0.81631 | 0.82366 | 0.83135 | 0.83931 | 0.87837 | 0.91749
|  | 20 | 1 | Conservative [MW] |  |  | 3.6774 | 3.6922 | 3.7064 | 3.7219 | 3.7367 | 3.7528 | 3.7719 | 3.7939 | 3.8145 | 3.8357 | 3.8598 | 3.8823 | 3.903 | 3.9264 | 3.9502 | 3.9745 | 4.0947 | 4.215
|  |  |  | Best View [MW] |  |  | 3.6774 | 3.6944 | 3.7106 | 3.7279 | 3.7442 | 3.7618 | 3.7903 | 3.8203 | 3.8498 | 3.8807 | 3.9107 | 3.9441 | 3.9762 | 4.0092 | 4.0429 | 4.0771 | 4.2466 | 4.4162
|  |  |  | Base Case [MW] |  |  | 3.6774 | 3.6998 | 3.7207 | 3.7442 | 3.7681 | 3.7903 | 3.8231 | 3.8547 | 3.8872 | 3.9226 | 3.9563 | 3.9926 | 4.0289 | 4.0651 | 4.1031 | 4.143 | 4.3374 | 4.5321
|  |  |  | Aggressive [MW] |  |  | 3.6774 | 3.7112 | 3.7453 | 3.7818 | 3.8204 | 3.8587 | 3.8943 | 3.9341 | 3.9733 | 4.0118 | 4.0537 | 4.0965 | 4.1372 | 4.1829 | 4.2257 | 4.27 | 4.4876 | 4.7055
| ARDGEEHA | 10 | 1 | Conservative [MW] |  |  | 7.0991 | 7.141 | 7.1831 | 7.2262 | 7.2696 | 7.3142 | 7.3739 | 7.4341 | 7.4964 | 7.5599 | 7.6246 | 7.6905 | 7.7586 | 7.8268 | 7.8972 | 7.9687 | 8.3232 | 8.6779
|  |  |  | Best View [MW] |  |  | 7.0991 | 7.1466 | 7.1944 | 7.2434 | 7.2926 | 7.3438 | 7.4255 | 7.5105 | 7.5979 | 7.6875 | 7.7795 | 7.875 | 7.9725 | 8.0723 | 8.1752 | 8.2813 | 8.8032 | 9.3256
|  |  |  | Base Case [MW] |  |  | 7.0991 | 7.1613 | 7.2249 | 7.2898 | 7.357 | 7.4255 | 7.5176 | 7.6121 | 7.7101 | 7.8114 | 7.9151 | 8.0231 | 8.1333 | 8.2465 | 8.3639 | 8.4842 | 9.0779 | 9.6721
|  |  |  | Aggressive [MW] |  |  | 7.0991 | 7.1961 | 7.2968 | 7.4014 | 7.5104 | 7.6232 | 7.7324 | 7.8461 | 7.963 | 8.0845 | 8.2089 | 8.3386 | 8.4723 | 8.6099 | 8.7507 | 8.8962 | 9.6112 | 10.327
| ARDNAREE | 10 | 1 | Conservative [MW] |  |  | 7.1633 | 7.1681 | 7.1729 | 7.1775 | 7.1821 | 7.1866 | 7.2017 | 7.2163 | 7.2321 | 7.249 | 7.2654 | 7.2829 | 7.3015 | 7.3192 | 7.3381 | 7.3562 | 7.4487 | 7.5411
|  |  |  | Best View [MW] |  |  | 7.1633 | 7.1731 | 7.1845 | 7.1936 | 7.2044 | 7.2149 | 7.236 | 7.256 | 7.2768 | 7.3003 | 7.3225 | 7.3454 | 7.3688 | 7.3948 | 7.4192 | 7.4461 | 7.5739 | 7.7022
|  |  |  | Base Case [MW] |  |  | 7.1633 | 7.1775 | 7.1911 | 7.2041 | 7.2187 | 7.2344 | 7.2584 | 7.2826 | 7.3091 | 7.3378 | 7.3645 | 7.3951 | 7.4237 | 7.4561 | 7.4881 | 7.5217 | 7.6855 | 7.8496
|  |  |  | Aggressive [MW] |  |  | 7.1633 | 7.1893 | 7.2173 | 7.245 | 7.2744 | 7.3053 | 7.3397 | 7.3784 | 7.4177 | 7.4591 | 7.5027 | 7.5478 | 7.5944 | 7.6442 | 7.6969 | 7.7523 | 8.0223 | 8.2927
|  | 20 | 1 | Conservative [MW] |  |  | 7.423 | 7.43 | 7.4369 | 7.4437 | 7.4503 | 7.457 | 7.479 | 7.502 | 7.5238 | 7.5485 | 7.5719 | 7.5982 | 7.6231 | 7.6486 | 7.677 | 7.7038 | 7.8418 | 7.9797
|  |  |  | Best View [MW] |  |  | 7.423 | 7.4382 | 7.4529 | 7.4691 | 7.4847 | 7.4998 | 7.5276 | 7.5575 | 7.5895 | 7.6214 | 7.6534 | 7.6872 | 7.7208 | 7.7581 | 7.7949 | 7.8311 | 8.0139 | 8.1965
|  |  |  | Base Case [MW] |  |  | 7.423 | 7.4437 | 7.4635 | 7.4843 | 7.5044 | 7.5253 | 7.562 | 7.5979 | 7.6351 | 7.6754 | 7.7145 | 7.7566 | 7.7993 | 7.8446 | 7.8921 | 7.9397 | 8.1777 | 8.4156
|  |  |  | Aggressive [MW] |  |  | 7.423 | 7.461 | 7.5016 | 7.5407 | 7.5841 | 7.6278 | 7.68 | 7.7348 | 7.7898 | 7.849 | 7.9117 | 7.9755 | 8.0423 | 8.1133 | 8.186 | 8.2619 | 8.6329 | 9.0044
| ASHBOURNE | 20 | 1 | Conservative [MW] |  |  | 2.6051 | 2.7525 | 2.9027 | 3.056 | 3.2119 | 3.3706 | 3.4611 | 3.553 | 3.6442 | 3.7366 | 3.829 | 3.9219 | 4.015 | 4.1082 | 4.2035 | 4.2982 | 4.7733 | 5.2484
|  |  |  | Best View [MW] |  |  | 2.6051 | 2.7675 | 2.9339 | 3.1035 | 3.2767 | 3.4527 | 3.5575 | 3.6626 | 3.7679 | 3.8739 | 3.9806 | 4.087 | 4.1955 | 4.3045 | 4.4135 | 4.52 | 5.059 | 5.5976
|  |  |  | Base Case [MW] |  |  | 2.6051 | 2.7838 | 2.9666 | 3.154 | 3.3451 | 3.5397 | 3.6577 | 3.7759 | 3.8951 | 4.0145 | 4.1353 | 4.2574 | 4.3795 | 4.4997 | 4.6188 | 4.7361 | 5.3273 | 5.9182
|  |  |  | Aggressive [MW] |  |  | 2.6051 | 2.8243 | 3.0501 | 3.2819 | 3.5192 | 3.7595 | 3.8671 | 3.9715 | 4.0776 | 4.1862 | 4.2949 | 4.4031 | 4.5096 | 4.6152 | 4.7196 | 4.8226 | 5.3414 | 5.8599
| ATHBOY | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.010726 | 0.040645 | 0.071344 | 0.10284 | 0.13505 | 0.16804 | 0.20179 | 0.36851 | 0.53535
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.014669 | 0.048875 | 0.0841 | 0.12025 | 0.15743 | 0.19561 | 0.23472 | 0.27486 | 0.4728 | 0.67091
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.00015863 | 0.035083 | 0.071049 | 0.10798 | 0.14594 | 0.18498 | 0.22508 | 0.26619 | 0.30824 | 0.35109 | 0.39478 | 0.61099 | 0.82734
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.018763 | 0.070196 | 0.11247 | 0.15604 | 0.20092 | 0.24716 | 0.29471 | 0.34324 | 0.39289 | 0.44391 | 0.49614 | 0.54924 | 0.81241 | 1.0757
|  | 20 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| ATHENRY | 10 | 1 | Conservative [MW] |  |  | 6.2275 | 6.2487 | 6.269 | 6.2886 | 6.3074 | 6.3311 | 6.3657 | 6.4024 | 6.4409 | 6.4767 | 6.5189 | 6.5581 | 6.5988 | 6.6413 | 6.6801 | 6.7252 | 6.9339 | 7.1436
|  |  |  | Best View [MW] |  |  | 6.2275 | 6.2551 | 6.2854 | 6.3141 | 6.3457 | 6.3769 | 6.4248 | 6.4767 | 6.5327 | 6.5878 | 6.6418 | 6.6989 | 6.7591 | 6.8172 | 6.8778 | 6.9404 | 7.2481 | 7.556
|  |  |  | Base Case [MW] |  |  | 6.2275 | 6.2664 | 6.3025 | 6.3403 | 6.3798 | 6.4222 | 6.4817 | 6.5394 | 6.5992 | 6.6657 | 6.7293 | 6.7938 | 6.8641 | 6.9348 | 7.005 | 7.0796 | 7.4409 | 7.8029
|  |  |  | Aggressive [MW] |  |  | 6.2275 | 6.2878 | 6.3538 | 6.4206 | 6.4925 | 6.5612 | 6.6387 | 6.7142 | 6.7968 | 6.8809 | 6.9656 | 7.0501 | 7.1383 | 7.2339 | 7.3262 | 7.4184 | 7.8796 | 8.3407
|  | 20 | 1 | Conservative [MW] |  |  | 7.7661 | 7.7858 | 7.8026 | 7.8232 | 7.8408 | 7.861 | 7.102 | 7.1376 | 7.172 | 7.208 | 7.2456 | 7.2819 | 7.3212 | 7.3591 | 7.4 | 7.4406 | 7.6445 | 7.8483
|  |  |  | Best View [MW] |  |  | 7.7661 | 7.7923 | 7.8192 | 7.8471 | 7.8756 | 7.9039 | 7.1588 | 7.208 | 7.2577 | 7.3093 | 7.3627 | 7.4162 | 7.4728 | 7.529 | 7.5881 | 7.6481 | 7.9457 | 8.2434
|  |  |  | Base Case [MW] |  |  | 7.7661 | 7.8014 | 7.8365 | 7.8715 | 7.9086 | 7.9464 | 7.2091 | 7.2663 | 7.3233 | 7.3828 | 7.4446 | 7.5087 | 7.573 | 7.639 | 7.7081 | 7.7782 | 8.1263 | 8.4744
|  |  |  | Aggressive [MW] |  |  | 7.7661 | 7.8251 | 7.8841 | 7.9451 | 8.0097 | 8.0768 | 7.3585 | 7.4322 | 7.5093 | 7.588 | 7.6692 | 7.7525 | 7.839 | 7.9282 | 8.0193 | 8.1115 | 8.5694 | 9.0276
| ATHGARVAN | 10 | 1 | Conservative [MW] |  |  | 9.4921 | 9.5562 | 9.6218 | 9.6872 | 9.7537 | 8.6098 | 8.6946 | 8.7803 | 8.8669 | 8.9531 | 9.0405 | 9.1272 | 9.215 | 9.301 | 9.3874 | 9.4745 | 9.9082 | 10.342
|  |  |  | Best View [MW] |  |  | 9.4921 | 9.5734 | 9.6553 | 9.7385 | 9.8227 | 8.698 | 8.8093 | 8.9217 | 9.0337 | 9.146 | 9.2592 | 9.3702 | 9.4819 | 9.5912 | 9.6985 | 9.8036 | 10.3351 | 10.8661
|  |  |  | Base Case [MW] |  |  | 9.4921 | 9.5885 | 9.6872 | 9.786 | 9.8856 | 8.7787 | 8.9076 | 9.0383 | 9.1683 | 9.2991 | 9.4275 | 9.5562 | 9.6811 | 9.8015 | 9.9166 | 10.0262 | 10.589 | 11.1508
|  |  |  | Aggressive [MW] |  |  | 9.4921 | 9.6162 | 9.743 | 9.8706 | 9.9993 | 8.9238 | 9.0788 | 9.2343 | 9.3891 | 9.542 | 9.6914 | 9.8339 | 9.9681 | 10.0911 | 10.198 | 10.2862 | 10.7772 | 11.2651
| ATHLONE | 10 | 1 | Conservative [MW] |  |  | 14.7969 | 14.8542 | 14.9127 | 14.9719 | 15.0266 | 15.0872 | 15.1819 | 15.2753 | 15.3708 | 15.4685 | 15.5624 | 15.652 | 15.7481 | 15.8378 | 15.9332 | 16.0209 | 16.4801 | 16.9379
|  |  |  | Best View [MW] |  |  | 14.7969 | 14.8853 | 14.9742 | 15.0675 | 15.1549 | 15.247 | 15.3829 | 15.5134 | 15.6423 | 15.7728 | 15.9042 | 16.0279 | 16.1482 | 16.2614 | 16.3711 | 16.4667 | 16.9824 | 17.4957
|  |  |  | Base Case [MW] |  |  | 14.7969 | 14.9212 | 15.0509 | 15.1792 | 15.3059 | 15.4343 | 15.5749 | 15.7192 | 15.8545 | 15.9943 | 16.1252 | 16.249 | 16.3619 | 16.4728 | 16.5646 | 16.6377 | 17.0531 | 17.4654
|  |  |  | Aggressive [MW] |  |  | 14.7969 | 14.9873 | 15.1853 | 15.3771 | 15.5743 | 15.7664 | 15.9206 | 16.0656 | 16.2076 | 16.3358 | 16.4557 | 16.563 | 16.6446 | 16.7049 | 16.7261 | 16.7096 | 16.7277 | 16.7395
| BAGENALSTOWN | 20 | 1 | Conservative [MW] |  |  | 8.5862 | 8.6309 | 8.677 | 8.7228 | 8.7684 | 8.8168 | 8.8853 | 8.9565 | 9.03 | 9.1026 | 9.1778 | 9.2553 | 9.3336 | 9.4141 | 9.495 | 9.5782 | 9.9882 | 10.3985
|  |  |  | Best View [MW] |  |  | 8.5862 | 8.6407 | 8.6963 | 8.7532 | 8.8113 | 8.8689 | 8.9648 | 9.0625 | 9.162 | 9.2648 | 9.3708 | 9.4781 | 9.5882 | 9.7029 | 9.8182 | 9.9378 | 10.5243 | 11.1114
|  |  |  | Base Case [MW] |  |  | 8.5862 | 8.6519 | 8.7172 | 8.785 | 8.8538 | 8.9252 | 9.0395 | 9.1566 | 9.2781 | 9.4036 | 9.5312 | 9.6642 | 9.8004 | 9.9416 | 10.0852 | 10.2325 | 10.9593 | 11.6867
|  |  |  | Aggressive [MW] |  |  | 8.5862 | 8.6951 | 8.8057 | 8.9224 | 9.0421 | 9.1645 | 9.3139 | 9.4677 | 9.6271 | 9.7916 | 9.9626 | 10.1392 | 10.3206 | 10.5057 | 10.6978 | 10.8935 | 11.8623 | 12.8318
| BAILIEBORO | 10 | 1 | Conservative [MW] |  |  | 6.592 | 6.6199 | 6.6466 | 6.6762 | 6.7044 | 6.7353 | 6.7732 | 6.817 | 6.8577 | 6.904 | 6.947 | 6.9908 | 7.0354 | 7.0808 | 7.1318 | 7.1781 | 7.4221 | 7.6654
|  |  |  | Best View [MW] |  |  | 6.592 | 6.6281 | 6.6618 | 6.702 | 6.7398 | 6.7748 | 6.8343 | 6.892 | 6.9526 | 7.0111 | 7.0763 | 7.1388 | 7.2025 | 7.2675 | 7.338 | 7.4036 | 7.7447 | 8.0849
|  |  |  | Base Case [MW] |  |  | 6.592 | 6.6385 | 6.6814 | 6.7296 | 6.7735 | 6.8223 | 6.889 | 6.9524 | 7.0217 | 7.0868 | 7.1567 | 7.2313 | 7.3049 | 7.377 | 7.4571 | 7.5341 | 7.9272 | 8.3199
|  |  |  | Aggressive [MW] |  |  | 6.592 | 6.6603 | 6.7333 | 6.8056 | 6.8812 | 6.9597 | 7.04 | 7.1266 | 7.2087 | 7.3 | 7.3896 | 7.4816 | 7.5745 | 7.673 | 7.7699 | 7.8632 | 8.3392 | 8.8146
|  | 20 | 1 | Conservative [MW] |  |  | 1.0427 | 1.0425 | 1.0423 | 1.0421 | 1.042 | 1.0418 | 1.0416 | 1.0414 | 1.0412 | 1.0409 | 1.0407 | 1.0404 | 1.0402 | 1.0399 | 1.0396 | 1.0393 | 1.0379 | 1.0365
|  |  |  | Best View [MW] |  |  | 1.0427 | 1.0424 | 1.0423 | 1.042 | 1.0418 | 1.0416 | 1.0413 | 1.041 | 1.0406 | 1.0403 | 1.04 | 1.0396 | 1.0392 | 1.0389 | 1.0385 | 1.0382 | 1.0364 | 1.0347
|  |  |  | Base Case [MW] |  |  | 1.0427 | 1.0424 | 1.0421 | 1.0418 | 1.0416 | 1.0413 | 1.041 | 1.0406 | 1.0402 | 1.0399 | 1.0395 | 1.039 | 1.0386 | 1.0382 | 1.0378 | 1.0374 | 1.0352 | 1.0331
|  |  |  | Aggressive [MW] |  |  | 1.0427 | 1.0423 | 1.0418 | 1.0414 | 1.041 | 1.0406 | 1.0402 | 1.0396 | 1.0392 | 1.0388 | 1.0382 | 1.0378 | 1.0372 | 1.0367 | 1.0362 | 1.0358 | 1.0337 | 1.0316
| BALBRIGGAN | 10 | 1 | Conservative [MW] |  |  | 12.882 | 12.9076 | 12.9355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Best View [MW] |  |  | 12.882 | 12.9111 | 12.9421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Base Case [MW] |  |  | 12.882 | 12.9145 | 12.9483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Aggressive [MW] |  |  | 12.882 | 12.9226 | 12.9633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BALGADDY | 10 | 1 | Conservative [MW] |  |  | 13.4973 | 13.5909 | 13.6849 | 13.7788 | 13.8765 | 13.388 | 13.4476 | 13.5081 | 13.5699 | 13.6322 | 13.6955 | 13.7597 | 13.8244 | 13.89 | 13.9558 | 14.0221 | 14.3522 | 14.6824
|  |  |  | Best View [MW] |  |  | 13.4973 | 13.6005 | 13.7024 | 13.811 | 13.921 | 13.4432 | 13.5099 | 13.5808 | 13.6515 | 13.7262 | 13.8004 | 13.8743 | 13.9517 | 14.028 | 14.108 | 14.1869 | 14.5842 | 14.9813
|  |  |  | Base Case [MW] |  |  | 13.4973 | 13.6091 | 13.7217 | 13.843 | 13.9634 | 13.4982 | 13.5757 | 13.656 | 13.7391 | 13.8207 | 13.9088 | 13.9949 | 14.0832 | 14.1733 | 14.2651 | 14.3578 | 14.819 | 15.2804
|  |  |  | Aggressive [MW] |  |  | 13.4973 | 13.632 | 13.7739 | 13.9223 | 14.0753 | 13.6477 | 13.719 | 13.794 | 13.8685 | 13.9423 | 14.0197 | 14.1006 | 14.1803 | 14.2629 | 14.3442 | 14.4278 | 14.8399 | 15.2523
| BALLAGHADERREEN | 10 | 1 | Conservative [MW] |  |  | 2.8077 | 2.8321 | 2.8574 | 2.8824 | 2.9071 | 14.9829 | 15.0529 | 15.1254 | 15.1992 | 15.2755 | 15.353 | 15.4315 | 15.5127 | 15.5948 | 15.6795 | 15.7651 | 16.1908 | 16.6166
|  |  |  | Best View [MW] |  |  | 2.8077 | 2.8493 | 2.8923 | 2.9355 | 2.978 | 15.1141 | 15.212 | 15.3136 | 15.4176 | 15.5239 | 15.6337 | 15.7472 | 15.8627 | 15.9833 | 16.1055 | 16.2326 | 16.8549 | 17.4781
|  |  |  | Base Case [MW] |  |  | 2.8077 | 2.8634 | 2.9189 | 2.9761 | 3.0328 | 15.2204 | 15.3389 | 15.4624 | 15.5894 | 15.721 | 15.8574 | 15.9982 | 16.1435 | 16.2928 | 16.4479 | 16.6083 | 17.3959 | 18.1845
|  |  |  | Aggressive [MW] |  |  | 2.8077 | 2.8932 | 2.9799 | 3.068 | 3.1563 | 15.4667 | 15.6296 | 15.7996 | 15.9778 | 16.1625 | 16.3547 | 16.5556 | 16.7648 | 16.9811 | 17.2063 | 17.4371 | 18.5761 | 19.7161
| BALLINACURRA | 10 | 1 | Conservative [MW] |  |  | 7.5266 | 7.5642 | 7.6009 | 7.6391 | 7.6762 | 7.7144 | 7.7558 | 7.7978 | 7.84 | 7.8817 | 7.9255 | 7.9659 | 8.0078 | 8.051 | 8.0928 | 8.1329 | 8.338 | 8.5428
|  |  |  | Best View [MW] |  |  | 7.5266 | 7.5635 | 7.6017 | 7.6412 | 7.6794 | 7.7186 | 7.7743 | 7.8317 | 7.8896 | 7.9448 | 8.0017 | 8.0599 | 8.1164 | 8.1703 | 8.2236 | 8.278 | 8.547 | 8.8162
|  |  |  | Base Case [MW] |  |  | 7.5266 | 7.5796 | 7.6307 | 7.6847 | 7.7386 | 7.7924 | 7.8548 | 7.9209 | 7.9857 | 8.051 | 8.116 | 8.1797 | 8.2407 | 8.2978 | 8.355 | 8.4053 | 8.6752 | 8.944
|  |  |  | Aggressive [MW] |  |  | 7.5266 | 7.6101 | 7.6952 | 7.7809 | 7.868 | 7.9549 | 8.0241 | 8.0934 | 8.1639 | 8.2315 | 8.2943 | 8.3562 | 8.4121 | 8.4595 | 8.4976 | 8.5257 | 8.6931 | 8.8587
| BALLINASLOE | 10 | 1 | Conservative [MW] |  |  | 7.042 | 7.0601 | 7.0818 | 7.0985 | 7.1187 | 7.1428 | 7.1761 | 7.2075 | 7.2455 | 7.2766 | 7.3145 | 7.3499 | 7.3873 | 7.4266 | 7.4633 | 7.5063 | 7.7045 | 7.9038
|  |  |  | Best View [MW] |  |  | 7.042 | 7.0711 | 7.1029 | 7.1328 | 7.1651 | 7.2002 | 7.2459 | 7.2963 | 7.3464 | 7.4005 | 7.4542 | 7.507 | 7.5631 | 7.6226 | 7.6806 | 7.7361 | 8.0204 | 8.3042
|  |  |  | Base Case [MW] |  |  | 7.042 | 7.0826 | 7.1284 | 7.1749 | 7.2175 | 7.2651 | 7.3219 | 7.3775 | 7.4318 | 7.4939 | 7.549 | 7.6113 | 7.6757 | 7.7418 | 7.8041 | 7.8724 | 8.198 | 8.5246
|  |  |  | Aggressive [MW] |  |  | 7.042 | 7.1059 | 7.1747 | 7.2476 | 7.3199 | 7.3951 | 7.4595 | 7.5251 | 7.592 | 7.6592 | 7.7315 | 7.8034 | 7.8741 | 7.9532 | 8.0298 | 8.1085 | 8.4964 | 8.8846
| BALLINCLEA | 10 | 1 | Conservative [MW] |  |  | 7.5805 | 7.6072 | 7.6346 | 7.6623 | 7.6924 | 7.7227 | 7.7447 | 7.7696 | 7.7934 | 7.8181 | 7.8436 | 7.87 | 7.8951 | 7.9231 | 7.9497 | 7.9771 | 8.1118 | 8.2468
|  |  |  | Best View [MW] |  |  | 7.5805 | 7.6118 | 7.6432 | 7.6763 | 7.7113 | 7.7459 | 7.7735 | 7.8015 | 7.832 | 7.8609 | 7.8922 | 7.9239 | 7.9558 | 7.9878 | 8.0222 | 8.0565 | 8.2282 | 8.3999
|  |  |  | Base Case [MW] |  |  | 7.5805 | 7.615 | 7.6509 | 7.6881 | 7.7285 | 7.7678 | 7.7999 | 7.8321 | 7.8664 | 7.9006 | 7.9367 | 7.9726 | 8.0081 | 8.0474 | 8.0861 | 8.1264 | 8.3237 | 8.5212
|  |  |  | Aggressive [MW] |  |  | 7.5805 | 7.6307 | 7.6854 | 7.7422 | 7.8004 | 7.864 | 7.8962 | 7.9283 | 7.9626 | 7.9968 | 8.0331 | 8.0691 | 8.1069 | 8.1443 | 8.1835 | 8.222 | 8.4164 | 8.6107
| BALLINCOLLIG | 10 | 1 | Conservative [MW] |  |  | 11.9236 | 11.9585 | 11.9919 | 12.0275 | 12.0657 | 12.1021 | 12.1382 | 12.1767 | 12.2176 | 12.2564 | 12.2975 | 12.3408 | 12.382 | 12.4254 | 12.4706 | 12.5137 | 12.7346 | 12.9552
|  |  |  | Best View [MW] |  |  | 11.9236 | 11.9594 | 11.9972 | 12.0333 | 12.0756 | 12.1122 | 12.1654 | 12.2157 | 12.2706 | 12.3262 | 12.3825 | 12.4389 | 12.4998 | 12.5608 | 12.626 | 12.6907 | 13.0155 | 13.3403
|  |  |  | Base Case [MW] |  |  | 11.9236 | 11.9726 | 12.0266 | 12.0772 | 12.132 | 12.1875 | 12.2399 | 12.2971 | 12.3508 | 12.4091 | 12.4675 | 12.5304 | 12.5931 | 12.6598 | 12.7262 | 12.7921 | 13.1229 | 13.4536
|  |  |  | Aggressive [MW] |  |  | 11.9236 | 11.9844 | 12.0483 | 12.115 | 12.1838 | 12.2592 | 12.3289 | 12.4013 | 12.4757 | 12.5517 | 12.6337 | 12.7207 | 12.8044 | 12.8967 | 12.9892 | 13.0852 | 13.556 | 14.0273
| BALLINDERRY | 10 | 1 | Conservative [MW] |  |  | 7.8736 | 7.8929 | 7.9117 | 7.9297 | 7.9492 | 7.9702 | 8.0107 | 8.0524 | 8.0952 | 8.1389 | 8.1854 | 8.2326 | 8.2802 | 8.3281 | 8.3782 | 8.4307 | 8.687 | 8.9437
|  |  |  | Best View [MW] |  |  | 7.8736 | 7.8988 | 7.9227 | 7.9478 | 7.9736 | 7.9984 | 8.0458 | 8.0955 | 8.1452 | 8.1966 | 8.2518 | 8.3064 | 8.3618 | 8.4207 | 8.4802 | 8.5423 | 8.8458 | 9.1498
|  |  |  | Base Case [MW] |  |  | 7.8736 | 7.9206 | 7.9698 | 8.0187 | 8.0715 | 8.1235 | 8.1778 | 8.2313 | 8.2883 | 8.3438 | 8.4044 | 8.4656 | 8.529 | 8.592 | 8.6591 | 8.7273 | 9.0653 | 9.4036
|  |  |  | Aggressive [MW] |  |  | 7.8736 | 7.9387 | 8.0059 | 8.0774 | 8.1519 | 8.2292 | 8.2941 | 8.3602 | 8.4274 | 8.4996 | 8.5719 | 8.6459 | 8.7235 | 8.8042 | 8.8839 | 8.9677 | 9.3759 | 9.7848
|  | 20 | 1 | Conservative [MW] |  |  | 4.0232 | 4.0497 | 4.0772 | 4.1047 | 4.1321 | 4.1601 | 4.2182 | 4.2779 | 4.339 | 4.4009 | 4.4652 | 4.5301 | 4.5966 | 4.6648 | 4.734 | 4.8044 | 5.1532 | 5.5021
|  |  |  | Best View [MW] |  |  | 4.0232 | 4.0578 | 4.0933 | 4.1288 | 4.1653 | 4.2023 | 4.2694 | 4.3384 | 4.4098 | 4.4823 | 4.557 | 4.6336 | 4.7117 | 4.7913 | 4.8725 | 4.9556 | 5.3659 | 5.7766
|  |  |  | Base Case [MW] |  |  | 4.0232 | 4.09 | 4.1593 | 4.2301 | 4.3034 | 4.379 | 4.4531 | 4.5295 | 4.6078 | 4.6874 | 4.7693 | 4.8527 | 4.9379 | 5.024 | 5.1123 | 5.2008 | 5.6429 | 6.0849
|  |  |  | Aggressive [MW] |  |  | 4.0232 | 4.1161 | 4.2129 | 4.3138 | 4.4189 | 4.5281 | 4.6169 | 4.7086 | 4.8026 | 4.8987 | 4.9965 | 5.0964 | 5.1979 | 5.3004 | 5.4042 | 5.5097 | 6.0327 | 6.5561
| BALLINROBE | 20 | 1 | Conservative [MW] |  |  | 12.5803 | 12.5973 | 12.6111 | 12.6276 | 12.6473 | 12.6635 | 12.73 | 12.7968 | 12.8671 | 12.9376 | 13.0112 | 13.0848 | 13.1614 | 13.2376 | 13.3163 | 13.3979 | 13.7982 | 14.1989
|  |  |  | Best View [MW] |  |  | 12.5803 | 12.6169 | 12.6556 | 12.6966 | 12.7365 | 12.7787 | 12.8611 | 12.9486 | 13.0377 | 13.1282 | 13.2231 | 13.319 | 13.4187 | 13.5189 | 13.6259 | 13.7288 | 14.2544 | 14.7793
|  |  |  | Base Case [MW] |  |  | 12.5803 | 12.6334 | 12.6908 | 12.7494 | 12.8091 | 12.8665 | 12.9739 | 13.0809 | 13.1933 | 13.3072 | 13.4259 | 13.5489 | 13.6753 | 13.8049 | 13.9403 | 14.0736 | 14.7458 | 15.4177
|  |  |  | Aggressive [MW] |  |  | 12.5803 | 12.6905 | 12.8082 | 12.9301 | 13.0554 | 13.1867 | 13.3401 | 13.4979 | 13.6626 | 13.8361 | 14.0136 | 14.1974 | 14.3852 | 14.5829 | 14.784 | 14.9894 | 16.005 | 17.0214
| BALLINVALLY | 20 | 1 | Conservative [MW] |  |  | 9.5775 | 9.5775 | 9.5775 | 9.5779 | 9.5779 | 9.5783 | 9.5783 | 9.5783 | 9.5783 | 9.5787 | 9.5787 | 9.5787 | 9.5787 | 9.5787 | 9.5791 | 9.5791 | 9.5802 | 9.5812
|  |  |  | Best View [MW] |  |  | 9.5775 | 9.5775 | 9.5779 | 9.5779 | 9.5779 | 9.5783 | 9.5783 | 9.5787 | 9.5787 | 9.5787 | 9.5787 | 9.5791 | 9.5791 | 9.5791 | 9.5795 | 9.5795 | 9.5806 | 9.5816
|  |  |  | Base Case [MW] |  |  | 9.5775 | 9.5775 | 9.5779 | 9.5779 | 9.5779 | 9.5783 | 9.5787 | 9.5787 | 9.5787 | 9.5791 | 9.5791 | 9.5791 | 9.5795 | 9.5795 | 9.5795 | 9.5799 | 9.5808 | 9.5819
|  |  |  | Aggressive [MW] |  |  | 9.5775 | 9.5775 | 9.5779 | 9.5779 | 9.5779 | 9.5787 | 9.5787 | 9.5791 | 9.5791 | 9.5795 | 9.5795 | 9.5799 | 9.5799 | 9.5803 | 9.5807 | 9.5807 | 9.5818 | 9.5828
| BALLYARD | 10 | 1 | Conservative [MW] |  |  | 6.5447 | 6.5655 | 6.5857 | 6.6051 | 6.6238 | 19.11 | 19.1529 | 19.1983 | 19.2451 | 19.2901 | 19.3412 | 19.3898 | 19.4405 | 19.4926 | 19.5464 | 19.6017 | 19.8743 | 20.1472
|  |  |  | Best View [MW] |  |  | 6.5447 | 6.5789 | 6.6154 | 6.6497 | 6.6861 | 19.202 | 19.2589 | 19.3201 | 19.3859 | 19.4525 | 19.5186 | 19.5893 | 19.6595 | 19.7336 | 19.8076 | 19.8847 | 20.2617 | 20.6392
|  |  |  | Base Case [MW] |  |  | 6.5447 | 6.5822 | 6.6217 | 6.6626 | 6.7052 | 19.2261 | 19.2901 | 19.358 | 19.4294 | 19.5008 | 19.5757 | 19.6498 | 19.7273 | 19.8117 | 19.8947 | 19.9804 | 20.4017 | 20.8235
|  |  |  | Aggressive [MW] |  |  | 6.5447 | 6.6061 | 6.665 | 6.7302 | 6.797 | 19.3693 | 19.4548 | 19.5416 | 19.6337 | 19.7306 | 19.8281 | 19.93 | 20.0396 | 20.1487 | 20.2647 | 20.383 | 20.9685 | 21.5543
| BALLYBAILIE | 10 | 1 | Conservative [MW] |  |  | 3.9592 | 3.978 | 3.9977 | 4.0183 | 4.0378 | 4.058 | 4.0802 | 4.1029 | 4.1261 | 4.1497 | 4.1737 | 4.1982 | 4.2229 | 4.2477 | 4.2728 | 4.2979 | 4.4232 | 4.5485
|  |  |  | Best View [MW] |  |  | 3.9592 | 3.9797 | 4.0026 | 4.0243 | 4.0466 | 4.0693 | 4.1003 | 4.1326 | 4.1639 | 4.1981 | 4.2311 | 4.2667 | 4.3007 | 4.337 | 4.3733 | 4.4094 | 4.5902 | 4.7711
|  |  |  | Base Case [MW] |  |  | 3.9592 | 3.9898 | 4.0214 | 4.0541 | 4.0875 | 4.1236 | 4.1589 | 4.1963 | 4.2337 | 4.2728 | 4.3113 | 4.3531 | 4.3937 | 4.4349 | 4.4763 | 4.5201 | 4.7328 | 4.9459
|  |  |  | Aggressive [MW] |  |  | 3.9592 | 4.0009 | 4.0452 | 4.0899 | 4.1364 | 4.1863 | 4.2302 | 4.2744 | 4.3204 | 4.3678 | 4.4162 | 4.4651 | 4.514 | 4.5645 | 4.6157 | 4.667 | 4.9232 | 5.1794
| BALLYBAY | 10 | 1 | Conservative [MW] |  |  | 12.9761 | 13.0035 | 13.0302 | 13.0596 | 13.0843 | 19.3131 | 19.3508 | 19.3945 | 19.4361 | 19.4802 | 19.5257 | 19.5734 | 19.619 | 19.6702 | 19.7194 | 19.7699 | 20.0188 | 20.2679
|  |  |  | Best View [MW] |  |  | 12.9761 | 13.0109 | 13.044 | 13.0799 | 13.1181 | 19.353 | 19.4114 | 19.4705 | 19.5296 | 19.5931 | 19.6604 | 19.7278 | 19.7983 | 19.8688 | 19.9461 | 20.0226 | 20.4071 | 20.7915
|  |  |  | Base Case [MW] |  |  | 12.9761 | 13.0207 | 13.0631 | 13.1069 | 13.1523 | 19.3993 | 19.4652 | 19.5347 | 19.6036 | 19.6756 | 19.7505 | 19.8279 | 19.9077 | 19.9939 | 20.0782 | 20.1677 | 20.6012 | 21.0356
|  |  |  | Aggressive [MW] |  |  | 12.9761 | 13.0413 | 13.1125 | 13.182 | 13.257 | 19.542 | 19.6264 | 19.7115 | 19.8052 | 19.9027 | 20.0041 | 20.1085 | 20.2199 | 20.3331 | 20.4525 | 20.5764 | 21.1838 | 21.792
| BALLYBEGGAN | 10 | 1 | Conservative [MW] |  |  | 13.5654 | 13.6026 | 13.6385 | 13.6776 | 13.715 | 13.7512 | 13.8241 | 13.901 | 13.9726 | 14.0524 | 14.1311 | 14.2084 | 14.2887 | 14.3715 | 14.4526 | 14.5409 | 14.9629 | 15.3862
|  |  |  | Best View [MW] |  |  | 13.5654 | 13.6285 | 13.6963 | 13.7641 | 13.8321 | 13.9046 | 14.0022 | 14.0998 | 14.2018 | 14.3026 | 14.4114 | 14.5183 | 14.6276 | 14.7385 | 14.8512 | 14.9689 | 15.544 | 16.12
|  |  |  | Base Case [MW] |  |  | 13.5654 | 13.6361 | 13.7105 | 13.7884 | 13.8653 | 13.9451 | 14.0521 | 14.157 | 14.2692 | 14.3833 | 14.4982 | 14.6143 | 14.7349 | 14.8547 | 14.9832 | 15.1093 | 15.7461 | 16.3825
|  |  |  | Aggressive [MW] |  |  | 13.5654 | 13.6797 | 13.799 | 13.9182 | 14.045 | 14.1745 | 14.3112 | 14.4483 | 14.5893 | 14.7332 | 14.8838 | 15.0345 | 15.1898 | 15.3469 | 15.5096 | 15.6659 | 16.4647 | 17.2624
| BALLYBODEN | 10 | 1 | Conservative [MW] |  |  | 11.7066 | 11.7833 | 11.8667 | 11.9481 | 12.0365 | 12.1218 | 12.2031 | 12.2825 | 12.3649 | 12.4499 | 12.5326 | 12.6219 | 12.7082 | 12.7964 | 12.8903 | 12.9806 | 13.4419 | 13.9025
|  |  |  | Best View [MW] |  |  | 11.7066 | 11.7968 | 11.8917 | 11.9907 | 12.0941 | 12.1965 | 12.2845 | 12.3787 | 12.4688 | 12.5645 | 12.6645 | 12.7598 | 12.8642 | 12.9628 | 13.0696 | 13.1749 | 13.7053 | 14.2354
|  |  |  | Base Case [MW] |  |  | 11.7066 | 11.8147 | 11.9248 | 12.0401 | 12.1561 | 12.2808 | 12.377 | 12.4817 | 12.5852 | 12.6919 | 12.8012 | 12.9081 | 13.0213 | 13.1359 | 13.2514 | 13.3718 | 13.9606 | 14.5503
|  |  |  | Aggressive [MW] |  |  | 11.7066 | 11.8898 | 12.0836 | 12.2845 | 12.499 | 12.7228 | 12.826 | 12.9321 | 13.0363 | 13.1475 | 13.2556 | 13.3704 | 13.4863 | 13.6023 | 13.7177 | 13.837 | 14.4232 | 15.01
| BALLYBUNION | 20 | 1 | Conservative [MW] |  |  | 6.5082 | 6.5225 | 6.5404 | 6.5536 | 6.5706 | 6.587 | 6.6193 | 6.6498 | 6.6825 | 6.7177 | 6.7506 | 6.7859 | 6.8189 | 6.854 | 6.8913 | 6.9304 | 7.1213 | 7.3125
|  |  |  | Best View [MW] |  |  | 6.5082 | 6.5355 | 6.5613 | 6.5941 | 6.6209 | 6.6502 | 6.6927 | 6.7362 | 6.7806 | 6.8257 | 6.8713 | 6.9174 | 6.9683 | 7.0192 | 7.07 | 7.1205 | 7.3738 | 7.627
|  |  |  | Base Case [MW] |  |  | 6.5082 | 6.5369 | 6.5724 | 6.6014 | 6.637 | 6.6704 | 6.7176 | 6.765 | 6.8128 | 6.8606 | 6.9127 | 6.9645 | 7.0157 | 7.0706 | 7.1244 | 7.1815 | 7.4583 | 7.7356
|  |  |  | Aggressive [MW] |  |  | 6.5082 | 6.5555 | 6.6064 | 6.661 | 6.7147 | 6.7712 | 6.829 | 6.8893 | 6.9514 | 7.0151 | 7.0798 | 7.15 | 7.2207 | 7.2909 | 7.3649 | 7.4426 | 7.8214 | 8.2008
|  |  | 2 | Conservative [MW] |  |  | 0.15377 | 0.15377 | 0.15387 | 0.15387 | 0.15396 | 0.15197 | 0.15206 | 0.15216 | 0.15225 | 0.15235 | 0.15244 | 0.15254 | 0.15263 | 0.15273 | 0.15282 | 0.15282 | 0.15308 | 0.15331
|  |  |  | Best View [MW] |  |  | 0.15377 | 0.15377 | 0.15387 | 0.15387 | 0.15377 | 0.15206 | 0.15216 | 0.15235 | 0.15244 | 0.15254 | 0.15273 | 0.15292 | 0.15254 | 0.15216 | 0.15178 | 0.1513 | 0.14918 | 0.14704
|  |  |  | Base Case [MW] |  |  | 0.15377 | 0.15387 | 0.15396 | 0.15387 | 0.15368 | 0.15216 | 0.15225 | 0.15244 | 0.15254 | 0.15273 | 0.15292 | 0.15254 | 0.15216 | 0.15168 | 0.15121 | 0.15073 | 0.14836 | 0.14598
|  |  |  | Aggressive [MW] |  |  | 0.15377 | 0.15387 | 0.15387 | 0.15358 | 0.1533 | 0.15244 | 0.15263 | 0.15282 | 0.15263 | 0.15216 | 0.15159 | 0.15102 | 0.15045 | 0.14988 | 0.14921 | 0.14874 | 0.14585 | 0.143
| BALLYCONNELL | 20 | 1 | Conservative [MW] |  |  | 1.0584 | 1.0923 | 1.127 | 1.1623 | 1.198 | 1.2342 | 1.2843 | 1.3352 | 1.387 | 1.44 | 1.4938 | 1.5478 | 1.6031 | 1.6594 | 1.7164 | 1.7739 | 2.0601 | 2.3463
|  |  |  | Best View [MW] |  |  | 1.0584 | 1.1022 | 1.1469 | 1.1925 | 1.2384 | 1.2856 | 1.3551 | 1.4265 | 1.4991 | 1.5736 | 1.6493 | 1.7268 | 1.8053 | 1.8853 | 1.9659 | 2.0476 | 2.453 | 2.8586
|  |  |  | Base Case [MW] |  |  | 1.0584 | 1.1128 | 1.1688 | 1.2258 | 1.2842 | 1.3437 | 1.4217 | 1.5014 | 1.583 | 1.6666 | 1.7518 | 1.8386 | 1.9265 | 2.0163 | 2.1067 | 2.1973 | 2.6499 | 3.1026
|  |  |  | Aggressive [MW] |  |  | 1.0584 | 1.1431 | 1.2306 | 1.3213 | 1.4145 | 1.5107 | 1.6094 | 1.7107 | 1.8141 | 1.9199 | 2.0269 | 2.136 | 2.2457 | 2.3552 | 2.4642 | 2.571 | 3.1109 | 3.6504
| BALLYCONRA | 20 | 1 | Conservative [MW] |  |  | 0.38428 | 0.38428 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566
|  |  |  | Best View [MW] |  |  | 0.38428 | 0.38428 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566
|  |  |  | Base Case [MW] |  |  | 0.38428 | 0.38428 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.35669 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566
|  |  |  | Aggressive [MW] |  |  | 0.38428 | 0.38428 | 0.35669 | 0.35669 | 0.35669 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566 | 0.3566
| BALLYCOOLIN | 10 | 1 | Conservative [MW] |  |  | 34.0559 | 34.3491 | 34.6329 | 34.9245 | 35.2108 | 35.509 | 35.666 | 35.801 | 35.962 | 36.1204 | 36.2666 | 36.4169 | 36.5527 | 36.6914 | 36.8308 | 37.2416 | 38.5719 | 39.9474
|  |  |  | Best View [MW] |  |  | 34.0559 | 34.376 | 34.6886 | 35.014 | 35.3334 | 35.6543 | 35.8393 | 35.99 | 36.1674 | 36.3401 | 36.5071 | 36.6667 | 36.8163 | 37.2619 | 37.7616 | 38.0188 | 39.9513 | 41.8434
|  |  |  | Base Case [MW] |  |  | 34.0559 | 34.4119 | 34.7511 | 35.1062 | 35.4584 | 35.809 | 36.0076 | 36.1851 | 36.3697 | 36.555 | 36.7383 | 37.0555 | 37.6127 | 37.9985 | 38.1308 | 38.2527 | 38.8899 | 39.5254
|  |  |  | Aggressive [MW] |  |  | 34.0559 | 34.4886 | 34.9142 | 35.3472 | 35.768 | 36.1789 | 36.6393 | 36.4894 | 36.6552 | 36.8025 | 37.2212 | 37.7148 | 38.0091 | 38.1277 | 38.2429 | 38.3303 | 38.8414 | 39.3478
| BALLYCROSSAUN | 20 | 1 | Conservative [MW] |  |  | 2.9655 | 2.98 | 2.9947 | 3.0088 | 3.0238 | 3.0397 | 3.061 | 3.0832 | 3.1063 | 3.129 | 3.1533 | 3.1772 | 3.202 | 3.2279 | 3.2531 | 3.2801 | 3.4105 | 3.5412
|  |  |  | Best View [MW] |  |  | 2.9655 | 2.9832 | 3.0012 | 3.0193 | 3.0383 | 3.0577 | 3.0893 | 3.1227 | 3.1566 | 3.1918 | 3.2282 | 3.2658 | 3.3046 | 3.3439 | 3.3853 | 3.4279 | 3.6375 | 3.8474
|  |  |  | Base Case [MW] |  |  | 2.9655 | 2.9893 | 3.0142 | 3.0394 | 3.065 | 3.0917 | 3.1271 | 3.1638 | 3.2017 | 3.241 | 3.2815 | 3.3234 | 3.3665 | 3.4109 | 3.4575 | 3.5054 | 3.7414 | 3.9776
|  |  |  | Aggressive [MW] |  |  | 2.9655 | 3.0036 | 3.0427 | 3.0839 | 3.1267 | 3.1712 | 3.2124 | 3.2559 | 3.3007 | 3.3468 | 3.3953 | 3.4451 | 3.4971 | 3.5505 | 3.6061 | 3.6639 | 3.9472 | 4.2307
| BALLYCUMMIN | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
| BALLYDEHOB | 20 | 1 | Conservative [MW] |  |  | 4.1441 | 4.1622 | 4.1814 | 4.2017 | 4.2205 | 4.2425 | 4.2617 | 4.2819 | 4.3027 | 4.3244 | 4.3468 | 4.3675 | 4.3888 | 4.4131 | 4.4355 | 4.4583 | 4.5711 | 4.6839
|  |  |  | Best View [MW] |  |  | 4.1441 | 4.1642 | 4.1852 | 4.2047 | 4.2251 | 4.2484 | 4.2742 | 4.302 | 4.3316 | 4.3606 | 4.3889 | 4.421 | 4.4521 | 4.4819 | 4.5152 | 4.5469 | 4.7099 | 4.8725
|  |  |  | Base Case [MW] |  |  | 4.1441 | 4.1712 | 4.2003 | 4.2289 | 4.2568 | 4.2885 | 4.3147 | 4.3451 | 4.3748 | 4.4036 | 4.4363 | 4.4678 | 4.4979 | 4.5314 | 4.5633 | 4.5982 | 4.7647 | 4.9317
|  |  |  | Aggressive [MW] |  |  | 4.1441 | 4.1823 | 4.22 | 4.2613 | 4.3036 | 4.3465 | 4.3769 | 4.4062 | 4.4392 | 4.471 | 4.5036 | 4.537 | 4.5711 | 4.6055 | 4.6399 | 4.6742 | 4.846 | 5.0179
| BALLYGAR | 10 | 1 | Conservative [MW] |  |  | 7.4374 | 7.4597 | 7.4857 | 7.515 | 7.5381 | 12.8118 | 12.8403 | 12.8713 | 12.9011 | 12.9335 | 12.9644 | 12.9978 | 13.0302 | 13.0646 | 13.1016 | 13.1368 | 13.3175 | 13.498
|  |  |  | Best View [MW] |  |  | 7.4374 | 7.475 | 7.5096 | 7.5466 | 7.5854 | 12.8506 | 12.8913 | 12.9335 | 12.977 | 13.0218 | 13.0681 | 13.1152 | 13.1671 | 13.216 | 13.2697 | 13.3238 | 13.5933 | 13.8628
|  |  |  | Base Case [MW] |  |  | 7.4374 | 7.486 | 7.53 | 7.5792 | 7.6329 | 12.8852 | 12.9351 | 12.9819 | 13.0334 | 13.0853 | 13.1412 | 13.1974 | 13.2576 | 13.3175 | 13.3768 | 13.4437 | 13.7581 | 14.0737
|  |  |  | Aggressive [MW] |  |  | 7.4374 | 7.5158 | 7.5958 | 7.6814 | 7.7667 | 13.0017 | 13.0658 | 13.128 | 13.1964 | 13.2671 | 13.3436 | 13.4215 | 13.5003 | 13.5839 | 13.672 | 13.7637 | 14.2126 | 14.6621
| BALLYHALE | 10 | 1 | Conservative [MW] |  |  | 6.0901 | 6.1282 | 6.1855 | 6.2194 | 6.2481 | 6.2806 | 6.3208 | 6.3819 | 6.4279 | 6.4627 | 6.5143 | 6.5666 | 6.6097 | 6.6648 | 6.7203 | 6.7775 | 7.059 | 7.3408
|  |  |  | Best View [MW] |  |  | 6.0901 | 6.1587 | 6.2023 | 6.2476 | 6.2641 | 6.306 | 6.3583 | 6.423 | 6.4826 | 6.5375 | 6.6008 | 6.6701 | 6.7296 | 6.8276 | 6.9357 | 7.0424 | 7.5799 | 8.1171
|  |  |  | Base Case [MW] |  |  | 6.0901 | 6.1497 | 6.218 | 6.2395 | 6.2944 | 6.3367 | 6.3964 | 6.4753 | 6.542 | 6.6118 | 6.6931 | 6.7885 | 6.9028 | 7.0208 | 7.1401 | 7.2881 | 7.9516 | 8.6199
|  |  |  | Aggressive [MW] |  |  | 6.0901 | 6.1953 | 6.2503 | 6.3257 | 6.3997 | 6.4723 | 6.5512 | 6.6454 | 6.7358 | 6.883 | 7.0289 | 7.1852 | 7.3609 | 7.4954 | 7.6079 | 7.7024 | 8.2229 | 8.7405
|  | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
| BALLYHAUNIS | 10 | 1 | Conservative [MW] |  |  | 7.4801 | 7.5075 | 7.5336 | 7.5629 | 7.5907 | 20.2108 | 20.2748 | 20.3401 | 20.402 | 20.4688 | 20.5403 | 20.6086 | 20.6811 | 20.7545 | 20.828 | 20.9057 | 21.283 | 21.661
|  |  |  | Best View [MW] |  |  | 7.4801 | 7.5185 | 7.5588 | 7.6008 | 7.6395 | 20.2919 | 20.3794 | 20.4688 | 20.5642 | 20.6572 | 20.7604 | 20.8599 | 20.9645 | 21.0738 | 21.1877 | 21.301 | 21.8692 | 22.4373
|  |  |  | Base Case [MW] |  |  | 7.4801 | 7.5304 | 7.5854 | 7.6348 | 7.6884 | 20.3727 | 20.4717 | 20.5792 | 20.6866 | 20.7978 | 20.9125 | 21.0339 | 21.1579 | 21.2839 | 21.4152 | 21.5518 | 22.2208 | 22.8906
|  |  |  | Aggressive [MW] |  |  | 7.4801 | 7.5676 | 7.65 | 7.741 | 7.8296 | 20.6185 | 20.7531 | 20.8908 | 21.0358 | 21.1828 | 21.339 | 21.5038 | 21.672 | 21.8467 | 22.027 | 22.2165 | 23.1394 | 24.0638
| BALLYJAMESDUFF | 10 | 1 | Conservative [MW] |  |  | 9.4147 | 9.4499 | 9.4857 | 9.5213 | 9.5584 | 9.5954 | 9.6474 | 9.7008 | 9.7553 | 9.8119 | 9.8694 | 9.9274 | 9.9874 | 10.0485 | 10.1106 | 10.1745 | 10.4893 | 10.8044
|  |  |  | Best View [MW] |  |  | 9.4147 | 9.4601 | 9.5053 | 9.5526 | 9.6005 | 9.6489 | 9.7224 | 9.7976 | 9.8749 | 9.9549 | 10.0372 | 10.1225 | 10.2098 | 10.299 | 10.3919 | 10.4864 | 10.9546 | 11.4231
|  |  |  | Base Case [MW] |  |  | 9.4147 | 9.4711 | 9.5279 | 9.5866 | 9.6473 | 9.7102 | 9.7918 | 9.8779 | 9.9656 | 10.0561 | 10.1502 | 10.2469 | 10.347 | 10.4492 | 10.5554 | 10.6653 | 11.2051 | 11.7455
|  |  |  | Aggressive [MW] |  |  | 9.4147 | 9.5017 | 9.5918 | 9.6863 | 9.7846 | 9.887 | 9.9937 | 10.1043 | 10.2194 | 10.3387 | 10.462 | 10.5909 | 10.7239 | 10.8616 | 11.0038 | 11.1511 | 11.874 | 12.5977
| BALLYLICKEY | 20 | 1 | Conservative [MW] |  |  | 4.1332 | 4.1332 | 4.1332 | 4.1332 | 4.1332 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331
|  |  |  | Best View [MW] |  |  | 4.1332 | 4.1332 | 4.1332 | 4.1332 | 4.1332 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331
|  |  |  | Base Case [MW] |  |  | 4.1332 | 4.1332 | 4.1332 | 4.1332 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331
|  |  |  | Aggressive [MW] |  |  | 4.1332 | 4.1332 | 4.1332 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331 | 4.1331
| BALLYMACARRY | 20 | 1 | Conservative [MW] |  |  | 3.7568 | 3.7615 | 3.7661 | 3.7707 | 3.7751 | 3.7795 | 3.7893 | 3.8006 | 3.8114 | 3.8217 | 3.8336 | 3.8469 | 3.8576 | 3.8698 | 3.8835 | 3.8945 | 3.9566 | 4.0182
|  |  |  | Best View [MW] |  |  | 3.7568 | 3.7666 | 3.776 | 3.7869 | 3.7975 | 3.8076 | 3.8223 | 3.838 | 3.8547 | 3.8724 | 3.8888 | 3.9082 | 3.9263 | 3.9452 | 3.9648 | 3.985 | 4.0845 | 4.1841
|  |  |  | Base Case [MW] |  |  | 3.7568 | 3.7687 | 3.7781 | 3.789 | 3.8014 | 3.8133 | 3.8308 | 3.8509 | 3.8696 | 3.8908 | 3.9125 | 3.9344 | 3.9565 | 3.981 | 4.0033 | 4.0299 | 4.1514 | 4.2737
|  |  |  | Aggressive [MW] |  |  | 3.7568 | 3.7732 | 3.7903 | 3.8083 | 3.8251 | 3.8445 | 3.8663 | 3.8901 | 3.9138 | 3.9393 | 3.9665 | 3.9931 | 4.0234 | 4.0527 | 4.0832 | 4.1145 | 4.2689 | 4.4234
| BALLYMAHON | 10 | 1 | Conservative [MW] |  |  | 1.8399 | 1.8562 | 1.872 | 1.8885 | 1.905 | 1.9216 | 1.961 | 2.0015 | 2.0424 | 2.0843 | 2.1277 | 2.1709 | 2.2157 | 2.2613 | 2.3081 | 2.3556 | 2.5911 | 2.8268
|  |  |  | Best View [MW] |  |  | 1.8399 | 1.8717 | 1.9038 | 1.9367 | 1.9705 | 2.0046 | 2.0531 | 2.1029 | 2.1536 | 2.2061 | 2.2598 | 2.3144 | 2.3701 | 2.4273 | 2.4862 | 2.5451 | 2.8396 | 3.1341
|  |  |  | Base Case [MW] |  |  | 1.8399 | 1.8773 | 1.9156 | 1.9545 | 1.9949 | 2.0357 | 2.097 | 2.1598 | 2.2247 | 2.2915 | 2.3608 | 2.4311 | 2.5039 | 2.5783 | 2.6543 | 2.7324 | 3.1174 | 3.5027
|  |  |  | Aggressive [MW] |  |  | 1.8399 | 1.9003 | 1.9623 | 2.0272 | 2.0936 | 2.1628 | 2.2428 | 2.3252 | 2.4109 | 2.5 | 2.5908 | 2.6855 | 2.7822 | 2.8824 | 2.9839 | 3.088 | 3.6015 | 4.1154
| BALLYMAKENNY | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 18.525 | 19.0041 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 18.525 | 19.0041 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 18.525 | 19.0041 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 18.525 | 19.0041 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192
| BALLYMOTE | 10 | 1 | Conservative [MW] |  |  | 0.21507 | 0.22419 | 0.23341 | 0.24273 | 0.25212 | 0.26165 | 0.28007 | 0.29887 | 0.318 | 0.33762 | 0.35765 | 0.37809 | 0.39894 | 0.42029 | 0.44207 | 0.46425 | 0.5741 | 0.68401
|  |  |  | Best View [MW] |  |  | 0.21507 | 0.23067 | 0.24658 | 0.26273 | 0.27928 | 0.2961 | 0.32143 | 0.34754 | 0.37439 | 0.40196 | 0.43026 | 0.45934 | 0.48928 | 0.51996 | 0.55139 | 0.58338 | 0.74185 | 0.90041
|  |  |  | Base Case [MW] |  |  | 0.21507 | 0.23568 | 0.25677 | 0.27844 | 0.30065 | 0.32345 | 0.3542 | 0.38604 | 0.4189 | 0.45278 | 0.48778 | 0.52381 | 0.56078 | 0.59882 | 0.63791 | 0.67812 | 0.87618 | 1.0744
|  |  |  | Aggressive [MW] |  |  | 0.21507 | 0.24691 | 0.27998 | 0.31439 | 0.35013 | 0.38731 | 0.42935 | 0.47308 | 0.51854 | 0.56565 | 0.61429 | 0.66475 | 0.71687 | 0.77082 | 0.82643 | 0.88389 | 1.1663 | 1.4489
| BALLYMOUNT | 10 | 1 | Conservative [MW] |  |  | 14.1665 | 14.2432 | 14.3192 | 14.3937 | 14.4757 | 14.5556 | 14.6295 | 14.7069 | 14.7835 | 14.8632 | 14.9414 | 15.0224 | 15.1063 | 15.1879 | 15.276 | 15.362 | 15.7977 | 16.233
|  |  |  | Best View [MW] |  |  | 14.1665 | 14.2554 | 14.3417 | 14.4328 | 14.5293 | 14.6258 | 14.7096 | 14.7958 | 14.8834 | 14.9728 | 15.0634 | 15.155 | 15.2517 | 15.3488 | 15.446 | 15.5474 | 16.0431 | 16.5395
|  |  |  | Base Case [MW] |  |  | 14.1665 | 14.2683 | 14.3731 | 14.4803 | 14.5894 | 14.7045 | 14.7948 | 14.8899 | 14.9898 | 15.0893 | 15.193 | 15.2958 | 15.4014 | 15.51 | 15.6208 | 15.7333 | 16.2913 | 16.8496
|  |  |  | Aggressive [MW] |  |  | 14.1665 | 14.3385 | 14.5163 | 14.7099 | 14.9077 | 15.1151 | 15.2161 | 15.3165 | 15.4165 | 15.5201 | 15.6269 | 15.7319 | 15.8394 | 15.9538 | 16.0649 | 16.182 | 16.7516 | 17.3221
| BALLYMUN | 10 | 1 | Conservative [MW] |  |  | 13.201 | 13.2693 | 13.3405 | 13.4145 | 13.4911 | 13.5699 | 13.6168 | 13.662 | 13.7089 | 13.758 | 13.8047 | 13.8574 | 13.908 | 13.9599 | 14.0095 | 14.0649 | 14.3264 | 14.5889
|  |  |  | Best View [MW] |  |  | 13.201 | 13.2763 | 13.3535 | 13.4361 | 13.5244 | 13.6089 | 13.6657 | 13.7195 | 13.7744 | 13.8307 | 13.888 | 13.9466 | 14.0057 | 14.0701 | 14.1308 | 14.1922 | 14.4973 | 14.8026
|  |  |  | Base Case [MW] |  |  | 13.201 | 13.2827 | 13.373 | 13.4632 | 13.5573 | 13.6544 | 13.7161 | 13.7783 | 13.8409 | 13.908 | 13.9752 | 14.0422 | 14.1093 | 14.1802 | 14.2549 | 14.329 | 14.7011 | 15.0731
|  |  |  | Aggressive [MW] |  |  | 13.201 | 13.3041 | 13.4119 | 13.5275 | 13.6462 | 13.7711 | 13.828 | 13.8815 | 13.9405 | 14.0001 | 14.0607 | 14.1264 | 14.1884 | 14.251 | 14.3181 | 14.3857 | 14.7224 | 15.0592
| BALLYRAGGET | 20 | 1 | Conservative [MW] |  |  | 3.8578 | 3.8668 | 5.7645 | 5.7832 | 5.8045 | 5.8273 | 5.8563 | 5.8876 | 5.9183 | 5.9516 | 5.9841 | 6.0189 | 6.053 | 6.0896 | 6.1286 | 6.1634 | 6.3487 | 6.5333
|  |  |  | Best View [MW] |  |  | 3.8578 | 3.8702 | 5.7732 | 5.7974 | 5.8214 | 5.8495 | 5.8913 | 5.935 | 5.9776 | 6.0251 | 6.0713 | 6.1193 | 6.1689 | 6.2236 | 6.2765 | 6.3308 | 6.5984 | 6.8663
|  |  |  | Base Case [MW] |  |  | 3.8578 | 3.8717 | 5.7817 | 5.8114 | 5.8406 | 5.8739 | 5.9244 | 5.9763 | 6.0296 | 6.0842 | 6.143 | 6.2064 | 6.2673 | 6.3323 | 6.4016 | 6.4712 | 6.8183 | 7.1655
|  |  |  | Aggressive [MW] |  |  | 3.8578 | 3.8808 | 5.8198 | 5.8702 | 5.9219 | 5.9795 | 6.0449 | 6.1137 | 6.1858 | 6.2645 | 6.3426 | 6.4271 | 6.5139 | 6.6067 | 6.7052 | 6.805 | 7.3004 | 7.796
| BALLYRAINE | 10 | 1 | Conservative [MW] |  |  | 6.5935 | 6.6085 | 6.6229 | 6.6417 | 6.6598 | 6.6775 | 6.7172 | 6.7586 | 6.8015 | 6.8408 | 6.8861 | 6.9276 | 6.9753 | 7.0187 | 7.0628 | 7.1073 | 7.3288 | 7.5504
|  |  |  | Best View [MW] |  |  | 6.5935 | 6.6273 | 6.668 | 6.706 | 6.7409 | 6.7827 | 6.8396 | 6.8988 | 6.9606 | 7.0242 | 7.0896 | 7.1511 | 7.2187 | 7.2812 | 7.349 | 7.416 | 7.753 | 8.0898
|  |  |  | Base Case [MW] |  |  | 6.5935 | 6.6343 | 6.6767 | 6.7154 | 6.7603 | 6.8063 | 6.8721 | 6.9476 | 7.0172 | 7.0905 | 7.1668 | 7.2455 | 7.3204 | 7.4015 | 7.477 | 7.5571 | 7.9454 | 8.3344
|  |  |  | Aggressive [MW] |  |  | 6.5935 | 6.6538 | 6.7206 | 6.7841 | 6.8531 | 6.9226 | 7.0035 | 7.0894 | 7.1744 | 7.2626 | 7.3525 | 7.4432 | 7.5334 | 7.6272 | 7.7175 | 7.8074 | 8.258 | 8.7085
| BALLYRICKARD | 10 | 1 | Conservative [MW] |  |  | 5.5996 | 5.6347 | 5.67 | 5.7063 | 5.7426 | 5.7792 | 5.8487 | 5.92 | 5.9919 | 6.0658 | 6.1416 | 6.2177 | 6.2967 | 6.3759 | 6.458 | 6.54 | 6.9503 | 7.3607
|  |  |  | Best View [MW] |  |  | 5.5996 | 5.6616 | 5.7257 | 5.7901 | 5.8565 | 5.9241 | 6.0166 | 6.1121 | 6.2107 | 6.3114 | 6.4142 | 6.52 | 6.6276 | 6.7381 | 6.8513 | 6.9671 | 7.5392 | 8.1118
|  |  |  | Base Case [MW] |  |  | 5.5996 | 5.6696 | 5.7411 | 5.8138 | 5.8886 | 5.9646 | 6.0658 | 6.1702 | 6.2768 | 6.3865 | 6.4991 | 6.6146 | 6.733 | 6.8551 | 6.9786 | 7.1056 | 7.7313 | 8.3575
|  |  |  | Aggressive [MW] |  |  | 5.5996 | 5.709 | 5.8221 | 5.9395 | 6.0602 | 6.1852 | 6.3158 | 6.4514 | 6.5899 | 6.7341 | 6.882 | 7.0341 | 7.1901 | 7.3512 | 7.5155 | 7.6839 | 8.5152 | 9.3471
| BALLYSHANNON | 10 | 1 | Conservative [MW] |  |  | 6.2272 | 6.2389 | 6.2503 | 6.2653 | 6.2762 | 6.2906 | 6.323 | 6.354 | 6.3872 | 6.4186 | 6.4524 | 6.4842 | 6.5183 | 6.5543 | 6.5925 | 6.6287 | 6.8148 | 7.0005
|  |  |  | Best View [MW] |  |  | 6.2272 | 6.2512 | 6.2817 | 6.311 | 6.3389 | 6.3694 | 6.4125 | 6.4605 | 6.5087 | 6.5573 | 6.606 | 6.6588 | 6.7112 | 6.7632 | 6.8188 | 6.8777 | 7.1636 | 7.4501
|  |  |  | Base Case [MW] |  |  | 6.2272 | 6.2555 | 6.29 | 6.3228 | 6.3538 | 6.3908 | 6.4445 | 6.4971 | 6.557 | 6.6153 | 6.6762 | 6.7393 | 6.8041 | 6.8661 | 6.9336 | 7.0061 | 7.3552 | 7.7051
|  |  |  | Aggressive [MW] |  |  | 6.2272 | 6.2718 | 6.3242 | 6.3764 | 6.4282 | 6.4834 | 6.5496 | 6.6165 | 6.6881 | 6.7594 | 6.8344 | 6.9123 | 6.9926 | 7.0747 | 7.1624 | 7.2455 | 7.6735 | 8.1006
| BALLYTIVNAN | 10 | 1 | Conservative [MW] |  |  | 14.2277 | 14.2704 | 14.3115 | 14.3512 | 14.3935 | 14.4343 | 14.5135 | 14.5957 | 14.6804 | 14.7627 | 14.8474 | 14.9342 | 15.0227 | 15.1127 | 15.204 | 15.296 | 15.754 | 16.2121
|  |  |  | Best View [MW] |  |  | 14.2277 | 14.297 | 14.3664 | 14.4402 | 14.5091 | 14.582 | 14.6946 | 14.8043 | 14.92 | 15.0369 | 15.1534 | 15.2748 | 15.3996 | 15.5222 | 15.6519 | 15.7781 | 16.4185 | 17.0584
|  |  |  | Base Case [MW] |  |  | 14.2277 | 14.3176 | 14.4133 | 14.505 | 14.6015 | 14.7031 | 14.8338 | 14.9708 | 15.1074 | 15.2484 | 15.3917 | 15.5416 | 15.6865 | 15.84 | 15.9909 | 16.1475 | 16.9155 | 17.6844
|  |  |  | Aggressive [MW] |  |  | 14.2277 | 14.3669 | 14.5145 | 14.6638 | 14.8139 | 14.9728 | 15.1516 | 15.3309 | 15.5179 | 15.7098 | 15.8989 | 16.0972 | 16.29 | 16.4899 | 16.6817 | 16.8743 | 17.8352 | 18.7963
| BALTINGLASS | 20 | 1 | Conservative [MW] |  |  | 4.5473 | 10.9096 | 10.9531 | 10.9954 | 11.0395 | 11.0855 | 11.1479 | 11.2107 | 11.2773 | 11.344 | 11.4142 | 11.4845 | 11.5546 | 11.628 | 11.7009 | 11.7768 | 12.1483 | 12.5203
|  |  |  | Best View [MW] |  |  | 4.5473 | 10.9196 | 10.9725 | 11.0235 | 11.0789 | 11.1356 | 11.2166 | 11.2996 | 11.3875 | 11.4769 | 11.5674 | 11.6589 | 11.7544 | 11.8537 | 11.9528 | 12.0551 | 12.558 | 13.0614
|  |  |  | Base Case [MW] |  |  | 4.5473 | 10.9303 | 10.996 | 11.0622 | 11.1285 | 11.1982 | 11.297 | 11.3957 | 11.5003 | 11.6107 | 11.7195 | 11.8331 | 11.9512 | 12.073 | 12.1942 | 12.3218 | 12.9428 | 13.5648
|  |  |  | Aggressive [MW] |  |  | 4.5473 | 10.9658 | 11.0693 | 11.1783 | 11.289 | 11.4043 | 11.5384 | 11.6797 | 11.8238 | 11.9765 | 12.1294 | 12.2922 | 12.4596 | 12.6301 | 12.8053 | 12.9831 | 13.8654 | 14.748
| BANAGHER | 10 | 1 | Conservative [MW] |  |  | 6.35 | 6.3657 | 6.3808 | 6.3954 | 6.4094 | 6.4269 | 6.4445 | 6.4651 | 6.4888 | 6.5113 | 6.5327 | 6.553 | 6.5763 | 6.6025 | 6.6273 | 6.6509 | 6.7723 | 6.8934
|  |  |  | Best View [MW] |  |  | 6.35 | 6.3672 | 6.3876 | 6.407 | 6.4255 | 6.4471 | 6.4731 | 6.5013 | 6.5319 | 6.5605 | 6.5912 | 6.6199 | 6.6546 | 6.6871 | 6.7214 | 6.7573 | 6.9325 | 7.1079
|  |  |  | Base Case [MW] |  |  | 6.35 | 6.3733 | 6.3953 | 6.4162 | 6.4437 | 6.4658 | 6.4989 | 6.5296 | 6.566 | 6.5996 | 6.6388 | 6.6748 | 6.7161 | 6.754 | 6.7968 | 6.8402 | 7.0556 | 7.2711
|  |  |  | Aggressive [MW] |  |  | 6.35 | 6.3786 | 6.4093 | 6.4379 | 6.4682 | 6.5041 | 6.5432 | 6.5828 | 6.6267 | 6.6705 | 6.7182 | 6.7695 | 6.8201 | 6.8695 | 6.9259 | 6.9848 | 7.2727 | 7.561
| BANDON | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| BANGOR ERRIS | 20 | 1 | Conservative [MW] |  |  | 3.7421 | 3.7465 | 3.7488 | 3.753 | 3.7552 | 3.7592 | 3.7718 | 3.7817 | 3.795 | 3.8058 | 3.82 | 3.8314 | 3.8442 | 3.8584 | 3.8719 | 3.8866 | 3.9568 | 4.0271
|  |  |  | Best View [MW] |  |  | 3.7421 | 3.7494 | 3.7584 | 3.7651 | 3.7736 | 3.7817 | 3.7958 | 3.811 | 3.8273 | 3.8445 | 3.8607 | 3.8777 | 3.8956 | 3.9144 | 3.9339 | 3.952 | 4.0464 | 4.1405
|  |  |  | Base Case [MW] |  |  | 3.7421 | 3.753 | 3.7634 | 3.7735 | 3.7849 | 3.7958 | 3.8142 | 3.8312 | 3.851 | 3.8711 | 3.8917 | 3.9147 | 3.9359 | 3.9594 | 3.9829 | 4.0086 | 4.1312 | 4.2542
|  |  |  | Aggressive [MW] |  |  | 3.7421 | 3.7612 | 3.7825 | 3.8043 | 3.8259 | 3.8475 | 3.8742 | 3.9023 | 3.9314 | 3.9615 | 3.9943 | 4.0275 | 4.061 | 4.0965 | 4.136 | 4.1748 | 4.3706 | 4.5662
| BANTRY | 10 | 1 | Conservative [MW] |  |  | 3.8508 | 3.8954 | 3.941 | 3.9875 | 4.0348 | 4.083 | 4.1304 | 4.1808 | 4.2297 | 4.2791 | 4.3314 | 4.3818 | 4.4325 | 4.4859 | 4.5394 | 4.5929 | 4.8603 | 5.1277
|  |  |  | Best View [MW] |  |  | 3.8508 | 3.898 | 3.946 | 3.9967 | 4.0462 | 4.0963 | 4.1627 | 4.2286 | 4.2961 | 4.365 | 4.4325 | 4.5034 | 4.5749 | 4.6494 | 4.7213 | 4.7955 | 5.1604 | 5.5256
|  |  |  | Base Case [MW] |  |  | 3.8508 | 3.9158 | 3.9826 | 4.0511 | 4.1211 | 4.1923 | 4.2589 | 4.327 | 4.3962 | 4.4665 | 4.5376 | 4.6117 | 4.6835 | 4.7576 | 4.8312 | 4.9067 | 5.2791 | 5.6519
|  |  |  | Aggressive [MW] |  |  | 3.8508 | 3.9395 | 4.0339 | 4.1296 | 4.2281 | 4.3312 | 4.4013 | 4.4723 | 4.5463 | 4.6181 | 4.6924 | 4.769 | 4.8447 | 4.919 | 4.9974 | 5.0733 | 5.4594 | 5.8451
| BEALISTOWN | 20 | 1 | Conservative [MW] |  |  | 1.2814 | 1.3035 | 1.3248 | 1.3462 | 1.3671 | 1.3894 | 1.4407 | 1.493 | 1.5473 | 1.6023 | 1.6582 | 1.7159 | 1.7742 | 1.8343 | 1.8949 | 1.9571 | 2.2639 | 2.5709
|  |  |  | Best View [MW] |  |  | 1.2814 | 1.3195 | 1.3568 | 1.3952 | 1.4341 | 1.4734 | 1.5317 | 1.5908 | 1.6518 | 1.7134 | 1.7767 | 1.8416 | 1.9081 | 1.9761 | 2.0454 | 2.1143 | 2.46 | 2.8056
|  |  |  | Base Case [MW] |  |  | 1.2814 | 1.3277 | 1.3741 | 1.4216 | 1.4695 | 1.5189 | 1.5833 | 1.6505 | 1.7184 | 1.789 | 1.8598 | 1.9333 | 2.0078 | 2.0848 | 2.1623 | 2.2403 | 2.6292 | 3.0182
|  |  |  | Aggressive [MW] |  |  | 1.2814 | 1.354 | 1.4269 | 1.5027 | 1.5806 | 1.6619 | 1.7569 | 1.855 | 1.9559 | 2.0604 | 2.1667 | 2.2755 | 2.3879 | 2.4994 | 2.6144 | 2.7275 | 3.298 | 3.8681
| BEALNABLATH | 20 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| BEDFORD ROW | 10 | 1 | Conservative [MW] |  |  | 20.8067 | 20.8721 | 20.942 | 21.0119 | 21.0859 | 21.1594 | 21.2283 | 21.298 | 21.3676 | 21.4421 | 21.5164 | 21.5948 | 21.6734 | 21.7516 | 21.8339 | 21.9193 | 22.338 | 22.7573
|  |  |  | Best View [MW] |  |  | 20.8067 | 20.8851 | 20.9667 | 21.0465 | 21.1331 | 21.222 | 21.3017 | 21.3808 | 21.4596 | 21.5456 | 21.6304 | 21.7182 | 21.809 | 21.9022 | 21.998 | 22.0959 | 22.5796 | 23.0636
|  |  |  | Base Case [MW] |  |  | 20.8067 | 20.8953 | 20.9891 | 21.0878 | 21.1909 | 21.2943 | 21.3812 | 21.471 | 21.5631 | 21.657 | 21.7534 | 21.8511 | 21.9543 | 22.0591 | 22.1685 | 22.2785 | 22.827 | 23.3756
|  |  |  | Aggressive [MW] |  |  | 20.8067 | 20.9615 | 21.1245 | 21.3017 | 21.4879 | 21.6846 | 21.7758 | 21.8733 | 21.9687 | 22.0699 | 22.1727 | 22.2767 | 22.3864 | 22.4964 | 22.6107 | 22.7299 | 23.313 | 23.8969
|  |  | 2 | Conservative [MW] |  |  | 22.3947 | 22.528 | 22.6636 | 22.801 | 22.9401 | 23.0851 | 23.2116 | 23.3454 | 23.481 | 23.615 | 23.7548 | 23.896 | 24.0381 | 24.1853 | 24.3321 | 24.4782 | 25.2106 | 25.9429
|  |  |  | Best View [MW] |  |  | 22.3947 | 22.5502 | 22.7082 | 22.8689 | 23.035 | 23.203 | 23.3509 | 23.4987 | 23.6504 | 23.8054 | 23.9627 | 24.1268 | 24.2876 | 24.4539 | 24.6201 | 24.7895 | 25.628 | 26.4671
|  |  |  | Base Case [MW] |  |  | 22.3947 | 22.5739 | 22.7592 | 22.9454 | 23.1408 | 23.3395 | 23.5021 | 23.67 | 23.8383 | 24.0111 | 24.1872 | 24.366 | 24.546 | 24.7269 | 24.912 | 25.0988 | 26.028 | 26.9576
|  |  |  | Aggressive [MW] |  |  | 22.3947 | 22.6975 | 23.0161 | 23.3505 | 23.6982 | 24.0583 | 24.2278 | 24.3967 | 24.5689 | 24.7438 | 24.9205 | 25.0965 | 25.2767 | 25.4554 | 25.6362 | 25.8166 | 26.7196 | 27.6226
| BELFIELD | 10 | 1 | Conservative [MW] |  |  | 14.3001 | 14.4028 | 14.5089 | 14.614 | 14.726 | 14.8363 | 14.9208 | 14.4198 | 14.5085 | 14.5953 | 14.687 | 14.7759 | 14.8657 | 14.9599 | 15.0505 | 15.141 | 15.5939 | 16.0468
|  |  |  | Best View [MW] |  |  | 14.3001 | 14.4211 | 14.5426 | 14.6644 | 14.7932 | 14.9211 | 15.0216 | 14.5389 | 14.6429 | 14.7496 | 14.8547 | 14.9617 | 15.0661 | 15.1756 | 15.2855 | 15.3915 | 15.9318 | 16.4714
|  |  |  | Base Case [MW] |  |  | 14.3001 | 14.4346 | 14.5707 | 14.7113 | 14.8557 | 15.003 | 15.1167 | 14.6453 | 14.7652 | 14.8811 | 15.0039 | 15.1215 | 15.2449 | 15.3659 | 15.4868 | 15.6077 | 16.2121 | 16.8165
|  |  |  | Aggressive [MW] |  |  | 14.3001 | 14.4957 | 14.6962 | 14.9069 | 15.1171 | 15.3352 | 15.4462 | 14.9795 | 15.0924 | 15.2054 | 15.3213 | 15.4356 | 15.5477 | 15.66 | 15.7729 | 15.8849 | 16.4472 | 17.0094
| BELGARD | 10 | 1 | Conservative [MW] |  |  | 14.6916 | 14.771 | 14.8492 | 14.9255 | 15.0091 | 15.0905 | 15.1571 | 15.224 | 15.2912 | 15.3585 | 15.4256 | 15.4975 | 15.5688 | 15.6444 | 15.7148 | 15.7891 | 16.1502 | 16.5119
|  |  |  | Best View [MW] |  |  | 14.6916 | 14.7792 | 14.872 | 14.9658 | 15.0599 | 15.1586 | 15.2339 | 15.3122 | 15.3936 | 15.4777 | 15.5599 | 15.6443 | 15.731 | 15.8195 | 15.905 | 15.9967 | 16.4387 | 16.8818
|  |  |  | Base Case [MW] |  |  | 14.6916 | 14.7939 | 14.8951 | 14.9991 | 15.1059 | 15.2189 | 15.3063 | 15.3953 | 15.4903 | 15.5812 | 15.6777 | 15.7742 | 15.8754 | 15.9759 | 16.0757 | 16.1835 | 16.7012 | 17.2202
|  |  |  | Aggressive [MW] |  |  | 14.6916 | 14.8361 | 14.986 | 15.1445 | 15.3096 | 15.4799 | 15.5679 | 15.6575 | 15.7482 | 15.8401 | 15.9373 | 16.0304 | 16.128 | 16.2299 | 16.3313 | 16.4321 | 16.9379 | 17.4435
| BELLFIELD | 10 | 1 | Conservative [MW] |  |  | 12.0715 | 12.0933 | 12.1176 | 12.139 | 12.1626 | 12.186 | 12.2416 | 12.298 | 12.3554 | 12.4164 | 12.4782 | 12.5407 | 12.6036 | 12.6699 | 12.7396 | 12.8094 | 13.1583 | 13.5071
|  |  |  | Best View [MW] |  |  | 12.0715 | 12.1115 | 12.1508 | 12.1916 | 12.2344 | 12.2762 | 12.3381 | 12.4032 | 12.4688 | 12.5374 | 12.6092 | 12.6808 | 12.7554 | 12.8326 | 12.9093 | 12.9914 | 13.3872 | 13.784
|  |  |  | Base Case [MW] |  |  | 12.0715 | 12.1202 | 12.1703 | 12.219 | 12.2716 | 12.3256 | 12.3964 | 12.4672 | 12.5434 | 12.6191 | 12.7002 | 12.7833 | 12.8685 | 12.9551 | 13.0465 | 13.1392 | 13.5991 | 14.0591
|  |  |  | Aggressive [MW] |  |  | 12.0715 | 12.1484 | 12.2247 | 12.3083 | 12.3936 | 12.4803 | 12.5864 | 12.6947 | 12.8077 | 12.9277 | 13.0514 | 13.1812 | 13.3165 | 13.4564 | 13.6 | 13.7534 | 14.4941 | 15.2364
| BELMAYNE | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192
| BELMULLET | 20 | 1 | Conservative [MW] |  |  | 1.5751 | 1.58 | 1.5849 | 1.5929 | 1.5979 | 1.6011 | 1.6174 | 1.6344 | 1.6514 | 1.6692 | 1.6871 | 1.7058 | 1.7244 | 1.7438 | 1.7634 | 1.7838 | 1.8837 | 1.9837
|  |  |  | Best View [MW] |  |  | 1.5751 | 1.5859 | 1.597 | 1.6117 | 1.623 | 1.6326 | 1.6541 | 1.6765 | 1.6992 | 1.7228 | 1.7467 | 1.7715 | 1.7972 | 1.8231 | 1.8499 | 1.8777 | 2.014 | 2.1505
|  |  |  | Base Case [MW] |  |  | 1.5751 | 1.5898 | 1.6046 | 1.6231 | 1.6389 | 1.6526 | 1.6787 | 1.7059 | 1.7337 | 1.7626 | 1.7925 | 1.823 | 1.8545 | 1.8873 | 1.9208 | 1.9556 | 2.1259 | 2.2965
|  |  |  | Aggressive [MW] |  |  | 1.5751 | 1.6031 | 1.6323 | 1.6661 | 1.6977 | 1.7284 | 1.7665 | 1.8059 | 1.8472 | 1.8901 | 1.9348 | 1.9813 | 2.0291 | 2.079 | 2.1303 | 2.1833 | 2.444 | 2.705
| BELVIEW | 20 | 1 | Conservative [MW] |  |  | 23.5343 | 23.6272 | 23.7208 | 23.8149 | 23.9114 | 24.0077 | 24.1306 | 24.255 | 24.3809 | 24.5074 | 24.6369 | 24.7661 | 24.8966 | 25.026 | 25.1581 | 25.2896 | 25.9487 | 26.6077
|  |  |  | Best View [MW] |  |  | 23.5343 | 23.6365 | 23.7402 | 23.845 | 23.9509 | 24.0573 | 24.2152 | 24.3739 | 24.5351 | 24.6997 | 24.8619 | 25.028 | 25.1935 | 25.3604 | 25.5262 | 25.6923 | 26.5219 | 27.3516
|  |  |  | Base Case [MW] |  |  | 23.5343 | 23.6556 | 23.7754 | 23.9004 | 24.0248 | 24.153 | 24.3353 | 24.5205 | 24.7089 | 24.8986 | 25.0907 | 25.2827 | 25.475 | 25.665 | 25.8521 | 26.036 | 26.9643 | 27.8921
|  |  |  | Aggressive [MW] |  |  | 23.5343 | 23.7233 | 23.9196 | 24.1163 | 24.3185 | 24.5225 | 24.7466 | 24.9751 | 25.2044 | 25.4332 | 25.6598 | 25.8847 | 26.1023 | 26.3115 | 26.5064 | 26.6867 | 27.6272 | 28.5653
| BETTYSTOWN | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3192 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 19.3192 | 19.3192 | 19.3192 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 19.3192 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195 | 19.3195
| BIRDHILL | 20 | 1 | Conservative [MW] |  |  | 11.3986 | 11.4432 | 11.4864 | 11.5316 | 11.5753 | 11.621 | 10.1014 | 10.169 | 10.2373 | 10.3089 | 10.3809 | 10.4532 | 10.5258 | 10.6012 | 10.6796 | 10.758 | 11.15 | 11.5421
|  |  |  | Best View [MW] |  |  | 11.3986 | 11.4515 | 11.5057 | 11.5615 | 11.6183 | 11.6766 | 10.1878 | 10.289 | 10.391 | 10.4963 | 10.6044 | 10.7153 | 10.8288 | 10.9439 | 11.0639 | 11.1851 | 11.7878 | 12.3906
|  |  |  | Base Case [MW] |  |  | 11.3986 | 11.471 | 11.5468 | 11.6218 | 11.6995 | 11.7804 | 10.3023 | 10.4123 | 10.5249 | 10.6397 | 10.7591 | 10.8826 | 11.01 | 11.1377 | 11.2683 | 11.4046 | 12.0709 | 12.7382
|  |  |  | Aggressive [MW] |  |  | 11.3986 | 11.5137 | 11.633 | 11.7561 | 11.8819 | 12.0137 | 10.5567 | 10.6849 | 10.8191 | 10.9529 | 11.0915 | 11.2347 | 11.3816 | 11.5348 | 11.6864 | 11.8461 | 12.6229 | 13.4011
| BIRR | 10 | 1 | Conservative [MW] |  |  | 7.4599 | 7.4727 | 7.4889 | 7.5028 | 7.5201 | 7.5348 | 7.5578 | 7.5797 | 7.6026 | 7.6263 | 7.6509 | 7.6763 | 7.7026 | 7.7274 | 7.7551 | 7.7815 | 7.9169 | 8.0521
|  |  |  | Best View [MW] |  |  | 7.4599 | 7.4766 | 7.4947 | 7.514 | 7.5345 | 7.5542 | 7.5864 | 7.6205 | 7.6563 | 7.6915 | 7.7282 | 7.7683 | 7.8076 | 7.8479 | 7.8892 | 7.9335 | 8.1471 | 8.3611
|  |  |  | Base Case [MW] |  |  | 7.4599 | 7.4837 | 7.508 | 7.535 | 7.5606 | 7.5887 | 7.6244 | 7.6635 | 7.7017 | 7.7409 | 7.7832 | 7.8261 | 7.8697 | 7.9158 | 7.9643 | 8.0128 | 8.2555 | 8.4981
|  |  |  | Aggressive [MW] |  |  | 7.4599 | 7.497 | 7.5388 | 7.581 | 7.6254 | 7.6698 | 7.713 | 7.7565 | 7.8043 | 7.8502 | 7.9 | 7.9515 | 8.0045 | 8.0586 | 8.1159 | 8.1738 | 8.4617 | 8.7497
|  | 20 | 1 | Conservative [MW] |  |  | 1.8389 | 1.8656 | 1.893 | 1.9205 | 1.9486 | 1.9769 | 2.0174 | 2.0587 | 2.1007 | 2.1437 | 2.1873 | 2.2319 | 2.2772 | 2.3234 | 2.3705 | 2.4182 | 2.6549 | 2.8918
|  |  |  | Best View [MW] |  |  | 1.8389 | 1.8721 | 1.9059 | 1.9403 | 1.9753 | 2.0108 | 2.0702 | 2.1313 | 2.1942 | 2.2585 | 2.3247 | 2.3925 | 2.462 | 2.5332 | 2.6062 | 2.681 | 3.0501 | 3.4194
|  |  |  | Base Case [MW] |  |  | 1.8389 | 1.8836 | 1.9296 | 1.9766 | 2.0249 | 2.0742 | 2.1396 | 2.2069 | 2.2761 | 2.3474 | 2.4205 | 2.4955 | 2.5725 | 2.6516 | 2.7322 | 2.8149 | 3.2228 | 3.6311
|  |  |  | Aggressive [MW] |  |  | 1.8389 | 1.9096 | 1.9832 | 2.0594 | 2.1385 | 2.2205 | 2.2966 | 2.3749 | 2.4556 | 2.5387 | 2.6239 | 2.7115 | 2.8012 | 2.8931 | 2.9869 | 3.0831 | 3.5579 | 4.033
| BISHOPSTOWN | 10 | 1 | Conservative [MW] |  |  | 12.9601 | 13.0266 | 13.097 | 13.167 | 13.2414 | 21.9654 | 22.0479 | 22.1277 | 22.21 | 22.2959 | 22.3815 | 22.4662 | 22.5542 | 22.6454 | 22.7398 | 22.8324 | 23.3001 | 23.7676
|  |  |  | Best View [MW] |  |  | 12.9601 | 13.0312 | 13.1052 | 13.1785 | 13.2552 | 21.9914 | 22.0961 | 22.2072 | 22.3208 | 22.4383 | 22.5553 | 22.6796 | 22.8022 | 22.9317 | 23.0631 | 23.196 | 23.8564 | 24.5171
|  |  |  | Base Case [MW] |  |  | 12.9601 | 13.0564 | 13.1604 | 13.2632 | 13.3687 | 22.1496 | 22.2586 | 22.3736 | 22.4948 | 22.6148 | 22.738 | 22.8635 | 22.9955 | 23.1292 | 23.2639 | 23.4035 | 24.0885 | 24.7743
|  |  |  | Aggressive [MW] |  |  | 12.9601 | 13.084 | 13.21 | 13.3379 | 13.4762 | 22.2951 | 22.4393 | 22.5929 | 22.7496 | 22.9151 | 23.0804 | 23.2528 | 23.4315 | 23.6152 | 23.8029 | 23.9928 | 24.9364 | 25.8804
| BLAKE | 10 | 1 | Conservative [MW] |  |  | 1.5787 | 1.6106 | 1.6428 | 1.6754 | 1.7092 | 14.2543 | 14.3059 | 14.3589 | 14.4121 | 14.4678 | 14.5237 | 14.5821 | 14.642 | 14.7032 | 14.7644 | 14.8282 | 15.1404 | 15.453
|  |  |  | Best View [MW] |  |  | 1.5787 | 1.6189 | 1.66 | 1.7017 | 1.7447 | 14.3075 | 14.3758 | 14.4468 | 14.5191 | 14.5955 | 14.672 | 14.7524 | 14.8354 | 14.9199 | 15.0082 | 15.0978 | 15.5423 | 15.987
|  |  |  | Base Case [MW] |  |  | 1.5787 | 1.6267 | 1.6758 | 1.7262 | 1.778 | 14.3574 | 14.439 | 14.5234 | 14.6105 | 14.7004 | 14.7941 | 14.8918 | 14.9922 | 15.0963 | 15.2042 | 15.3158 | 15.8639 | 16.4127
|  |  |  | Aggressive [MW] |  |  | 1.5787 | 1.6402 | 1.7044 | 1.7701 | 1.8376 | 14.4483 | 14.5504 | 14.6555 | 14.7658 | 14.8814 | 15.001 | 15.1255 | 15.2565 | 15.3923 | 15.5329 | 15.6796 | 16.3968 | 17.1151
| BLANCHFIELD | 20 | 1 | Conservative [MW] |  |  | 3.581 | 3.581 | 3.5812 | 3.5812 | 3.5814 | 3.5813 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816
|  |  |  | Best View [MW] |  |  | 3.581 | 3.581 | 3.5812 | 3.5814 | 3.5813 | 3.5813 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5817 | 3.5821 | 3.5824
|  |  |  | Base Case [MW] |  |  | 3.581 | 3.581 | 3.5812 | 3.5813 | 3.5815 | 3.5815 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5817 | 3.5819 | 3.582 | 3.5827 | 3.5834
|  |  |  | Aggressive [MW] |  |  | 3.581 | 3.581 | 3.5813 | 3.5815 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5816 | 3.5819 | 3.582 | 3.5822 | 3.5824 | 3.5826 | 3.5836 | 3.5846
|  |  | 2 | Conservative [MW] |  |  | 8.0758 | 8.0758 | 8.0758 | 8.0758 | 8.0758 | 8.0758 | 8.0758 | 8.0755 | 8.0755 | 8.0752 | 8.0752 | 8.0749 | 8.0747 | 8.0747 | 8.0744 | 8.0741 | 8.0727 | 8.0712
|  |  |  | Best View [MW] |  |  | 8.0758 | 8.0758 | 8.0758 | 8.0758 | 8.0758 | 8.0758 | 8.0755 | 8.0755 | 8.0752 | 8.0749 | 8.0747 | 8.0744 | 8.0741 | 8.0738 | 8.0735 | 8.0735 | 8.0728 | 8.0721
|  |  |  | Base Case [MW] |  |  | 8.0758 | 8.0758 | 8.0758 | 8.0758 | 8.0758 | 8.0758 | 8.0752 | 8.0752 | 8.0749 | 8.0747 | 8.0744 | 8.0738 | 8.0735 | 8.0735 | 8.0735 | 8.0735 | 8.0735 | 8.0735
|  |  |  | Aggressive [MW] |  |  | 8.0758 | 8.0758 | 8.0758 | 8.0758 | 8.0758 | 8.0755 | 8.0747 | 8.0744 | 8.0741 | 8.0738 | 8.0735 | 8.0735 | 8.0735 | 8.0735 | 8.0738 | 8.0738 | 8.0746 | 8.0753
| BLESSINGTON | 20 | 1 | Conservative [MW] |  |  | 0.4434 | 0.51175 | 6.8942 | 6.9691 | 7.0462 | 7.1254 | 7.1868 | 7.2501 | 7.3141 | 7.3802 | 7.4469 | 7.5155 | 7.5856 | 7.6565 | 7.7293 | 7.804 | 8.1725 | 8.5413
|  |  |  | Best View [MW] |  |  | 0.4434 | 0.52231 | 6.9174 | 7.0047 | 7.0946 | 7.188 | 7.2618 | 7.3374 | 7.4145 | 7.4939 | 7.5755 | 7.6587 | 7.7434 | 7.8306 | 7.9199 | 8.011 | 8.4617 | 8.9127
|  |  |  | Base Case [MW] |  |  | 0.4434 | 0.53236 | 6.9386 | 7.0376 | 7.1404 | 7.2469 | 7.3312 | 7.4173 | 7.5066 | 7.5976 | 7.6913 | 7.7872 | 7.8866 | 7.9878 | 8.0915 | 8.1986 | 8.725 | 9.2519
|  |  |  | Aggressive [MW] |  |  | 0.4434 | 0.57294 | 7.0269 | 7.1761 | 7.3333 | 7.4986 | 7.5842 | 7.6719 | 7.7622 | 7.8549 | 7.9492 | 8.0465 | 8.1458 | 8.2474 | 8.3522 | 8.4586 | 8.9862 | 9.5141
| BOGHALL ROAD | 10 | 1 | Conservative [MW] |  |  | 14.1468 | 14.2234 | 14.3074 | 14.3893 | 14.4734 | 14.5639 | 14.6286 | 14.6981 | 14.7674 | 14.8411 | 14.9099 | 14.9831 | 15.0599 | 15.1364 | 15.2114 | 15.2904 | 15.6746 | 16.0595
|  |  |  | Best View [MW] |  |  | 14.1468 | 14.2387 | 14.3311 | 14.4283 | 14.5295 | 14.6301 | 14.7102 | 14.7935 | 14.8746 | 14.9626 | 15.0482 | 15.1359 | 15.225 | 15.3155 | 15.4121 | 15.5041 | 15.9763 | 16.4477
|  |  |  | Base Case [MW] |  |  | 14.1468 | 14.2473 | 14.3551 | 14.465 | 14.5763 | 14.6934 | 14.7843 | 14.8806 | 14.973 | 15.0702 | 15.1722 | 15.2737 | 15.3746 | 15.4786 | 15.5852 | 15.6946 | 16.2344 | 16.7745
|  |  |  | Aggressive [MW] |  |  | 14.1468 | 14.2958 | 14.4536 | 14.618 | 14.7873 | 14.9641 | 15.0595 | 15.1509 | 15.2433 | 15.3408 | 15.4384 | 15.5398 | 15.6408 | 15.7401 | 15.8429 | 15.9487 | 16.4697 | 16.9912
| BOOLTIAGH | 20 | 1 | Conservative [MW] |  |  | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197
|  |  |  | Best View [MW] |  |  | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197
|  |  |  | Base Case [MW] |  |  | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197
|  |  |  | Aggressive [MW] |  |  | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197 | 4.2197
| BORRISOLEIGH | 20 | 1 | Conservative [MW] |  |  | 0 | 6.175 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229
|  |  |  | Best View [MW] |  |  | 0 | 6.175 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229
|  |  |  | Base Case [MW] |  |  | 0 | 6.175 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229
|  |  |  | Aggressive [MW] |  |  | 0 | 6.175 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229 | 6.7229
| BOYLE | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.099227 | 0.20933 | 0.3224 | 0.87984 | 1.4378
| BRAY | 10 | 1 | Conservative [MW] |  |  | 12.9677 | 13.046 | 13.1273 | 13.2109 | 13.2922 | 13.3797 | 13.4462 | 13.517 | 13.5834 | 13.6542 | 13.7294 | 13.7994 | 13.8737 | 13.9519 | 14.0244 | 14.1052 | 14.487 | 14.8701
|  |  |  | Best View [MW] |  |  | 12.9677 | 13.0571 | 13.1514 | 13.2461 | 13.3447 | 13.4477 | 13.5297 | 13.6099 | 13.6931 | 13.7785 | 13.8662 | 13.9514 | 14.0428 | 14.1311 | 14.2252 | 14.315 | 14.7754 | 15.2351
|  |  |  | Base Case [MW] |  |  | 12.9677 | 13.0702 | 13.1757 | 13.2835 | 13.3974 | 13.5126 | 13.6053 | 13.6944 | 13.789 | 13.8887 | 13.9888 | 14.0881 | 14.1917 | 14.2936 | 14.3988 | 14.5065 | 15.0384 | 15.5707
|  |  |  | Aggressive [MW] |  |  | 12.9677 | 13.1155 | 13.2717 | 13.4352 | 13.6037 | 13.7847 | 13.8728 | 13.9668 | 14.0618 | 14.1571 | 14.2522 | 14.3518 | 14.4507 | 14.5532 | 14.6593 | 14.7634 | 15.2893 | 15.8148
| BREWERY ROAD | 10 | 1 | Conservative [MW] |  |  | 14.0614 | 14.144 | 14.2332 | 14.3193 | 14.4071 | 14.5007 | 14.5727 | 14.6444 | 14.7201 | 14.7951 | 14.8694 | 14.9473 | 15.0237 | 15.1036 | 15.1821 | 15.2635 | 15.6628 | 16.0625
|  |  |  | Best View [MW] |  |  | 14.0614 | 14.1566 | 14.2601 | 14.3629 | 14.4647 | 14.5738 | 14.6582 | 14.7448 | 14.8333 | 14.9232 | 15.0148 | 15.1026 | 15.196 | 15.2951 | 15.3892 | 15.4881 | 15.97 | 16.4526
|  |  |  | Base Case [MW] |  |  | 14.0614 | 14.1717 | 14.2833 | 14.4007 | 14.5185 | 14.6406 | 14.7374 | 14.8339 | 14.935 | 15.0353 | 15.1394 | 15.2465 | 15.352 | 15.4596 | 15.5743 | 15.6851 | 16.2497 | 16.8136
|  |  |  | Aggressive [MW] |  |  | 14.0614 | 14.2191 | 14.3874 | 14.5602 | 14.7397 | 14.9283 | 15.0236 | 15.1187 | 15.2186 | 15.3182 | 15.4214 | 15.5229 | 15.6277 | 15.7352 | 15.8388 | 15.9494 | 16.4838 | 17.0194
| BRUFF | 10 | 1 | Conservative [MW] |  |  | 3.705 | 3.7132 | 3.7212 | 3.7309 | 3.7383 | 3.7474 | 3.7592 | 3.7703 | 3.783 | 3.795 | 3.8064 | 3.8193 | 3.8336 | 3.8472 | 3.8601 | 3.8744 | 3.9422 | 4.0103
|  |  |  | Best View [MW] |  |  | 3.705 | 3.7163 | 3.7252 | 3.7357 | 3.7458 | 3.7554 | 3.7737 | 3.7906 | 3.8085 | 3.8271 | 3.8464 | 3.8664 | 3.887 | 3.908 | 3.9297 | 3.9516 | 4.0604 | 4.1692
|  |  |  | Base Case [MW] |  |  | 3.705 | 3.7186 | 3.7316 | 3.7458 | 3.7591 | 3.7737 | 3.7927 | 3.8123 | 3.8325 | 3.8532 | 3.8743 | 3.8958 | 3.9176 | 3.9417 | 3.9659 | 3.9901 | 4.1111 | 4.2322
|  |  |  | Aggressive [MW] |  |  | 3.705 | 3.7258 | 3.7469 | 3.77 | 3.7932 | 3.8162 | 3.838 | 3.8601 | 3.8824 | 3.9048 | 3.9293 | 3.956 | 3.9803 | 4.0087 | 4.0344 | 4.0639 | 4.2014 | 4.3395
|  | 20 | 1 | Conservative [MW] |  |  | 3.2599 | 3.2597 | 3.2596 | 3.2612 | 3.2609 | 3.2607 | 3.2605 | 3.2621 | 3.2617 | 3.2614 | 3.2611 | 3.2626 | 3.2622 | 3.262 | 3.2635 | 3.2631 | 3.266 | 3.2687
|  |  |  | Best View [MW] |  |  | 3.2599 | 3.2597 | 3.2595 | 3.2611 | 3.2608 | 3.2605 | 3.262 | 3.2615 | 3.2611 | 3.2624 | 3.262 | 3.2633 | 3.2628 | 3.2641 | 3.2636 | 3.2648 | 3.2664 | 3.2683
|  |  |  | Base Case [MW] |  |  | 3.2599 | 3.2596 | 3.2611 | 3.2608 | 3.2605 | 3.2619 | 3.2614 | 3.2629 | 3.2623 | 3.2638 | 3.2631 | 3.2645 | 3.2638 | 3.2651 | 3.2644 | 3.2656 | 3.2666 | 3.268
|  |  |  | Aggressive [MW] |  |  | 3.2599 | 3.2595 | 3.2607 | 3.2622 | 3.2614 | 3.2627 | 3.2622 | 3.2635 | 3.2629 | 3.2641 | 3.2636 | 3.2647 | 3.2659 | 3.2652 | 3.2663 | 3.2673 | 3.2726 | 3.2779
| BUNCLODY | 20 | 1 | Conservative [MW] |  |  | 6.639 | 6.6616 | 6.6788 | 6.7 | 6.7203 | 6.7444 | 6.7905 | 6.8413 | 6.8918 | 6.9421 | 6.9964 | 7.0499 | 7.1072 | 7.1633 | 7.2176 | 7.2751 | 7.554 | 7.8334
|  |  |  | Best View [MW] |  |  | 6.639 | 6.6735 | 6.71 | 6.7489 | 6.7852 | 6.8234 | 6.8778 | 6.9309 | 6.9921 | 7.0467 | 7.1088 | 7.1685 | 7.2304 | 7.294 | 7.3591 | 7.425 | 7.7523 | 8.0797
|  |  |  | Base Case [MW] |  |  | 6.639 | 6.685 | 6.7274 | 6.7706 | 6.8193 | 6.8637 | 6.9262 | 6.9907 | 7.0519 | 7.1193 | 7.1876 | 7.2565 | 7.3252 | 7.3932 | 7.4651 | 7.5405 | 7.9081 | 8.2764
|  |  |  | Aggressive [MW] |  |  | 6.639 | 6.7092 | 6.7797 | 6.8499 | 6.924 | 7.0014 | 7.091 | 7.1838 | 7.2733 | 7.3736 | 7.473 | 7.575 | 7.6724 | 7.7798 | 7.8781 | 7.9804 | 8.4814 | 8.9831
| BUNCRANA | 20 | 1 | Conservative [MW] |  |  | 7.112 | 7.1295 | 7.1418 | 7.1584 | 7.1745 | 7.1901 | 7.2242 | 7.2652 | 7.2986 | 7.3389 | 7.3808 | 7.4197 | 7.4604 | 7.4977 | 7.5412 | 7.5863 | 7.8075 | 8.0289
|  |  |  | Best View [MW] |  |  | 7.112 | 7.1475 | 7.181 | 7.2167 | 7.2502 | 7.2861 | 7.3371 | 7.3918 | 7.4501 | 7.507 | 7.5671 | 7.6249 | 7.6853 | 7.7479 | 7.8124 | 7.8731 | 8.1869 | 8.5
|  |  |  | Base Case [MW] |  |  | 7.112 | 7.1517 | 7.1887 | 7.2274 | 7.2634 | 7.3056 | 7.3663 | 7.4333 | 7.5013 | 7.5701 | 7.6393 | 7.708 | 7.7807 | 7.8569 | 7.9311 | 8.0074 | 8.3832 | 8.7594
|  |  |  | Aggressive [MW] |  |  | 7.112 | 7.1711 | 7.2285 | 7.2885 | 7.3511 | 7.4108 | 7.4903 | 7.5678 | 7.647 | 7.7277 | 7.8136 | 7.899 | 7.9879 | 8.0791 | 8.1663 | 8.2588 | 8.7073 | 9.1567
| BUNDORAN | 10 | 1 | Conservative [MW] |  |  | 6.7237 | 6.7352 | 6.7464 | 6.7615 | 6.7766 | 6.7866 | 6.8193 | 6.85 | 6.8833 | 6.9145 | 6.9482 | 6.9797 | 7.0181 | 7.0497 | 7.088 | 7.1238 | 7.3095 | 7.4948
|  |  |  | Best View [MW] |  |  | 6.7237 | 6.7516 | 6.778 | 6.8072 | 6.835 | 6.8654 | 6.9083 | 6.9562 | 7.0044 | 7.0528 | 7.1012 | 7.1538 | 7.2062 | 7.2579 | 7.3132 | 7.3722 | 7.6575 | 7.9434
|  |  |  | Base Case [MW] |  |  | 6.7237 | 6.7516 | 6.7864 | 6.819 | 6.854 | 6.8869 | 6.9403 | 6.9971 | 7.0524 | 7.1106 | 7.1713 | 7.2342 | 7.2989 | 7.365 | 7.4323 | 7.5001 | 7.8376 | 8.1752
|  |  |  | Aggressive [MW] |  |  | 6.7237 | 6.7721 | 6.8204 | 6.8725 | 6.9241 | 6.9792 | 7.0452 | 7.1117 | 7.1831 | 7.2541 | 7.3333 | 7.4063 | 7.4863 | 7.568 | 7.6554 | 7.7428 | 8.1796 | 8.6165
| BUSH | 20 | 1 | Conservative [MW] |  |  | 1.8924 | 1.912 | 1.9318 | 1.9523 | 1.9732 | 1.9949 | 2.0178 | 2.0416 | 2.0661 | 2.091 | 2.1164 | 2.1425 | 2.1691 | 2.1965 | 2.2242 | 2.2529 | 2.3939 | 2.535
|  |  |  | Best View [MW] |  |  | 1.8924 | 1.9143 | 1.9362 | 1.9594 | 1.9825 | 2.0068 | 2.0393 | 2.0724 | 2.1071 | 2.1426 | 2.1791 | 2.217 | 2.256 | 2.2962 | 2.3378 | 2.3811 | 2.5928 | 2.8049
|  |  |  | Base Case [MW] |  |  | 1.8924 | 1.924 | 1.9567 | 1.9908 | 2.0261 | 2.0623 | 2.1006 | 2.1407 | 2.1818 | 2.2242 | 2.2686 | 2.3144 | 2.3615 | 2.4108 | 2.4608 | 2.5135 | 2.77 | 3.0269
|  |  |  | Aggressive [MW] |  |  | 1.8924 | 1.9355 | 1.9805 | 2.0278 | 2.0771 | 2.1293 | 2.1771 | 2.2265 | 2.2783 | 2.3316 | 2.3873 | 2.4453 | 2.5057 | 2.5691 | 2.6342 | 2.7016 | 3.0325 | 3.3637
| BUSHFIELD | 10 | 1 | Conservative [MW] |  |  | 13.8223 | 13.87 | 13.9158 | 13.9596 | 14.0058 | 14.0545 | 14.1325 | 14.2135 | 14.2932 | 14.3711 | 14.4565 | 14.5396 | 14.6208 | 14.7084 | 14.7935 | 14.8849 | 15.3251 | 15.7663
|  |  |  | Best View [MW] |  |  | 13.8223 | 13.8922 | 13.966 | 14.0394 | 14.1126 | 14.1894 | 14.2981 | 14.4131 | 14.5289 | 14.6499 | 14.7661 | 14.8905 | 15.0136 | 15.1441 | 15.2713 | 15.3991 | 16.0365 | 16.6741
|  |  |  | Base Case [MW] |  |  | 13.8223 | 13.9216 | 14.0248 | 14.1272 | 14.2372 | 14.3452 | 14.4663 | 14.5959 | 14.7226 | 14.856 | 14.9904 | 15.1244 | 15.2622 | 15.4031 | 15.5451 | 15.6872 | 16.3974 | 17.1076
|  |  |  | Aggressive [MW] |  |  | 13.8223 | 13.9754 | 14.1328 | 14.2979 | 14.4638 | 14.6384 | 14.7843 | 14.9282 | 15.0779 | 15.2321 | 15.3845 | 15.5384 | 15.6976 | 15.8542 | 16.0119 | 16.168 | 16.9527 | 17.7371
| BUTTEVANT | 10 | 1 | Conservative [MW] |  |  | 2.4042 | 2.4318 | 2.4602 | 2.4891 | 2.5188 | 2.5488 | 2.5789 | 2.6099 | 2.6419 | 2.6742 | 2.7067 | 2.7409 | 2.7745 | 2.81 | 2.8456 | 2.8823 | 3.0628 | 3.2434
|  |  |  | Best View [MW] |  |  | 2.4042 | 2.4333 | 2.4633 | 2.4937 | 2.525 | 2.5574 | 2.5984 | 2.6407 | 2.6841 | 2.7287 | 2.7744 | 2.8213 | 2.8701 | 2.9201 | 2.9702 | 3.0233 | 3.2809 | 3.5391
|  |  |  | Base Case [MW] |  |  | 2.4042 | 2.4443 | 2.4851 | 2.5276 | 2.5715 | 2.6166 | 2.6593 | 2.7038 | 2.7496 | 2.7964 | 2.8444 | 2.8945 | 2.9447 | 2.9969 | 3.0502 | 3.1053 | 3.3762 | 3.6474
|  |  |  | Aggressive [MW] |  |  | 2.4042 | 2.4593 | 2.5174 | 2.5774 | 2.6406 | 2.7061 | 2.7524 | 2.8006 | 2.85 | 2.9013 | 2.9538 | 3.0073 | 3.0619 | 3.1185 | 3.176 | 3.2353 | 3.5272 | 3.8194
| CAHERDAVIN | 10 | 1 | Conservative [MW] |  |  | 12.9444 | 12.9839 | 13.0298 | 13.0736 | 13.1195 | 13.1635 | 13.216 | 13.2699 | 13.3209 | 13.3776 | 13.4313 | 13.4903 | 13.5461 | 13.6072 | 13.6693 | 13.7275 | 14.0289 | 14.3296
|  |  |  | Best View [MW] |  |  | 12.9444 | 12.986 | 13.0296 | 13.0754 | 13.1235 | 13.169 | 13.2392 | 13.3124 | 13.385 | 13.4603 | 13.5382 | 13.6191 | 13.702 | 13.7872 | 13.874 | 13.9624 | 14.4003 | 14.8384
|  |  |  | Base Case [MW] |  |  | 12.9444 | 13.0045 | 13.0649 | 13.1295 | 13.1944 | 13.259 | 13.3427 | 13.428 | 13.5188 | 13.6101 | 13.7017 | 13.7977 | 13.8979 | 14.0013 | 14.1077 | 14.2168 | 14.7552 | 15.294
|  |  |  | Aggressive [MW] |  |  | 12.9444 | 13.0409 | 13.14 | 13.2446 | 13.3547 | 13.4697 | 13.5691 | 13.6721 | 13.7734 | 13.8814 | 13.9958 | 14.1113 | 14.2272 | 14.3471 | 14.4756 | 14.6024 | 15.2407 | 15.8788
| CAHIR | 10 | 1 | Conservative [MW] |  |  | 9.7095 | 9.756 | 9.8039 | 9.8514 | 9.9002 | 9.9486 | 10.0152 | 10.0808 | 10.1491 | 10.2203 | 10.2902 | 10.3629 | 10.4382 | 10.514 | 10.5904 | 10.6692 | 11.0567 | 11.4446
|  |  |  | Best View [MW] |  |  | 9.7095 | 9.7615 | 9.8148 | 9.8693 | 9.9251 | 9.9802 | 10.0712 | 10.1659 | 10.2605 | 10.3608 | 10.4624 | 10.5653 | 10.6735 | 10.7825 | 10.8944 | 11.0086 | 11.5734 | 12.1386
|  |  |  | Base Case [MW] |  |  | 9.7095 | 9.7784 | 9.8499 | 9.9223 | 9.9955 | 10.0712 | 10.1742 | 10.2786 | 10.3863 | 10.4967 | 10.6101 | 10.728 | 10.8481 | 10.9724 | 11.0982 | 11.2275 | 11.8647 | 12.5024
|  |  |  | Aggressive [MW] |  |  | 9.7095 | 9.8178 | 9.9292 | 10.0453 | 10.1659 | 10.289 | 10.4101 | 10.5334 | 10.6627 | 10.7957 | 10.9317 | 11.0706 | 11.2163 | 11.3636 | 11.5141 | 11.6698 | 12.4346 | 13.2002
| CAHIRCALLA | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| CALLAN | 10 | 1 | Conservative [MW] |  |  | 1.9614 | 1.9804 | 2 | 2.0193 | 2.0393 | 2.0596 | 2.0895 | 2.1197 | 2.151 | 2.1825 | 2.215 | 2.2485 | 2.2823 | 2.317 | 2.3521 | 2.3881 | 2.5654 | 2.743
|  |  |  | Best View [MW] |  |  | 1.9614 | 1.9846 | 2.0081 | 2.0324 | 2.057 | 2.0824 | 2.1228 | 2.165 | 2.2078 | 2.2519 | 2.2978 | 2.3449 | 2.3932 | 2.4428 | 2.4935 | 2.5461 | 2.8042 | 3.0627
|  |  |  | Base Case [MW] |  |  | 1.9614 | 1.989 | 2.0175 | 2.0463 | 2.0755 | 2.1057 | 2.1551 | 2.2053 | 2.2582 | 2.3119 | 2.3684 | 2.4263 | 2.4863 | 2.5476 | 2.6117 | 2.6769 | 2.9999 | 3.3232
|  |  |  | Aggressive [MW] |  |  | 1.9614 | 2.0075 | 2.0551 | 2.1044 | 2.1557 | 2.2092 | 2.2737 | 2.3398 | 2.4098 | 2.4823 | 2.557 | 2.6356 | 2.7163 | 2.8008 | 2.888 | 2.9778 | 3.4201 | 3.8627
| CAMDEN ROW | 10 | 1 | Conservative [MW] |  |  | 13.0815 | 13.1643 | 13.2477 | 13.3312 | 13.4172 | 13.5056 | 13.5839 | 13.6634 | 13.7436 | 13.8243 | 13.905 | 13.988 | 14.0693 | 14.1519 | 14.2353 | 14.3164 | 14.7283 | 15.1397
|  |  |  | Best View [MW] |  |  | 13.0815 | 13.1775 | 13.276 | 13.3735 | 13.4746 | 13.5789 | 13.6661 | 13.7566 | 13.8451 | 13.9365 | 14.0294 | 14.1206 | 14.2099 | 14.3017 | 14.3927 | 14.4819 | 14.9328 | 15.3833
|  |  |  | Base Case [MW] |  |  | 13.0815 | 13.1923 | 13.3058 | 13.4209 | 13.5396 | 13.6613 | 13.7581 | 13.856 | 13.9538 | 14.0532 | 14.1535 | 14.2542 | 14.3514 | 14.4493 | 14.5473 | 14.6438 | 15.1302 | 15.6163
|  |  |  | Aggressive [MW] |  |  | 13.0815 | 13.2701 | 13.4655 | 13.6658 | 13.8702 | 14.0818 | 14.1759 | 14.2718 | 14.366 | 14.4602 | 14.5503 | 14.6417 | 14.7328 | 14.8168 | 14.9015 | 14.9829 | 15.3989 | 15.8142
| CAPPAMORE | 10 | 1 | Conservative [MW] |  |  | 2.4669 | 2.4919 | 2.5169 | 2.5429 | 2.569 | 2.5951 | 2.6317 | 2.6671 | 2.7048 | 2.7423 | 2.7809 | 2.8206 | 2.8614 | 2.9019 | 2.9434 | 2.9859 | 3.1959 | 3.406
|  |  |  | Best View [MW] |  |  | 2.4669 | 2.4973 | 2.5278 | 2.5594 | 2.591 | 2.6236 | 2.6764 | 2.7302 | 2.7849 | 2.8417 | 2.8993 | 2.9602 | 3.0204 | 3.0839 | 3.1478 | 3.2133 | 3.5365 | 3.8599
|  |  |  | Base Case [MW] |  |  | 2.4669 | 2.5071 | 2.5485 | 2.591 | 2.6345 | 2.6792 | 2.7369 | 2.7955 | 2.8561 | 2.9188 | 2.9834 | 3.0484 | 3.1167 | 3.1849 | 3.2563 | 3.3288 | 3.6884 | 4.0481
|  |  |  | Aggressive [MW] |  |  | 2.4669 | 2.5305 | 2.5964 | 2.6643 | 2.7356 | 2.8087 | 2.8745 | 2.9408 | 3.009 | 3.0788 | 3.1516 | 3.2258 | 3.3011 | 3.3789 | 3.4592 | 3.5397 | 3.9417 | 4.3438
| CARNDONAGH | 20 | 1 | Conservative [MW] |  |  | 6.6513 | 6.6667 | 6.6818 | 6.7009 | 6.7151 | 6.7333 | 6.7673 | 6.808 | 6.8457 | 6.8851 | 6.9263 | 6.969 | 7.0083 | 7.0492 | 7.096 | 7.1391 | 7.3646 | 7.5894
|  |  |  | Best View [MW] |  |  | 6.6513 | 6.6872 | 6.7208 | 6.7568 | 6.7949 | 6.8306 | 6.8835 | 6.94 | 6.9998 | 7.0576 | 7.1182 | 7.1811 | 7.2412 | 7.3029 | 7.3708 | 7.4344 | 7.764 | 8.0929
|  |  |  | Base Case [MW] |  |  | 6.6513 | 6.6908 | 6.7321 | 6.7706 | 6.8106 | 6.852 | 6.9181 | 6.9852 | 7.0529 | 7.1206 | 7.1929 | 7.2644 | 7.339 | 7.4163 | 7.4907 | 7.5715 | 7.9583 | 8.3462
|  |  |  | Aggressive [MW] |  |  | 6.6513 | 6.7122 | 6.7714 | 6.8327 | 6.8962 | 6.9612 | 7.0389 | 7.1185 | 7.2044 | 7.2857 | 7.3713 | 7.4601 | 7.5515 | 7.6384 | 7.7305 | 7.8209 | 8.2775 | 8.7338
| CAROLINE STREET | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162
| CARRAROE | 10 | 1 | Conservative [MW] |  |  | 1.4558 | 1.4737 | 1.4923 | 1.5107 | 1.5297 | 1.5487 | 1.5745 | 1.601 | 1.6279 | 1.6551 | 1.6827 | 1.7105 | 1.739 | 1.7677 | 1.7967 | 1.8257 | 1.9707 | 2.1157
|  |  |  | Best View [MW] |  |  | 1.4558 | 1.4785 | 1.5017 | 1.5249 | 1.5489 | 1.5732 | 1.61 | 1.648 | 1.6867 | 1.726 | 1.7661 | 1.8066 | 1.8479 | 1.8898 | 1.9316 | 1.9738 | 2.1839 | 2.394
|  |  |  | Base Case [MW] |  |  | 1.4558 | 1.4845 | 1.5142 | 1.544 | 1.5749 | 1.6058 | 1.6469 | 1.6891 | 1.7322 | 1.7761 | 1.8203 | 1.8655 | 1.9111 | 1.9574 | 2.0037 | 2.0504 | 2.2829 | 2.5154
|  |  |  | Aggressive [MW] |  |  | 1.4558 | 1.5011 | 1.5476 | 1.5957 | 1.6452 | 1.696 | 1.7453 | 1.7961 | 1.8473 | 1.8992 | 1.9519 | 2.0052 | 2.0583 | 2.1112 | 2.1639 | 2.2152 | 2.4755 | 2.7355
| CARRICK ON SHANNON | 10 | 1 | Conservative [MW] |  |  | 3.3602 | 3.388 | 3.4156 | 3.4442 | 3.4725 | 3.502 | 3.5565 | 3.6126 | 3.6689 | 3.7249 | 3.7824 | 3.8395 | 3.8977 | 3.9553 | 4.0119 | 4.0712 | 4.3603 | 4.6499
|  |  |  | Best View [MW] |  |  | 3.3602 | 3.4076 | 3.4555 | 3.5054 | 3.5543 | 3.6037 | 3.6783 | 3.7531 | 3.8295 | 3.9055 | 3.9824 | 4.0579 | 4.1334 | 4.2107 | 4.2848 | 4.357 | 4.7231 | 5.0889
|  |  |  | Base Case [MW] |  |  | 3.3602 | 3.4225 | 3.4874 | 3.5522 | 3.6181 | 3.685 | 3.7717 | 3.8617 | 3.9514 | 4.04 | 4.1303 | 4.22 | 4.3056 | 4.3903 | 4.473 | 4.5495 | 4.9484 | 5.3464
|  |  |  | Aggressive [MW] |  |  | 3.3602 | 3.4567 | 3.5566 | 3.6581 | 3.7603 | 3.8643 | 3.9792 | 4.0941 | 4.2052 | 4.3167 | 4.4242 | 4.5247 | 4.6194 | 4.6985 | 4.7607 | 4.8013 | 5.0618 | 5.3186
| CARRICKMACROSS | 10 | 1 | Conservative [MW] |  |  | 13.3677 | 13.4285 | 13.4859 | 13.5442 | 13.6038 | 13.669 | 13.7504 | 13.8388 | 13.9289 | 14.0157 | 14.109 | 14.198 | 14.293 | 14.388 | 14.4829 | 14.5829 | 15.0694 | 15.5567
|  |  |  | Best View [MW] |  |  | 13.3677 | 13.4453 | 13.5172 | 13.5973 | 13.6759 | 13.7534 | 13.8734 | 13.9935 | 14.1173 | 14.2448 | 14.3744 | 14.5011 | 14.6382 | 14.7704 | 14.9069 | 15.046 | 15.7347 | 16.4238
|  |  |  | Base Case [MW] |  |  | 13.3677 | 13.4618 | 13.5565 | 13.6517 | 13.7511 | 13.8549 | 13.9848 | 14.1206 | 14.2611 | 14.4005 | 14.5475 | 14.6911 | 14.8405 | 14.9933 | 15.1493 | 15.3053 | 16.0852 | 16.8651
|  |  |  | Aggressive [MW] |  |  | 13.3677 | 13.5114 | 13.6617 | 13.8174 | 13.9727 | 14.1353 | 14.3035 | 14.4761 | 14.6498 | 14.8294 | 15.0115 | 15.1983 | 15.3871 | 15.5743 | 15.7618 | 15.9425 | 16.8642 | 17.7847
| CARRICKMINES | 10 | 1 | Conservative [MW] |  |  | 10.954 | 11.0473 | 11.1419 | 11.2404 | 11.3399 | 11.443 | 11.5232 | 11.6027 | 11.6848 | 11.7661 | 11.8498 | 11.9323 | 12.0202 | 12.1066 | 12.1949 | 12.2812 | 12.7179 | 13.1543
|  |  |  | Best View [MW] |  |  | 10.954 | 11.0633 | 11.1724 | 11.2867 | 11.4029 | 11.5241 | 11.6162 | 11.7128 | 11.8104 | 11.9086 | 12.0071 | 12.1093 | 12.2115 | 12.3129 | 12.4172 | 12.5239 | 13.051 | 13.5786
|  |  |  | Base Case [MW] |  |  | 10.954 | 11.075 | 11.2 | 11.3317 | 11.463 | 11.5999 | 11.7042 | 11.8144 | 11.9237 | 12.035 | 12.1484 | 12.2629 | 12.3786 | 12.4946 | 12.6144 | 12.7368 | 13.342 | 13.9477
|  |  |  | Aggressive [MW] |  |  | 10.954 | 11.1313 | 11.3151 | 11.5073 | 11.7059 | 11.9121 | 12.0165 | 12.1239 | 12.2338 | 12.3422 | 12.4523 | 12.564 | 12.6763 | 12.7885 | 12.9045 | 13.0156 | 13.584 | 14.1517
| CARRIGALINE | 10 | 1 | Conservative [MW] |  |  | 5.0639 | 5.1022 | 5.1422 | 5.1838 | 5.2226 | 4.6735 | 4.7137 | 4.7588 | 4.8015 | 4.8452 | 4.8863 | 4.932 | 4.9786 | 5.0221 | 5.07 | 5.1185 | 5.3593 | 5.6002
|  |  |  | Best View [MW] |  |  | 5.0639 | 5.1058 | 5.149 | 5.189 | 5.2348 | 4.6838 | 4.7425 | 4.7969 | 4.8576 | 4.9172 | 4.9791 | 5.0393 | 5.1013 | 5.1646 | 5.2293 | 5.2948 | 5.62 | 5.9454
|  |  |  | Base Case [MW] |  |  | 5.0639 | 5.1216 | 5.1779 | 5.237 | 5.2989 | 4.7699 | 4.8254 | 4.8873 | 4.9441 | 5.0067 | 5.0714 | 5.1339 | 5.1975 | 5.2624 | 5.3277 | 5.3976 | 5.7349 | 6.073
|  |  |  | Aggressive [MW] |  |  | 5.0639 | 5.1367 | 5.2049 | 5.2816 | 5.3572 | 4.8437 | 4.9216 | 4.9985 | 5.0779 | 5.1588 | 5.2411 | 5.3236 | 5.4098 | 5.4946 | 5.5815 | 5.6694 | 6.1062 | 6.5433
| CARRIGALLEN | 20 | 1 | Conservative [MW] |  |  | 3.9115 | 3.9198 | 3.9278 | 3.9356 | 3.9453 | 3.9546 | 3.9703 | 3.987 | 4.0049 | 4.0238 | 4.0416 | 4.0604 | 4.0802 | 4.0987 | 4.1181 | 4.1384 | 4.2373 | 4.3364
|  |  |  | Best View [MW] |  |  | 3.9115 | 3.9245 | 3.9389 | 3.9547 | 3.9697 | 3.986 | 4.0088 | 4.0319 | 4.0572 | 4.0827 | 4.1082 | 4.1334 | 4.1607 | 4.19 | 4.2188 | 4.2469 | 4.3894 | 4.5317
|  |  |  | Base Case [MW] |  |  | 3.9115 | 3.9299 | 3.9491 | 3.9691 | 3.9899 | 4.0113 | 4.0378 | 4.068 | 4.0974 | 4.128 | 4.1597 | 4.1924 | 4.2258 | 4.2622 | 4.2964 | 4.333 | 4.5097 | 4.6868
|  |  |  | Aggressive [MW] |  |  | 3.9115 | 3.9405 | 3.9704 | 4.0014 | 4.0352 | 4.0697 | 4.108 | 4.1478 | 4.1887 | 4.2303 | 4.2745 | 4.3208 | 4.3688 | 4.4155 | 4.4651 | 4.517 | 4.7703 | 5.024
| CARRIGLAWN | 10 | 1 | Conservative [MW] |  |  | 6.9501 | 6.9721 | 6.9935 | 7.0142 | 7.034 | 7.0529 | 7.1026 | 7.1519 | 7.2061 | 7.2597 | 7.3127 | 7.3647 | 7.4206 | 7.4749 | 7.5325 | 7.593 | 7.8878 | 8.1831
|  |  |  | Best View [MW] |  |  | 6.9501 | 6.9882 | 7.024 | 7.0572 | 7.0973 | 7.1347 | 7.1877 | 7.2441 | 7.3038 | 7.3617 | 7.422 | 7.4849 | 7.5447 | 7.6113 | 7.6739 | 7.7376 | 8.053 | 8.3686
|  |  |  | Base Case [MW] |  |  | 6.9501 | 6.9949 | 7.0409 | 7.083 | 7.1305 | 7.1787 | 7.2395 | 7.3023 | 7.3667 | 7.4322 | 7.5035 | 7.5699 | 7.6413 | 7.7119 | 7.7811 | 7.8591 | 8.2257 | 8.5937
|  |  |  | Aggressive [MW] |  |  | 6.9501 | 7.0186 | 7.092 | 7.1604 | 7.2373 | 7.3127 | 7.4048 | 7.4947 | 7.5912 | 7.688 | 7.7888 | 7.8922 | 7.9908 | 8.0934 | 8.1973 | 8.3003 | 8.8176 | 9.3347
| CARRIGSHANE | 20 | 1 | Conservative [MW] |  |  | 9.4927 | 9.5776 | 9.6635 | 9.7516 | 9.816 | 9.7186 | 9.7857 | 9.8538 | 9.9227 | 9.9924 | 10.0648 | 10.1378 | 10.2134 | 10.2895 | 10.3663 | 10.4449 | 10.8331 | 11.2217
|  |  |  | Best View [MW] |  |  | 9.4927 | 9.5818 | 9.6734 | 9.7674 | 9.8379 | 9.7379 | 9.8279 | 9.9199 | 10.0155 | 10.1129 | 10.2119 | 10.3141 | 10.4196 | 10.5249 | 10.6349 | 10.7453 | 11.2962 | 11.8472
|  |  |  | Base Case [MW] |  |  | 9.4927 | 9.6138 | 9.7397 | 9.8718 | 9.9814 | 9.8672 | 9.9617 | 10.058 | 10.1577 | 10.259 | 10.3634 | 10.4703 | 10.5794 | 10.6911 | 10.8049 | 10.9207 | 11.4946 | 12.0688
|  |  |  | Aggressive [MW] |  |  | 9.4927 | 9.6616 | 9.8396 | 10.0273 | 10.1741 | 10.062 | 10.1644 | 10.2681 | 10.3768 | 10.4858 | 10.5968 | 10.7122 | 10.8295 | 10.9507 | 11.0733 | 11.2393 | 11.9535 | 12.675
| CARRIGTWOHILL | 10 | 1 | Conservative [MW] |  |  | 5.3152 | 5.355 | 5.3956 | 5.4371 | 5.4796 | 14.8149 | 14.8758 | 14.2733 | 14.3324 | 14.3763 | 14.4544 | 14.5172 | 14.5818 | 14.6483 | 14.6971 | 14.7575 | 15.0286 | 15.3016
|  |  |  | Best View [MW] |  |  | 5.3152 | 5.3572 | 5.4003 | 5.4444 | 5.4892 | 14.8299 | 14.9117 | 14.3306 | 14.402 | 14.495 | 14.5698 | 14.6704 | 14.7445 | 14.8272 | 14.9122 | 15.0085 | 15.46 | 15.9134
|  |  |  | Base Case [MW] |  |  | 5.3152 | 5.3726 | 5.4319 | 5.4928 | 5.5559 | 14.9487 | 15.0364 | 14.4489 | 14.5137 | 14.5993 | 14.6979 | 14.7735 | 14.8655 | 14.9586 | 15.0603 | 15.1571 | 15.6541 | 16.1502
|  |  |  | Aggressive [MW] |  |  | 5.3152 | 5.3948 | 5.478 | 5.5647 | 5.6555 | 15.1282 | 15.2203 | 14.6147 | 14.7019 | 14.7892 | 14.8889 | 14.9804 | 15.0772 | 15.1826 | 15.2865 | 15.3949 | 15.925 | 16.4559
| CARROWBEG | 10 | 1 | Conservative [MW] |  |  | 13.1747 | 13.1842 | 13.1979 | 13.2113 | 13.2246 | 13.2375 | 13.287 | 13.3421 | 13.3939 | 13.4469 | 13.5049 | 13.5638 | 13.6193 | 13.6795 | 13.7445 | 13.8055 | 14.1212 | 14.4362
|  |  |  | Best View [MW] |  |  | 13.1747 | 13.2027 | 13.234 | 13.2642 | 13.2934 | 13.3256 | 13.3889 | 13.4558 | 13.5265 | 13.596 | 13.6686 | 13.7445 | 13.8228 | 13.8993 | 13.9825 | 14.0674 | 14.4874 | 14.9076
|  |  |  | Base Case [MW] |  |  | 13.1747 | 13.2161 | 13.2594 | 13.3048 | 13.348 | 13.3931 | 13.4748 | 13.5575 | 13.6454 | 13.7338 | 13.8266 | 13.9235 | 14.0237 | 14.1271 | 14.2331 | 14.3411 | 14.8757 | 15.4106
|  |  |  | Aggressive [MW] |  |  | 13.1747 | 13.2589 | 13.3472 | 13.4431 | 13.5378 | 13.6391 | 13.7611 | 13.8854 | 14.0152 | 14.1492 | 14.2912 | 14.4393 | 14.5922 | 14.7532 | 14.9208 | 15.0928 | 15.941 | 16.79
|  | 20 | 1 | Conservative [MW] |  |  | 9.3899 | 9.4041 | 9.4207 | 9.434 | 9.4493 | 9.464 | 9.5211 | 9.5769 | 9.6336 | 9.6909 | 9.748 | 9.8018 | 9.8546 | 9.9091 | 9.9588 | 10.0084 | 10.2567 | 10.505
|  |  |  | Best View [MW] |  |  | 9.3899 | 9.426 | 9.4594 | 9.4921 | 9.5267 | 9.5607 | 9.6308 | 9.699 | 9.7669 | 9.834 | 9.8996 | 9.9626 | 10.0214 | 10.0775 | 10.1322 | 10.1779 | 10.4302 | 10.681
|  |  |  | Base Case [MW] |  |  | 9.3899 | 9.4389 | 9.4895 | 9.5386 | 9.5863 | 9.6345 | 9.7188 | 9.7983 | 9.8762 | 9.9555 | 10.0267 | 10.0933 | 10.1556 | 10.207 | 10.247 | 10.27 | 10.4304 | 10.5879
|  |  |  | Aggressive [MW] |  |  | 9.3899 | 9.4883 | 9.5865 | 9.6847 | 9.7807 | 9.8713 | 9.9734 | 10.0665 | 10.1478 | 10.2154 | 10.2603 | 10.2765 | 10.2515 | 10.1527 | 9.947 | 9.5364 | 8.0299 | 6.4893
| CASHEL | 10 | 1 | Conservative [MW] |  |  | 12.2036 | 12.2387 | 12.2731 | 12.3064 | 12.3422 | 12.3801 | 11.4333 | 11.4851 | 11.5384 | 11.5905 | 11.6438 | 11.6985 | 11.7568 | 11.8137 | 11.8717 | 11.9335 | 12.2322 | 12.5315
|  |  |  | Best View [MW] |  |  | 12.2036 | 12.2458 | 12.2869 | 12.3298 | 12.3746 | 12.4179 | 11.4965 | 11.572 | 11.6501 | 11.7282 | 11.8111 | 11.896 | 11.983 | 12.0717 | 12.1646 | 12.2591 | 12.7275 | 13.1962
|  |  |  | Base Case [MW] |  |  | 12.2036 | 12.2574 | 12.3156 | 12.3744 | 12.4342 | 12.4978 | 11.5823 | 11.6637 | 11.7496 | 11.8375 | 11.9268 | 12.0203 | 12.1179 | 12.2163 | 12.318 | 12.426 | 12.9494 | 13.4739
|  |  |  | Aggressive [MW] |  |  | 12.2036 | 12.2891 | 12.3818 | 12.4747 | 12.5743 | 12.6767 | 11.7751 | 11.8678 | 11.9643 | 12.0645 | 12.1678 | 12.2743 | 12.3835 | 12.4978 | 12.6142 | 12.7352 | 13.3278 | 13.9211
| CASTLEBLAYNEY | 10 | 1 | Conservative [MW] |  |  | 13.8925 | 13.9406 | 13.9865 | 14.0347 | 14.0805 | 14.1328 | 14.198 | 14.2671 | 14.3405 | 14.4131 | 14.4852 | 14.5611 | 14.6401 | 14.718 | 14.7992 | 14.8786 | 15.2804 | 15.6819
|  |  |  | Best View [MW] |  |  | 13.8925 | 13.9512 | 14.0108 | 14.0756 | 14.1367 | 14.2025 | 14.2964 | 14.3951 | 14.4928 | 14.5989 | 14.7035 | 14.8152 | 14.9241 | 15.0393 | 15.1553 | 15.2764 | 15.8685 | 16.4614
|  |  |  | Base Case [MW] |  |  | 13.8925 | 13.9677 | 14.0414 | 14.1184 | 14.1983 | 14.2805 | 14.3887 | 14.4991 | 14.6108 | 14.7281 | 14.8501 | 14.9714 | 15.1005 | 15.2275 | 15.3608 | 15.4998 | 16.1797 | 16.8606
|  |  |  | Aggressive [MW] |  |  | 13.8925 | 14.0093 | 14.1258 | 14.2497 | 14.3763 | 14.5084 | 14.6463 | 14.7879 | 14.9366 | 15.087 | 15.2467 | 15.4047 | 15.5739 | 15.742 | 15.9126 | 16.0932 | 16.9696 | 17.8476
| CASTLECOMER | 10 | 1 | Conservative [MW] |  |  | 2.2303 | 2.2519 | 2.2733 | 2.2958 | 2.3186 | 14.7753 | 14.8135 | 14.852 | 14.892 | 14.932 | 14.9735 | 15.0162 | 15.0604 | 15.1048 | 15.1504 | 15.1975 | 15.4291 | 15.6609
|  |  |  | Best View [MW] |  |  | 2.2303 | 2.2564 | 2.2832 | 2.3105 | 2.3393 | 14.8043 | 14.8565 | 14.909 | 14.9642 | 15.0209 | 15.0803 | 15.1412 | 15.2037 | 15.2676 | 15.3355 | 15.4035 | 15.7434 | 16.0832
|  |  |  | Base Case [MW] |  |  | 2.2303 | 2.2617 | 2.2933 | 2.3267 | 2.3604 | 14.8349 | 14.8967 | 14.9611 | 15.0286 | 15.0986 | 15.1717 | 15.2463 | 15.325 | 15.4065 | 15.4908 | 15.5778 | 16.0058 | 16.4343
|  |  |  | Aggressive [MW] |  |  | 2.2303 | 2.2829 | 2.3367 | 2.3938 | 2.4523 | 14.9658 | 15.0484 | 15.1351 | 15.225 | 15.319 | 15.4185 | 15.5223 | 15.6302 | 15.7436 | 15.8623 | 15.9864 | 16.5923 | 17.1992
| CASTLEISLAND | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 12.6883 | 12.7429 | 12.7976 | 12.8548 | 12.912 | 12.9706 | 13.0316 | 13.0927 | 13.1562 | 13.221 | 13.2871 | 13.6142 | 13.9415
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 12.8005 | 12.8734 | 12.9489 | 13.0259 | 13.1052 | 13.1859 | 13.2703 | 13.3571 | 13.4452 | 13.5368 | 13.631 | 14.0952 | 14.5597
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 12.8332 | 12.912 | 12.9934 | 13.0784 | 13.1647 | 13.2548 | 13.3461 | 13.4423 | 13.5397 | 13.6407 | 13.7452 | 14.2584 | 14.7721
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.0006173 | 13.006 | 13.1083 | 13.2156 | 13.3265 | 13.4424 | 13.5618 | 13.686 | 13.8139 | 13.9474 | 14.085 | 14.227 | 14.925 | 15.6239
| CASTLEKNOCK | 10 | 1 | Conservative [MW] |  |  | 5.6041 | 5.6351 | 5.664 | 5.6949 | 5.7277 | 5.7582 | 5.7766 | 5.7983 | 5.8192 | 5.8393 | 5.8584 | 5.8809 | 5.8982 | 5.923 | 5.9426 | 5.9655 | 6.071 | 6.1771
|  |  |  | Best View [MW] |  |  | 5.6041 | 5.6379 | 5.6693 | 5.7022 | 5.7404 | 5.7758 | 5.7965 | 5.82 | 5.8426 | 5.8683 | 5.8926 | 5.9158 | 5.9419 | 5.9667 | 5.9943 | 6.0206 | 6.1556 | 6.2905
|  |  |  | Base Case [MW] |  |  | 5.6041 | 5.6406 | 5.6779 | 5.7123 | 5.7555 | 5.7953 | 5.8181 | 5.8476 | 5.8716 | 5.8983 | 5.9276 | 5.9553 | 5.9855 | 6.0182 | 6.0448 | 6.0781 | 6.2269 | 6.3767
|  |  |  | Aggressive [MW] |  |  | 5.6041 | 5.6468 | 5.6929 | 5.7384 | 5.7911 | 5.8422 | 5.868 | 5.8883 | 5.9158 | 5.9422 | 5.9672 | 5.9908 | 6.0173 | 6.0465 | 6.0743 | 6.1006 | 6.2359 | 6.3709
| CASTLELYONS | 20 | 1 | Conservative [MW] |  |  | 6.1545 | 6.1817 | 6.2076 | 6.2322 | 6.2595 | 6.2855 | 6.315 | 6.3429 | 6.3692 | 6.3984 | 6.43 | 6.4601 | 6.4927 | 6.5233 | 6.5521 | 6.5878 | 6.7478 | 6.909
|  |  |  | Best View [MW] |  |  | 6.1545 | 6.1831 | 6.2104 | 6.2361 | 6.2643 | 6.2954 | 6.3305 | 6.3713 | 6.4093 | 6.4486 | 6.489 | 6.5305 | 6.5774 | 6.6205 | 6.6687 | 6.7128 | 6.9443 | 7.1751
|  |  |  | Base Case [MW] |  |  | 6.1545 | 6.1938 | 6.2305 | 6.2684 | 6.3076 | 6.348 | 6.3868 | 6.427 | 6.4683 | 6.5108 | 6.5541 | 6.5983 | 6.6429 | 6.6926 | 6.738 | 6.7882 | 7.0265 | 7.2657
|  |  |  | Aggressive [MW] |  |  | 6.1545 | 6.2045 | 6.2574 | 6.3133 | 6.3674 | 6.4279 | 6.4713 | 6.5154 | 6.5604 | 6.606 | 6.6518 | 6.698 | 6.7487 | 6.7992 | 6.854 | 6.9036 | 7.1656 | 7.4266
| CASTLEREA | 10 | 1 | Conservative [MW] |  |  | 3.7189 | 3.7342 | 3.7496 | 3.7649 | 3.7803 | 3.7967 | 3.834 | 3.8724 | 3.9107 | 3.9513 | 3.9918 | 4.0333 | 4.0759 | 4.1182 | 4.1629 | 4.2085 | 4.4339 | 4.6596
|  |  |  | Best View [MW] |  |  | 3.7189 | 3.7494 | 3.78 | 3.8107 | 3.8423 | 3.8751 | 3.9214 | 3.9688 | 4.0172 | 4.0666 | 4.1169 | 4.1694 | 4.2228 | 4.2768 | 4.3316 | 4.3885 | 4.6671 | 4.9462
|  |  |  | Base Case [MW] |  |  | 3.7189 | 3.7539 | 3.7911 | 3.8272 | 3.8656 | 3.9039 | 3.9621 | 4.0226 | 4.0838 | 4.1471 | 4.2123 | 4.2807 | 4.3495 | 4.4198 | 4.493 | 4.5675 | 4.9367 | 5.306
|  |  |  | Aggressive [MW] |  |  | 3.7189 | 3.776 | 3.8353 | 3.8957 | 3.9594 | 4.0252 | 4.1011 | 4.1798 | 4.2614 | 4.3457 | 4.4323 | 4.5225 | 4.6161 | 4.7111 | 4.8085 | 4.9098 | 5.4059 | 5.9027
| CASTLETOWNBERE | 10 | 1 | Conservative [MW] |  |  | 3.1595 | 3.1664 | 3.1741 | 3.1809 | 3.1886 | 3.1962 | 3.2037 | 3.2122 | 3.2196 | 3.228 | 3.2362 | 3.2454 | 3.2544 | 3.2634 | 3.2724 | 3.2822 | 3.3288 | 3.3756
|  |  |  | Best View [MW] |  |  | 3.1595 | 3.1672 | 3.1749 | 3.1825 | 3.1901 | 3.1984 | 3.2091 | 3.2197 | 3.2311 | 3.2424 | 3.2544 | 3.2664 | 3.2792 | 3.2918 | 3.3052 | 3.3194 | 3.3884 | 3.4575
|  |  |  | Base Case [MW] |  |  | 3.1595 | 3.1695 | 3.1802 | 3.1908 | 3.2022 | 3.2136 | 3.225 | 3.2363 | 3.2475 | 3.2595 | 3.2724 | 3.2851 | 3.2985 | 3.3118 | 3.3259 | 3.3409 | 3.4133 | 3.4859
|  |  |  | Aggressive [MW] |  |  | 3.1595 | 3.1733 | 3.1886 | 3.2038 | 3.2197 | 3.2372 | 3.2483 | 3.2612 | 3.274 | 3.2865 | 3.2999 | 3.3141 | 3.3281 | 3.3428 | 3.3583 | 3.3747 | 3.4543 | 3.5341
|  | 20 | 1 | Conservative [MW] |  |  | 3.9913 | 4.0104 | 4.0283 | 4.0472 | 4.067 | 4.0878 | 4.1082 | 4.127 | 4.1491 | 4.1696 | 4.1909 | 4.2129 | 4.2332 | 4.2564 | 4.2802 | 4.3022 | 4.4169 | 4.5314
|  |  |  | Best View [MW] |  |  | 3.9913 | 4.0102 | 4.0299 | 4.0505 | 4.0719 | 4.094 | 4.119 | 4.1483 | 4.1748 | 4.2056 | 4.2332 | 4.2648 | 4.2954 | 4.3274 | 4.358 | 4.3921 | 4.5534 | 4.7153
|  |  |  | Base Case [MW] |  |  | 3.9913 | 4.0176 | 4.0458 | 4.0735 | 4.1029 | 4.134 | 4.1618 | 4.1891 | 4.2182 | 4.2488 | 4.2786 | 4.3097 | 4.342 | 4.3754 | 4.4071 | 4.4394 | 4.5994 | 4.7595
|  |  |  | Aggressive [MW] |  |  | 3.9913 | 4.0292 | 4.0665 | 4.1076 | 4.1476 | 4.1906 | 4.2204 | 4.2516 | 4.2817 | 4.3131 | 4.3456 | 4.3788 | 4.4128 | 4.4472 | 4.4818 | 4.5164 | 4.6895 | 4.8626
| CASTLETOWNROCHE | 10 | 1 | Conservative [MW] |  |  | 3.4825 | 3.493 | 3.5029 | 3.5144 | 3.5254 | 3.5359 | 3.5481 | 3.5598 | 3.5709 | 3.5835 | 3.5956 | 3.6091 | 3.6219 | 3.634 | 3.6476 | 3.6626 | 3.7337 | 3.8051
|  |  |  | Best View [MW] |  |  | 3.4825 | 3.494 | 3.5048 | 3.5173 | 3.5291 | 3.5403 | 3.5555 | 3.5717 | 3.5869 | 3.6051 | 3.6222 | 3.6402 | 3.6569 | 3.6765 | 3.6948 | 3.7159 | 3.814 | 3.9126
|  |  |  | Base Case [MW] |  |  | 3.4825 | 3.4971 | 3.5128 | 3.5295 | 3.5451 | 3.5615 | 3.5791 | 3.5956 | 3.613 | 3.6292 | 3.6483 | 3.6662 | 3.6849 | 3.7063 | 3.7263 | 3.7469 | 3.8482 | 3.9497
|  |  |  | Aggressive [MW] |  |  | 3.4825 | 3.5033 | 3.5241 | 3.547 | 3.5719 | 3.5964 | 3.6129 | 3.6303 | 3.6506 | 3.6695 | 3.689 | 3.7092 | 3.73 | 3.7512 | 3.7729 | 3.7971 | 3.9115 | 4.0262
| CASTLETROY | 10 | 1 | Conservative [MW] |  |  | 7.0012 | 7.0448 | 7.0803 | 7.1223 | 7.166 | 7.2059 | 7.2505 | 7.3007 | 7.3455 | 7.3955 | 7.44 | 7.4893 | 7.5379 | 7.5858 | 7.6379 | 7.683 | 7.927 | 8.1698
|  |  |  | Best View [MW] |  |  | 7.0012 | 7.0416 | 7.0836 | 7.127 | 7.1668 | 7.2128 | 7.2729 | 7.3393 | 7.4014 | 7.4637 | 7.5314 | 7.5984 | 7.6642 | 7.7281 | 7.7947 | 7.8581 | 8.1837 | 8.5087
|  |  |  | Base Case [MW] |  |  | 7.0012 | 7.0607 | 7.1137 | 7.1748 | 7.2338 | 7.2903 | 7.3639 | 7.4405 | 7.5138 | 7.5886 | 7.6638 | 7.7385 | 7.8115 | 7.8877 | 7.9603 | 8.0335 | 8.3979 | 8.7624
|  |  |  | Aggressive [MW] |  |  | 7.0012 | 7.0947 | 7.1858 | 7.2781 | 7.3755 | 7.4765 | 7.5558 | 7.6385 | 7.7177 | 7.8038 | 7.8837 | 7.9617 | 8.0361 | 8.1109 | 8.1842 | 8.2467 | 8.588 | 8.9275
| CAUSEWAY | 10 | 1 | Conservative [MW] |  |  | 1.3346 | 1.3505 | 1.366 | 1.3821 | 1.3983 | 1.4141 | 1.445 | 1.4762 | 1.5083 | 1.5413 | 1.5746 | 1.6088 | 1.6433 | 1.6787 | 1.715 | 1.7515 | 1.9334 | 2.1153
|  |  |  | Best View [MW] |  |  | 1.3346 | 1.3622 | 1.3905 | 1.4191 | 1.4485 | 1.4783 | 1.5191 | 1.5616 | 1.6052 | 1.6499 | 1.6956 | 1.7424 | 1.7902 | 1.8398 | 1.8902 | 1.9418 | 2.1967 | 2.4518
|  |  |  | Base Case [MW] |  |  | 1.3346 | 1.3658 | 1.3973 | 1.4297 | 1.4625 | 1.4962 | 1.5414 | 1.587 | 1.6345 | 1.6836 | 1.7333 | 1.7848 | 1.8374 | 1.8916 | 1.9469 | 2.0039 | 2.2842 | 2.5648
|  |  |  | Aggressive [MW] |  |  | 1.3346 | 1.3833 | 1.433 | 1.4851 | 1.5387 | 1.5943 | 1.6523 | 1.7122 | 1.7736 | 1.8375 | 1.904 | 1.9716 | 2.0418 | 2.1136 | 2.1878 | 2.2634 | 2.6375 | 3.0119
| CAVAN | 10 | 1 | Conservative [MW] |  |  | 8.5496 | 8.5835 | 8.6176 | 8.6546 | 8.6887 | 8.7254 | 8.7765 | 8.8271 | 8.8774 | 8.9296 | 8.9813 | 9.0342 | 9.0885 | 9.1438 | 9.1971 | 9.2511 | 9.5192 | 9.7875
|  |  |  | Best View [MW] |  |  | 8.5496 | 8.5928 | 8.6368 | 8.6845 | 8.7302 | 8.7768 | 8.8466 | 8.9165 | 8.9885 | 9.0591 | 9.1329 | 9.2068 | 9.2801 | 9.3549 | 9.4299 | 9.5046 | 9.879 | 10.2534
|  |  |  | Base Case [MW] |  |  | 8.5496 | 8.6034 | 8.6607 | 8.7172 | 8.7765 | 8.8339 | 8.9112 | 8.9908 | 9.0693 | 9.1486 | 9.2304 | 9.311 | 9.395 | 9.4754 | 9.5569 | 9.635 | 10.0346 | 10.4336
|  |  |  | Aggressive [MW] |  |  | 8.5496 | 8.634 | 8.7207 | 8.812 | 8.9057 | 8.9982 | 9.0938 | 9.1911 | 9.2881 | 9.3888 | 9.4858 | 9.5821 | 9.6756 | 9.7697 | 9.8549 | 9.9371 | 10.3561 | 10.7745
|  | 20 | 1 | Conservative [MW] |  |  | 8.3461 | 8.381 | 8.4158 | 8.4512 | 8.4857 | 6.9529 | 7.0045 | 7.056 | 7.1087 | 7.1624 | 7.2159 | 7.27 | 7.3246 | 7.3798 | 7.435 | 7.4903 | 7.7667 | 8.043
|  |  |  | Best View [MW] |  |  | 8.3461 | 8.3901 | 8.4348 | 8.4806 | 8.5261 | 7.0052 | 7.076 | 7.1482 | 7.2217 | 7.2955 | 7.3695 | 7.4447 | 7.5205 | 7.5948 | 7.6703 | 7.7445 | 8.1188 | 8.493
|  |  |  | Base Case [MW] |  |  | 8.3461 | 8.4005 | 8.4557 | 8.514 | 8.5718 | 7.0651 | 7.1437 | 7.2236 | 7.3054 | 7.3859 | 7.4688 | 7.5517 | 7.6328 | 7.7155 | 7.7957 | 7.8754 | 8.275 | 8.6746
|  |  |  | Aggressive [MW] |  |  | 8.3461 | 8.4306 | 8.5186 | 8.607 | 8.6982 | 7.2333 | 7.3308 | 7.4286 | 7.5285 | 7.6263 | 7.7251 | 7.8213 | 7.9146 | 8.0034 | 8.0853 | 8.1592 | 8.5498 | 8.9391
| CELBRIDGE | 10 | 1 | Conservative [MW] |  |  | 12.5426 | 12.6422 | 12.7453 | 12.8512 | 12.96 | 13.0734 | 13.1342 | 13.1996 | 13.2704 | 13.3367 | 13.4033 | 13.4747 | 13.5457 | 13.6167 | 13.6876 | 13.7625 | 14.1262 | 14.4906
|  |  |  | Best View [MW] |  |  | 12.5426 | 12.6532 | 12.7694 | 12.8865 | 13.0084 | 13.1319 | 13.2046 | 13.2812 | 13.3612 | 13.4401 | 13.5173 | 13.5977 | 13.6808 | 13.7668 | 13.8504 | 13.936 | 14.3587 | 14.7817
|  |  |  | Base Case [MW] |  |  | 12.5426 | 12.663 | 12.7906 | 12.9209 | 13.053 | 13.1927 | 13.2768 | 13.3635 | 13.4517 | 13.5461 | 13.6371 | 13.7295 | 13.8224 | 13.9202 | 14.0183 | 14.116 | 14.6056 | 15.0951
|  |  |  | Aggressive [MW] |  |  | 12.5426 | 12.6907 | 12.8478 | 13.0123 | 13.1785 | 13.3509 | 13.4305 | 13.5133 | 13.59 | 13.6743 | 13.7566 | 13.8412 | 13.9283 | 14.0124 | 14.1032 | 14.1906 | 14.6368 | 15.0824
| CHARLESTOWN | 10 | 1 | Conservative [MW] |  |  | 1.7588 | 1.7645 | 1.7702 | 1.7758 | 1.7815 | 1.7871 | 1.8062 | 1.8258 | 1.8459 | 1.8665 | 1.8872 | 1.9085 | 1.9307 | 1.953 | 1.9758 | 1.9991 | 2.1145 | 2.2299
|  |  |  | Best View [MW] |  |  | 1.7588 | 1.7716 | 1.7843 | 1.7976 | 1.8108 | 1.8238 | 1.8488 | 1.8748 | 1.9014 | 1.9286 | 1.9564 | 1.9852 | 2.0145 | 2.0448 | 2.0756 | 2.1072 | 2.2633 | 2.4194
|  |  |  | Base Case [MW] |  |  | 1.7588 | 1.7758 | 1.7933 | 1.8109 | 1.829 | 1.8472 | 1.8775 | 1.9089 | 1.941 | 1.9746 | 2.0091 | 2.0442 | 2.0808 | 2.1187 | 2.157 | 2.1966 | 2.3913 | 2.5861
|  |  |  | Aggressive [MW] |  |  | 1.7588 | 1.7914 | 1.8255 | 1.8608 | 1.8974 | 1.9349 | 1.9791 | 2.025 | 2.0723 | 2.1219 | 2.1734 | 2.2264 | 2.2809 | 2.3377 | 2.3955 | 2.4551 | 2.7484 | 3.042
| CHARLEVILLE | 20 | 1 | Conservative [MW] |  |  | 1.3771 | 1.4172 | 1.4581 | 1.4999 | 1.5427 | 1.5859 | 1.6334 | 1.6818 | 1.7314 | 1.7821 | 1.8338 | 1.8864 | 1.9402 | 1.9953 | 2.0516 | 2.1089 | 2.3929 | 2.677
|  |  |  | Best View [MW] |  |  | 1.3771 | 1.4188 | 1.4616 | 1.5051 | 1.5495 | 1.595 | 1.6588 | 1.7243 | 1.7918 | 1.8609 | 1.9324 | 2.0058 | 2.081 | 2.1583 | 2.2383 | 2.3198 | 2.7232 | 3.1269
|  |  |  | Base Case [MW] |  |  | 1.3771 | 1.4322 | 1.4887 | 1.5472 | 1.6068 | 1.6684 | 1.7437 | 1.8212 | 1.9012 | 1.9841 | 2.0695 | 2.1577 | 2.2484 | 2.3421 | 2.4388 | 2.5382 | 3.028 | 3.5182
|  |  |  | Aggressive [MW] |  |  | 1.3771 | 1.4614 | 1.5493 | 1.6409 | 1.7365 | 1.836 | 1.9236 | 2.0139 | 2.1076 | 2.2045 | 2.3048 | 2.4082 | 2.5153 | 2.6259 | 2.7397 | 2.8578 | 3.4368 | 4.0166
| CHURCHTOWN | 10 | 1 | Conservative [MW] |  |  | 7.3572 | 7.3733 | 7.3888 | 7.4057 | 7.4219 | 7.4394 | 7.4564 | 7.4764 | 7.4957 | 7.5142 | 7.5337 | 7.5544 | 7.5762 | 7.597 | 7.6188 | 7.6418 | 7.7536 | 7.8656
|  |  |  | Best View [MW] |  |  | 7.3572 | 7.3742 | 7.3907 | 7.4064 | 7.4253 | 7.4416 | 7.4658 | 7.4926 | 7.5177 | 7.5455 | 7.5715 | 7.6 | 7.6308 | 7.6597 | 7.6909 | 7.724 | 7.8846 | 8.0454
|  |  |  | Base Case [MW] |  |  | 7.3572 | 7.3796 | 7.4009 | 7.423 | 7.4458 | 7.4714 | 7.4997 | 7.53 | 7.5605 | 7.5927 | 7.6267 | 7.6603 | 7.6957 | 7.7326 | 7.7687 | 7.8082 | 7.9967 | 8.1857
|  |  |  | Aggressive [MW] |  |  | 7.3572 | 7.3908 | 7.4235 | 7.4595 | 7.4965 | 7.5361 | 7.5695 | 7.6044 | 7.6405 | 7.678 | 7.7166 | 7.7582 | 7.7986 | 7.8417 | 7.8876 | 7.9335 | 8.163 | 8.3924
|  | 20 | 1 | Conservative [MW] |  |  | 6.7855 | 6.7919 | 6.798 | 6.8039 | 6.8115 | 6.8189 | 6.8253 | 6.8335 | 6.8412 | 6.8489 | 6.858 | 6.865 | 6.8736 | 6.8819 | 6.8917 | 6.9012 | 6.9495 | 6.9977
|  |  |  | Best View [MW] |  |  | 6.7855 | 6.7915 | 6.7992 | 6.8047 | 6.8119 | 6.8188 | 6.8292 | 6.8392 | 6.8505 | 6.8613 | 6.8736 | 6.8851 | 6.8963 | 6.9087 | 6.9224 | 6.9355 | 7.0027 | 7.0698
|  |  |  | Base Case [MW] |  |  | 6.7855 | 6.7942 | 6.8027 | 6.8124 | 6.8219 | 6.8308 | 6.8424 | 6.8552 | 6.8673 | 6.8806 | 6.8952 | 6.9089 | 6.9239 | 6.9379 | 6.953 | 6.9692 | 7.0472 | 7.1254
|  |  |  | Aggressive [MW] |  |  | 6.7855 | 6.7992 | 6.8119 | 6.8275 | 6.8421 | 6.8575 | 6.8717 | 6.8851 | 6.9015 | 6.917 | 6.9315 | 6.9489 | 6.9671 | 6.9843 | 7.0023 | 7.023 | 7.1193 | 7.2161
| CLADY | 10 | 1 | Conservative [MW] |  |  | 0.3615 | 0.36145 | 0.36141 | 0.36136 | 0.36131 | 0.36127 | 0.36117 | 0.36108 | 0.36103 | 0.36098 | 0.36094 | 0.36084 | 0.3608 | 0.36075 | 0.36066 | 0.36061 | 0.36025 | 0.3599
|  |  |  | Best View [MW] |  |  | 0.3615 | 0.36141 | 0.36131 | 0.36122 | 0.36113 | 0.36108 | 0.36098 | 0.36089 | 0.3608 | 0.36075 | 0.36061 | 0.36051 | 0.36042 | 0.36033 | 0.36023 | 0.36009 | 0.35951 | 0.35893
|  |  |  | Base Case [MW] |  |  | 0.3615 | 0.36141 | 0.36127 | 0.36117 | 0.36108 | 0.36103 | 0.36094 | 0.36084 | 0.36075 | 0.36061 | 0.36051 | 0.36037 | 0.36023 | 0.36009 | 0.35995 | 0.35981 | 0.35911 | 0.3584
|  |  |  | Aggressive [MW] |  |  | 0.3615 | 0.36131 | 0.36117 | 0.36108 | 0.36098 | 0.36084 | 0.36075 | 0.36061 | 0.36047 | 0.36033 | 0.36019 | 0.36 | 0.35986 | 0.35967 | 0.35948 | 0.35925 | 0.3582 | 0.35714
| CLARA | 20 | 1 | Conservative [MW] |  |  | 9.5554 | 9.606 | 9.6578 | 9.7092 | 9.7636 | 9.8174 | 9.8858 | 9.957 | 10.0307 | 10.1053 | 10.1802 | 10.2578 | 10.3357 | 10.4182 | 10.4987 | 10.5837 | 10.9966 | 11.4103
|  |  |  | Best View [MW] |  |  | 9.5554 | 9.6202 | 9.684 | 9.7507 | 9.8201 | 9.8886 | 9.9817 | 10.0767 | 10.1752 | 10.2754 | 10.3768 | 10.4836 | 10.5913 | 10.7017 | 10.8149 | 10.9302 | 11.5008 | 12.0719
|  |  |  | Base Case [MW] |  |  | 9.5554 | 9.631 | 9.7091 | 9.7896 | 9.8724 | 9.9555 | 10.0659 | 10.1792 | 10.2951 | 10.4154 | 10.5379 | 10.6641 | 10.7964 | 10.9292 | 11.0673 | 11.2074 | 11.9024 | 12.5978
|  |  |  | Aggressive [MW] |  |  | 9.5554 | 9.6536 | 9.7551 | 9.8601 | 9.9683 | 10.0795 | 10.2153 | 10.3543 | 10.5002 | 10.6501 | 10.8059 | 10.967 | 11.1324 | 11.3038 | 11.4776 | 11.6579 | 12.542 | 13.4272
| CLAREGALWAY | 10 | 1 | Conservative [MW] |  |  | 4.2141 | 4.2299 | 4.247 | 4.2656 | 4.283 | 4.2994 | 4.3243 | 4.347 | 4.3723 | 4.3978 | 4.4208 | 4.4462 | 4.4741 | 4.4992 | 4.5238 | 4.5507 | 4.6791 | 4.8079
|  |  |  | Best View [MW] |  |  | 4.2141 | 4.2341 | 4.2573 | 4.2789 | 4.301 | 4.3215 | 4.3566 | 4.3897 | 4.4255 | 4.4612 | 4.4967 | 4.5341 | 4.5706 | 4.6085 | 4.6476 | 4.6845 | 4.875 | 5.0651
|  |  |  | Base Case [MW] |  |  | 4.2141 | 4.2414 | 4.2686 | 4.2954 | 4.3241 | 4.3522 | 4.3901 | 4.4273 | 4.4659 | 4.5057 | 4.5463 | 4.5874 | 4.6284 | 4.669 | 4.7113 | 4.7518 | 4.9593 | 5.1664
|  |  |  | Aggressive [MW] |  |  | 4.2141 | 4.2566 | 4.2997 | 4.3429 | 4.3885 | 4.433 | 4.48 | 4.5235 | 4.5706 | 4.6181 | 4.6653 | 4.7116 | 4.7584 | 4.8048 | 4.8502 | 4.893 | 5.114 | 5.3346
|  | 20 | 1 | Conservative [MW] |  |  | 4.699 | 4.7182 | 4.7385 | 4.7593 | 4.7782 | 4.7977 | 4.8247 | 4.853 | 4.8798 | 4.905 | 4.9309 | 4.9577 | 4.9822 | 5.01 | 5.032 | 5.0568 | 5.1735 | 5.2905
|  |  |  | Best View [MW] |  |  | 4.699 | 4.7232 | 4.7499 | 4.7736 | 4.7994 | 4.8244 | 4.8603 | 4.8987 | 4.9364 | 4.9729 | 5.0077 | 5.0431 | 5.075 | 5.1061 | 5.1345 | 5.1593 | 5.293 | 5.4261
|  |  |  | Base Case [MW] |  |  | 4.699 | 4.7318 | 4.7625 | 4.7936 | 4.8245 | 4.8581 | 4.8982 | 4.9387 | 4.979 | 5.0155 | 5.0529 | 5.0875 | 5.1211 | 5.1481 | 5.171 | 5.1916 | 5.3007 | 5.4094
|  |  |  | Aggressive [MW] |  |  | 4.699 | 4.7474 | 4.7973 | 4.8475 | 4.8974 | 4.9451 | 4.9888 | 5.0332 | 5.0737 | 5.112 | 5.1447 | 5.1741 | 5.1937 | 5.2041 | 5.2011 | 5.182 | 5.1296 | 5.0744
| CLARKSTOWN | 10 | 1 | Conservative [MW] |  |  | 3.333 | 3.3327 | 3.3341 | 3.3337 | 3.3352 | 3.3346 | 3.3344 | 3.336 | 3.3356 | 3.3353 | 3.3351 | 3.3366 | 3.3363 | 3.336 | 3.3376 | 3.3372 | 3.3404 | 3.3433
|  |  |  | Best View [MW] |  |  | 3.333 | 3.3327 | 3.334 | 3.3336 | 3.3349 | 3.3344 | 3.336 | 3.3355 | 3.3353 | 3.3368 | 3.3364 | 3.3361 | 3.3376 | 3.3372 | 3.3368 | 3.3382 | 3.3406 | 3.3433
|  |  |  | Base Case [MW] |  |  | 3.333 | 3.3327 | 3.3339 | 3.3335 | 3.3347 | 3.336 | 3.3356 | 3.3352 | 3.3368 | 3.3363 | 3.3359 | 3.3373 | 3.3369 | 3.3384 | 3.3379 | 3.3374 | 3.3351 | 3.3328
|  |  |  | Aggressive [MW] |  |  | 3.333 | 3.3344 | 3.3337 | 3.3348 | 3.3342 | 3.3353 | 3.3369 | 3.3365 | 3.3361 | 3.3376 | 3.3372 | 3.3368 | 3.3383 | 3.3379 | 3.3375 | 3.3389 | 3.3411 | 3.3436
| CLIFDEN | 10 | 1 | Conservative [MW] |  |  | 6.8258 | 6.8552 | 6.8831 | 6.9095 | 6.9389 | 6.9667 | 7.0111 | 7.0523 | 7.0903 | 7.1344 | 7.1748 | 7.2211 | 7.2637 | 7.312 | 7.3561 | 7.4008 | 7.6226 | 7.8445
|  |  |  | Best View [MW] |  |  | 6.8258 | 6.8599 | 6.8962 | 6.9299 | 6.9704 | 7.0084 | 7.0644 | 7.1233 | 7.1848 | 7.2439 | 7.3097 | 7.3724 | 7.4364 | 7.5011 | 7.5713 | 7.6361 | 7.9746 | 8.3123
|  |  |  | Base Case [MW] |  |  | 6.8258 | 6.8677 | 6.9149 | 6.9627 | 7.011 | 7.0596 | 7.1228 | 7.1872 | 7.2525 | 7.3231 | 7.3937 | 7.464 | 7.5379 | 7.6101 | 7.685 | 7.7618 | 8.1407 | 8.52
|  |  |  | Aggressive [MW] |  |  | 6.8258 | 6.8939 | 6.9662 | 7.0423 | 7.1168 | 7.1986 | 7.2752 | 7.3545 | 7.435 | 7.5163 | 7.6027 | 7.6879 | 7.7757 | 7.8602 | 7.9508 | 8.0405 | 8.4912 | 8.9417
| CLONAKILTY | 10 | 1 | Conservative [MW] |  |  | 6.4373 | 6.484 | 6.5355 | 6.5814 | 6.6321 | 19.4064 | 19.476 | 19.5461 | 19.6212 | 19.6964 | 19.7716 | 19.8471 | 19.9269 | 20.0108 | 20.0942 | 20.1771 | 20.5931 | 21.0089
|  |  |  | Best View [MW] |  |  | 6.4373 | 6.4892 | 6.5401 | 6.59 | 6.6438 | 19.4227 | 19.5189 | 19.6168 | 19.7164 | 19.8214 | 19.9273 | 20.0377 | 20.1488 | 20.2635 | 20.3826 | 20.5049 | 21.1078 | 21.7112
|  |  |  | Base Case [MW] |  |  | 6.4373 | 6.5055 | 6.5779 | 6.6486 | 6.7223 | 19.5642 | 19.6668 | 19.7665 | 19.8715 | 19.9816 | 20.092 | 20.2064 | 20.3249 | 20.4431 | 20.5686 | 20.6927 | 21.3171 | 21.9412
|  |  |  | Aggressive [MW] |  |  | 6.4373 | 6.5337 | 6.6289 | 6.7319 | 6.8301 | 19.7704 | 19.8795 | 19.9894 | 20.1034 | 20.221 | 20.3383 | 20.4631 | 20.5909 | 20.7207 | 20.8526 | 20.9907 | 21.6645 | 22.3393
| CLONARD | 10 | 1 | Conservative [MW] |  |  | 6.6707 | 6.6869 | 6.707 | 6.7264 | 6.7453 | 6.7635 | 6.8054 | 6.8525 | 6.8957 | 6.9441 | 6.9928 | 7.0416 | 7.0949 | 7.1433 | 7.1959 | 7.2526 | 7.5254 | 7.7988
|  |  |  | Best View [MW] |  |  | 6.6707 | 6.7042 | 6.7358 | 6.7653 | 6.8019 | 6.8363 | 6.8848 | 6.9332 | 6.9855 | 7.042 | 7.0977 | 7.1521 | 7.2098 | 7.2656 | 7.329 | 7.39 | 7.7014 | 8.0125
|  |  |  | Base Case [MW] |  |  | 6.6707 | 6.7096 | 6.7501 | 6.7876 | 6.8308 | 6.8753 | 6.9302 | 6.9883 | 7.0447 | 7.1035 | 7.1695 | 7.2325 | 7.2971 | 7.3629 | 7.4295 | 7.4963 | 7.8297 | 8.1631
|  |  |  | Aggressive [MW] |  |  | 6.6707 | 6.7292 | 6.7939 | 6.8601 | 6.9271 | 6.9943 | 7.0807 | 7.1633 | 7.2505 | 7.3411 | 7.4347 | 7.5296 | 7.6247 | 7.7234 | 7.8242 | 7.9262 | 8.4333 | 8.9405
| CLONDALKIN | 10 | 1 | Conservative [MW] |  |  | 29.0389 | 29.2743 | 29.5213 | 29.765 | 30.0226 | 29.1196 | 29.2712 | 29.424 | 29.5725 | 29.7289 | 29.8799 | 30.0376 | 30.1953 | 30.3522 | 30.5086 | 30.6637 | 31.4427 | 32.2216
|  |  |  | Best View [MW] |  |  | 29.0389 | 29.3001 | 29.5735 | 29.8422 | 30.125 | 29.2539 | 29.4274 | 29.6056 | 29.7819 | 29.9543 | 30.1363 | 30.314 | 30.4929 | 30.6799 | 30.8605 | 31.0397 | 31.9396 | 32.8393
|  |  |  | Base Case [MW] |  |  | 29.0389 | 29.3286 | 29.6227 | 29.925 | 30.2392 | 29.3972 | 29.598 | 29.792 | 29.9916 | 30.1958 | 30.3977 | 30.5954 | 30.8024 | 31.0109 | 31.2115 | 31.4181 | 32.4349 | 33.4527
|  |  |  | Aggressive [MW] |  |  | 29.0389 | 29.3942 | 29.7589 | 30.134 | 30.5203 | 29.7679 | 29.943 | 30.1208 | 30.3013 | 30.4835 | 30.6598 | 30.8438 | 31.0267 | 31.2086 | 31.3867 | 31.5664 | 32.4608 | 33.3554
| CLONES | 10 | 1 | Conservative [MW] |  |  | 7.35 | 7.3859 | 7.4195 | 7.4555 | 7.4888 | 7.5248 | 6.8909 | 6.9397 | 6.9924 | 7.0447 | 7.0967 | 7.1479 | 7.2022 | 7.2555 | 7.3115 | 7.3659 | 7.6421 | 7.9181
|  |  |  | Best View [MW] |  |  | 7.35 | 7.3949 | 7.4406 | 7.4824 | 7.5298 | 7.5777 | 6.9613 | 7.0315 | 7.1016 | 7.1749 | 7.2468 | 7.3213 | 7.3975 | 7.4706 | 7.5486 | 7.6217 | 8.0003 | 8.378
|  |  |  | Base Case [MW] |  |  | 7.35 | 7.4054 | 7.4595 | 7.517 | 7.5727 | 7.6313 | 7.0242 | 7.1039 | 7.1851 | 7.2628 | 7.3451 | 7.4265 | 7.5108 | 7.5924 | 7.6744 | 7.7552 | 8.1624 | 8.5695
|  |  |  | Aggressive [MW] |  |  | 7.35 | 7.4332 | 7.5209 | 7.6125 | 7.7021 | 7.7933 | 7.2098 | 7.3076 | 7.4034 | 7.5045 | 7.6004 | 7.7021 | 7.7934 | 7.8858 | 7.9715 | 8.0474 | 8.4529 | 8.8568
| CLONMINCH | 10 | 1 | Conservative [MW] |  |  | 8.8401 | 8.8774 | 8.9187 | 8.9593 | 8.999 | 9.0401 | 9.0922 | 9.1459 | 9.1983 | 9.2541 | 9.3081 | 9.3625 | 9.4172 | 9.4717 | 9.5256 | 9.5787 | 9.8464 | 10.1139
|  |  |  | Best View [MW] |  |  | 8.8401 | 8.8893 | 8.9384 | 8.992 | 9.0425 | 9.0946 | 9.1641 | 9.233 | 9.303 | 9.3739 | 9.4449 | 9.5152 | 9.5842 | 9.6536 | 9.7226 | 9.7903 | 10.132 | 10.4735
|  |  |  | Base Case [MW] |  |  | 8.8401 | 8.8995 | 8.9591 | 9.0208 | 9.0819 | 9.1447 | 9.2241 | 9.306 | 9.387 | 9.4688 | 9.5504 | 9.6329 | 9.7125 | 9.7905 | 9.8652 | 9.9404 | 10.315 | 10.6898
|  |  |  | Aggressive [MW] |  |  | 8.8401 | 8.9165 | 8.993 | 9.0738 | 9.1534 | 9.2358 | 9.3321 | 9.4281 | 9.5273 | 9.6219 | 9.7185 | 9.8115 | 9.9006 | 9.9857 | 10.0586 | 10.1239 | 10.4705 | 10.8159
|  | 20 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| CLONROCHE | 20 | 1 | Conservative [MW] |  |  | 5.8284 | 5.8431 | 5.8574 | 5.8753 | 5.8886 | 5.9056 | 5.9438 | 5.9834 | 6.0244 | 6.0666 | 6.11 | 6.1544 | 6.1953 | 6.2413 | 6.2879 | 6.3394 | 6.5839 | 6.8292
|  |  |  | Best View [MW] |  |  | 5.8284 | 5.8528 | 5.884 | 5.9097 | 5.9379 | 5.9687 | 6.012 | 6.0559 | 6.1046 | 6.1496 | 6.1991 | 6.2488 | 6.2983 | 6.3518 | 6.4049 | 6.4616 | 6.7356 | 7.0101
|  |  |  | Base Case [MW] |  |  | 5.8284 | 5.861 | 5.8955 | 5.932 | 5.9662 | 6.0023 | 6.0545 | 6.1023 | 6.1541 | 6.2096 | 6.2644 | 6.318 | 6.3746 | 6.434 | 6.4959 | 6.5599 | 6.8743 | 7.1891
|  |  |  | Aggressive [MW] |  |  | 5.8284 | 5.8808 | 5.936 | 5.9899 | 6.0504 | 6.1128 | 6.1829 | 6.2607 | 6.3369 | 6.415 | 6.4988 | 6.5879 | 6.6764 | 6.7681 | 6.8617 | 6.9565 | 7.4273 | 7.8983
| CLONSHAUGH | 10 | 1 | Conservative [MW] |  |  | 13.8792 | 13.9398 | 14.0043 | 14.0684 | 14.1321 | 14.2028 | 14.2399 | 14.2792 | 14.3213 | 14.3655 | 14.4079 | 14.4484 | 14.4953 | 14.5403 | 14.5872 | 14.6322 | 14.8621 | 15.0917
|  |  |  | Best View [MW] |  |  | 13.8792 | 13.9491 | 14.0137 | 14.0852 | 14.1588 | 14.2387 | 14.2839 | 14.3306 | 14.3794 | 14.4297 | 14.4775 | 14.5312 | 14.582 | 14.6342 | 14.6878 | 14.747 | 15.0279 | 15.3098
|  |  |  | Base Case [MW] |  |  | 13.8792 | 13.9536 | 14.0299 | 14.1074 | 14.1903 | 14.2739 | 14.3266 | 14.3805 | 14.4395 | 14.4953 | 14.5523 | 14.6138 | 14.672 | 14.7348 | 14.798 | 14.8617 | 15.1788 | 15.496
|  |  |  | Aggressive [MW] |  |  | 13.8792 | 13.9688 | 14.0647 | 14.1628 | 14.2664 | 14.3744 | 14.4253 | 14.4733 | 14.5233 | 14.5786 | 14.6314 | 14.6855 | 14.741 | 14.7976 | 14.8552 | 14.9138 | 15.2042 | 15.4948
| CLONTARF | 10 | 1 | Conservative [MW] |  |  | 8.3585 | 8.4066 | 8.4571 | 8.5078 | 8.5604 | 8.6126 | 8.6611 | 8.7074 | 8.7588 | 8.8077 | 8.8588 | 8.9096 | 8.9625 | 9.0145 | 9.0681 | 9.1205 | 9.3858 | 9.6508
|  |  |  | Best View [MW] |  |  | 8.3585 | 8.415 | 8.4725 | 8.5327 | 8.5931 | 8.6559 | 8.7096 | 8.7647 | 8.821 | 8.8783 | 8.934 | 8.9928 | 9.0516 | 9.113 | 9.1711 | 9.2337 | 9.5349 | 9.8368
|  |  |  | Base Case [MW] |  |  | 8.3585 | 8.425 | 8.4925 | 8.5628 | 8.6334 | 8.7078 | 8.7675 | 8.8272 | 8.8891 | 8.9506 | 9.0139 | 9.0807 | 9.1461 | 9.2116 | 9.2771 | 9.3444 | 9.676 | 10.008
|  |  |  | Aggressive [MW] |  |  | 8.3585 | 8.4689 | 8.5876 | 8.7097 | 8.8376 | 8.9678 | 9.0299 | 9.0914 | 9.1546 | 9.2164 | 9.279 | 9.3419 | 9.4076 | 9.47 | 9.5339 | 9.5987 | 9.9203 | 10.2421
| CLOON | 10 | 1 | Conservative [MW] |  |  | 4.381 | 4.3944 | 4.4078 | 4.4213 | 4.4353 | 4.449 | 4.4735 | 4.4986 | 4.5243 | 4.5504 | 4.5774 | 4.6046 | 4.6326 | 4.6615 | 4.6906 | 4.7209 | 4.8692 | 5.0177
|  |  |  | Best View [MW] |  |  | 4.381 | 4.4003 | 4.4198 | 4.4397 | 4.46 | 4.4806 | 4.5149 | 4.5504 | 4.587 | 4.625 | 4.6637 | 4.7037 | 4.7454 | 4.7878 | 4.8321 | 4.877 | 5.0997 | 5.3225
|  |  |  | Base Case [MW] |  |  | 4.381 | 4.4058 | 4.4316 | 4.4577 | 4.4844 | 4.5119 | 4.5517 | 4.5928 | 4.6352 | 4.679 | 4.7245 | 4.7714 | 4.8201 | 4.8705 | 4.9228 | 4.9762 | 5.2403 | 5.5045
|  |  |  | Aggressive [MW] |  |  | 4.381 | 4.4228 | 4.4666 | 4.5119 | 4.5592 | 4.6089 | 4.6609 | 4.7152 | 4.7721 | 4.8313 | 4.8925 | 4.9566 | 5.023 | 5.0922 | 5.1642 | 5.2382 | 5.6028 | 5.9677
|  | 20 | 1 | Conservative [MW] |  |  | 2.8821 | 2.8851 | 2.8883 | 2.8915 | 2.8948 | 2.898 | 2.9036 | 2.9096 | 2.9156 | 2.9217 | 2.9281 | 2.9346 | 2.9413 | 2.9482 | 2.9552 | 2.9625 | 2.9981 | 3.0337
|  |  |  | Best View [MW] |  |  | 2.8821 | 2.8865 | 2.8911 | 2.8957 | 2.9005 | 2.9053 | 2.9134 | 2.9217 | 2.9305 | 2.9395 | 2.9487 | 2.9584 | 2.9682 | 2.9786 | 2.9893 | 3.0003 | 3.0542 | 3.1083
|  |  |  | Base Case [MW] |  |  | 2.8821 | 2.8878 | 2.8939 | 2.8999 | 2.9062 | 2.9128 | 2.922 | 2.9318 | 2.942 | 2.9524 | 2.9633 | 2.9747 | 2.9865 | 2.9987 | 3.0115 | 3.0247 | 3.0898 | 3.155
|  |  |  | Aggressive [MW] |  |  | 2.8821 | 2.8918 | 2.902 | 2.9128 | 2.924 | 2.9356 | 2.9481 | 2.9611 | 2.9749 | 2.9891 | 3.004 | 3.0197 | 3.0362 | 3.0534 | 3.0716 | 3.0904 | 3.183 | 3.2757
| CLOONBANNIN | 10 | 1 | Conservative [MW] |  |  | 3.7226 | 3.7315 | 3.7381 | 3.7466 | 3.7547 | 3.7626 | 3.7736 | 3.7861 | 3.798 | 3.8113 | 3.824 | 3.8381 | 3.8514 | 3.8662 | 3.8803 | 3.8936 | 3.9621 | 4.0305
|  |  |  | Best View [MW] |  |  | 3.7226 | 3.7326 | 3.7422 | 3.7514 | 3.7623 | 3.7707 | 3.7872 | 3.8045 | 3.8227 | 3.8417 | 3.8594 | 3.8799 | 3.8989 | 3.9207 | 3.9409 | 3.9637 | 4.0708 | 4.1783
|  |  |  | Base Case [MW] |  |  | 3.7226 | 3.7357 | 3.7501 | 3.7637 | 3.7785 | 3.7925 | 3.8094 | 3.8293 | 3.8479 | 3.8651 | 3.8851 | 3.9058 | 3.9271 | 3.9489 | 3.969 | 3.9916 | 4.0979 | 4.2047
|  |  |  | Aggressive [MW] |  |  | 3.7226 | 3.7418 | 3.7615 | 3.7816 | 3.8041 | 3.8247 | 3.846 | 3.8696 | 3.8913 | 3.9152 | 3.9391 | 3.9651 | 3.9908 | 4.0183 | 4.0476 | 4.0763 | 4.2213 | 4.3662
|  | 20 | 1 | Conservative [MW] |  |  | 3.6459 | 3.6526 | 3.6572 | 3.6636 | 3.6699 | 3.676 | 3.6832 | 3.6921 | 3.7026 | 3.7106 | 3.7203 | 3.7315 | 3.7402 | 3.7505 | 3.7624 | 3.7737 | 3.8318 | 3.8899
|  |  |  | Best View [MW] |  |  | 3.6459 | 3.6525 | 3.659 | 3.6672 | 3.6751 | 3.6808 | 3.694 | 3.7065 | 3.7202 | 3.733 | 3.747 | 3.7621 | 3.7763 | 3.7915 | 3.8078 | 3.825 | 3.9087 | 3.9925
|  |  |  | Base Case [MW] |  |  | 3.6459 | 3.6557 | 3.665 | 3.6759 | 3.6862 | 3.6979 | 3.7102 | 3.7235 | 3.7381 | 3.7518 | 3.7666 | 3.7825 | 3.7974 | 3.8133 | 3.8302 | 3.846 | 3.9278 | 4.0094
|  |  |  | Aggressive [MW] |  |  | 3.6459 | 3.6607 | 3.6746 | 3.6893 | 3.705 | 3.7214 | 3.7382 | 3.7539 | 3.7703 | 3.7896 | 3.8074 | 3.8258 | 3.8469 | 3.8663 | 3.8882 | 3.9104 | 4.0207 | 4.131
| CLOONLOUGH | 10 | 1 | Conservative [MW] |  |  | 6.25 | 6.2896 | 6.3272 | 6.3664 | 6.4035 | 6.4423 | 6.4835 | 6.5262 | 6.5665 | 6.6082 | 6.6509 | 6.6949 | 6.74 | 6.7819 | 6.8289 | 6.8724 | 7.0991 | 7.3252
|  |  |  | Best View [MW] |  |  | 6.25 | 6.2894 | 6.3303 | 6.3727 | 6.4126 | 6.4539 | 6.508 | 6.5657 | 6.6226 | 6.6785 | 6.7371 | 6.7984 | 6.8578 | 6.9236 | 6.9869 | 7.0471 | 7.3562 | 7.6648
|  |  |  | Base Case [MW] |  |  | 6.25 | 6.3038 | 6.3611 | 6.4176 | 6.4733 | 6.5316 | 6.5901 | 6.6475 | 6.7078 | 6.7667 | 6.8279 | 6.8912 | 6.9521 | 7.0187 | 7.0819 | 7.1503 | 7.4785 | 7.8076
|  |  |  | Aggressive [MW] |  |  | 6.25 | 6.3248 | 6.4028 | 6.4836 | 6.5662 | 6.6504 | 6.711 | 6.7699 | 6.8348 | 6.8974 | 6.9614 | 7.0307 | 7.0962 | 7.1665 | 7.2323 | 7.3022 | 7.6405 | 7.9796
| CLOYNE | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 13.6706 | 13.6957 | 13.7218 | 13.7479 | 13.7746 | 13.8023 | 13.8312 | 13.8602 | 13.8896 | 13.9201 | 13.951 | 13.9831 | 14.1404 | 14.2979
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 13.6757 | 13.7031 | 13.7376 | 13.7742 | 13.8112 | 13.8497 | 13.8896 | 13.9306 | 13.9723 | 14.0165 | 14.0611 | 14.1079 | 14.3359 | 14.5643
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 13.7147 | 13.7539 | 13.7899 | 13.8283 | 13.868 | 13.9082 | 13.9507 | 13.9938 | 14.0381 | 14.0851 | 14.1324 | 14.1812 | 14.4213 | 14.6617
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 13.7735 | 13.8298 | 13.8708 | 13.9124 | 13.9554 | 13.9998 | 14.0458 | 14.0931 | 14.1429 | 14.1932 | 14.2461 | 14.2994 | 14.5648 | 14.8302
| COES ROAD | 10 | 1 | Conservative [MW] |  |  | 6.5916 | 6.6208 | 6.6526 | 6.687 | 6.7195 | 6.7499 | 6.7866 | 6.8209 | 6.8618 | 6.8999 | 6.9354 | 6.9771 | 7.016 | 7.0563 | 7.098 | 7.1413 | 7.3536 | 7.5661
|  |  |  | Best View [MW] |  |  | 6.5916 | 6.6263 | 6.659 | 6.6981 | 6.7303 | 6.769 | 6.817 | 6.8693 | 6.9213 | 6.9769 | 7.0319 | 7.0853 | 7.1468 | 7.2064 | 7.2638 | 7.3284 | 7.6324 | 7.9375
|  |  |  | Base Case [MW] |  |  | 6.5916 | 6.6405 | 6.6936 | 6.746 | 6.7976 | 6.8524 | 6.9127 | 6.9707 | 7.0358 | 7.098 | 7.1618 | 7.2314 | 7.2967 | 7.3671 | 7.4422 | 7.5162 | 7.889 | 8.2617
|  |  |  | Aggressive [MW] |  |  | 6.5916 | 6.6583 | 6.7296 | 6.8002 | 6.8784 | 6.9545 | 7.0273 | 7.0993 | 7.1748 | 7.2528 | 7.3379 | 7.4195 | 7.5015 | 7.5879 | 7.6779 | 7.7704 | 8.2264 | 8.6827
| COLLIGAN | 10 | 1 | Conservative [MW] |  |  | 13.0691 | 13.1049 | 13.1429 | 13.1838 | 13.2227 | 13.2644 | 13.3164 | 13.3741 | 13.4283 | 13.4881 | 13.5484 | 13.6055 | 13.6676 | 13.7301 | 13.7933 | 13.861 | 14.1876 | 14.5149
|  |  |  | Best View [MW] |  |  | 13.0691 | 13.112 | 13.1569 | 13.1996 | 13.2445 | 13.2914 | 13.3647 | 13.4404 | 13.5229 | 13.6035 | 13.6858 | 13.774 | 13.8635 | 13.9541 | 14.0456 | 14.146 | 14.6242 | 15.1039
|  |  |  | Base Case [MW] |  |  | 13.0691 | 13.1229 | 13.1817 | 13.2408 | 13.3047 | 13.3649 | 13.4482 | 13.5373 | 13.6231 | 13.7181 | 13.8089 | 13.9083 | 14.0074 | 14.1139 | 14.2192 | 14.3266 | 14.8582 | 15.39
|  |  |  | Aggressive [MW] |  |  | 13.0691 | 13.1574 | 13.2498 | 13.3417 | 13.4407 | 13.5469 | 13.6441 | 13.749 | 13.856 | 13.9651 | 14.0796 | 14.1949 | 14.3147 | 14.4426 | 14.5689 | 14.7016 | 15.348 | 15.9956
| COLLINSTOWN | 10 | 1 | Conservative [MW] |  |  | 7.0562 | 7.0909 | 7.1232 | 7.1572 | 7.1968 | 19.6237 | 19.6499 | 19.672 | 19.697 | 19.7212 | 19.7483 | 19.7747 | 19.8005 | 19.8287 | 19.8563 | 19.8832 | 20.0195 | 20.1557
|  |  |  | Best View [MW] |  |  | 7.0562 | 7.0929 | 7.1308 | 7.1697 | 7.2094 | 19.6458 | 19.6742 | 19.7013 | 19.7315 | 19.7604 | 19.7922 | 19.8229 | 19.8522 | 19.8841 | 19.9188 | 19.9522 | 20.1225 | 20.2926
|  |  |  | Base Case [MW] |  |  | 7.0562 | 7.0986 | 7.1375 | 7.1808 | 7.2284 | 19.6696 | 19.6994 | 19.7321 | 19.767 | 19.8005 | 19.8365 | 19.8708 | 19.9077 | 19.9466 | 19.9839 | 20.0233 | 20.2147 | 20.4065
|  |  |  | Aggressive [MW] |  |  | 7.0562 | 7.1066 | 7.1556 | 7.2113 | 7.2691 | 19.7271 | 19.7563 | 19.7884 | 19.8191 | 19.8488 | 19.881 | 19.9157 | 19.9494 | 19.9856 | 20.0204 | 20.0538 | 20.2246 | 20.3952
| COLLOONEY | 20 | 1 | Conservative [MW] |  |  | 3.3931 | 3.4139 | 3.4361 | 3.4598 | 3.4817 | 3.5051 | 3.5487 | 3.5932 | 3.6388 | 3.6852 | 3.7306 | 3.7786 | 3.8274 | 3.8768 | 3.9269 | 3.9774 | 4.2289 | 4.4804
|  |  |  | Best View [MW] |  |  | 3.3931 | 3.4296 | 3.4688 | 3.5076 | 3.5459 | 3.587 | 3.6461 | 3.7071 | 3.7701 | 3.8348 | 3.8993 | 3.9672 | 4.0345 | 4.1029 | 4.1743 | 4.2441 | 4.5975 | 4.9507
|  |  |  | Base Case [MW] |  |  | 3.3931 | 3.4413 | 3.4919 | 3.5448 | 3.5969 | 3.6512 | 3.7235 | 3.7969 | 3.8731 | 3.9519 | 4.0311 | 4.1123 | 4.1953 | 4.2797 | 4.365 | 4.4506 | 4.8778 | 5.305
|  |  |  | Aggressive [MW] |  |  | 3.3931 | 3.4687 | 3.5487 | 3.6299 | 3.7134 | 3.8008 | 3.8968 | 3.9971 | 4.1014 | 4.2045 | 4.3123 | 4.4215 | 4.5331 | 4.6436 | 4.7539 | 4.862 | 5.4083 | 5.9543
| CONG | 20 | 1 | Conservative [MW] |  |  | 6.7255 | 6.7335 | 6.7413 | 6.749 | 6.7567 | 6.7601 | 6.791 | 6.8163 | 6.8439 | 6.8742 | 6.9068 | 6.9375 | 6.9665 | 7.0018 | 7.0351 | 7.0662 | 7.2276 | 7.3887
|  |  |  | Best View [MW] |  |  | 6.7255 | 6.7413 | 6.7607 | 6.7754 | 6.7937 | 6.8072 | 6.8439 | 6.8779 | 6.9178 | 6.9549 | 6.9932 | 7.0327 | 7.0776 | 7.1192 | 7.1614 | 7.2088 | 7.432 | 7.656
|  |  |  | Base Case [MW] |  |  | 6.7255 | 6.7489 | 6.7754 | 6.7966 | 6.8207 | 6.8478 | 6.8879 | 6.9368 | 6.9815 | 7.0304 | 7.0789 | 7.1312 | 7.1825 | 7.2416 | 7.2946 | 7.3549 | 7.637 | 7.9204
|  |  |  | Aggressive [MW] |  |  | 6.7255 | 6.7753 | 6.8202 | 6.8729 | 6.9244 | 6.9788 | 7.0419 | 7.1095 | 7.1769 | 7.2524 | 7.3263 | 7.4071 | 7.4893 | 7.5765 | 7.6632 | 7.7531 | 8.1942 | 8.6358
| CONVOY | 10 | 1 | Conservative [MW] |  |  | 7.5137 | 7.5226 | 7.5311 | 7.5397 | 7.548 | 7.5581 | 7.5783 | 7.6014 | 7.6235 | 7.6466 | 7.6706 | 7.6957 | 7.7195 | 7.744 | 7.7695 | 7.7957 | 7.9248 | 8.0541
|  |  |  | Best View [MW] |  |  | 7.5137 | 7.5319 | 7.5514 | 7.5719 | 7.5937 | 7.6145 | 7.6458 | 7.6789 | 7.714 | 7.7489 | 7.7853 | 7.8213 | 7.8608 | 7.8996 | 7.9398 | 7.981 | 8.1843 | 8.3877
|  |  |  | Base Case [MW] |  |  | 7.5137 | 7.5341 | 7.5574 | 7.5797 | 7.6028 | 7.627 | 7.6655 | 7.703 | 7.7457 | 7.787 | 7.8311 | 7.8757 | 7.9226 | 7.9696 | 8.0186 | 8.0716 | 8.3258 | 8.5806
|  |  |  | Aggressive [MW] |  |  | 7.5137 | 7.5462 | 7.5802 | 7.6159 | 7.6528 | 7.6911 | 7.7375 | 7.7857 | 7.8356 | 7.8887 | 7.9409 | 7.9981 | 8.0556 | 8.1175 | 8.1793 | 8.2446 | 8.5618 | 8.8796
| COOLCARRON | 10 | 1 | Conservative [MW] |  |  | 4.3075 | 4.328 | 4.3493 | 4.3735 | 4.3959 | 3.6295 | 3.6525 | 3.6773 | 3.7011 | 3.7252 | 3.751 | 3.7755 | 3.8018 | 3.8283 | 3.8548 | 3.8814 | 4.0142 | 4.147
|  |  |  | Best View [MW] |  |  | 4.3075 | 4.3294 | 4.3517 | 4.3769 | 4.3999 | 3.6364 | 3.6681 | 3.7008 | 3.7329 | 3.7673 | 3.8023 | 3.8365 | 3.8725 | 3.9089 | 3.9453 | 3.9817 | 4.1636 | 4.3456
|  |  |  | Base Case [MW] |  |  | 4.3075 | 4.337 | 4.3699 | 4.4015 | 4.4363 | 3.682 | 3.7148 | 3.7484 | 3.7827 | 3.8176 | 3.8529 | 3.8902 | 3.926 | 3.9633 | 4.0004 | 4.0387 | 4.227 | 4.4154
|  |  |  | Aggressive [MW] |  |  | 4.3075 | 4.3505 | 4.3937 | 4.4415 | 4.4884 | 3.7494 | 3.7852 | 3.8215 | 3.8581 | 3.8949 | 3.9316 | 3.9697 | 4.009 | 4.0475 | 4.0869 | 4.125 | 4.3188 | 4.5125
| COOLCORCORAN | 10 | 1 | Conservative [MW] |  |  | 14.6064 | 14.6685 | 14.7312 | 14.7947 | 14.8587 | 14.1493 | 14.2423 | 14.335 | 14.4321 | 14.5283 | 14.6234 | 14.7215 | 14.8227 | 14.9159 | 15.0162 | 15.113 | 15.6062 | 16.0988
|  |  |  | Best View [MW] |  |  | 14.6064 | 14.6808 | 14.7591 | 14.8358 | 14.9108 | 14.2209 | 14.3473 | 14.4826 | 14.6129 | 14.7502 | 14.8848 | 15.0152 | 15.1491 | 15.2853 | 15.4116 | 15.5425 | 16.1847 | 16.8277
|  |  |  | Base Case [MW] |  |  | 14.6064 | 14.7141 | 14.8241 | 14.9354 | 15.0475 | 14.3892 | 14.5185 | 14.6514 | 14.7869 | 14.9235 | 15.055 | 15.1903 | 15.3218 | 15.4534 | 15.5781 | 15.6996 | 16.3155 | 16.931
|  |  |  | Aggressive [MW] |  |  | 14.6064 | 14.763 | 14.9177 | 15.074 | 15.2352 | 14.6326 | 14.7849 | 14.9453 | 15.1015 | 15.2556 | 15.4054 | 15.5532 | 15.696 | 15.8349 | 15.9608 | 16.0754 | 16.6784 | 17.2796
| COOLMINE | 10 | 1 | Conservative [MW] |  |  | 13.1467 | 13.2726 | 13.401 | 13.5312 | 13.6677 | 13.8039 | 12.9111 | 12.9876 | 13.0716 | 13.1493 | 13.2335 | 13.3155 | 13.3993 | 13.4799 | 13.562 | 13.645 | 14.0575 | 14.4702
|  |  |  | Best View [MW] |  |  | 13.1467 | 13.2856 | 13.4285 | 13.574 | 13.7207 | 13.8728 | 12.9937 | 13.0846 | 13.1809 | 13.2726 | 13.3689 | 13.4598 | 13.5589 | 13.652 | 13.7478 | 13.846 | 14.3306 | 14.8157
|  |  |  | Base Case [MW] |  |  | 13.1467 | 13.3014 | 13.4555 | 13.6173 | 13.7803 | 13.9478 | 13.0807 | 13.1846 | 13.2914 | 13.3951 | 13.5048 | 13.6104 | 13.7163 | 13.8263 | 13.9307 | 14.0376 | 14.5657 | 15.0941
|  |  |  | Aggressive [MW] |  |  | 13.1467 | 13.3343 | 13.528 | 13.7252 | 13.9319 | 14.1352 | 13.264 | 13.3601 | 13.4527 | 13.5485 | 13.6433 | 13.7407 | 13.8361 | 13.929 | 14.023 | 14.1184 | 14.5919 | 15.0655
| COOLOCK | 10 | 1 | Conservative [MW] |  |  | 13.8652 | 13.9432 | 14.0275 | 14.109 | 14.1959 | 14.284 | 14.3397 | 14.3886 | 14.4432 | 14.4996 | 14.553 | 14.6121 | 14.6683 | 14.7255 | 14.7838 | 14.8434 | 15.1382 | 15.4332
|  |  |  | Best View [MW] |  |  | 13.8652 | 13.952 | 14.0433 | 14.135 | 14.2344 | 14.3333 | 14.3914 | 14.4543 | 14.5182 | 14.5827 | 14.6473 | 14.7124 | 14.782 | 14.8473 | 14.9168 | 14.9909 | 15.349 | 15.7079
|  |  |  | Base Case [MW] |  |  | 13.8652 | 13.9598 | 14.0614 | 14.1657 | 14.2719 | 14.3837 | 14.4521 | 14.5204 | 14.5926 | 14.6683 | 14.7433 | 14.8173 | 14.8992 | 14.9751 | 15.0586 | 15.1399 | 15.5524 | 15.9645
|  |  |  | Aggressive [MW] |  |  | 13.8652 | 13.983 | 14.1072 | 14.2367 | 14.3707 | 14.5123 | 14.5772 | 14.6426 | 14.7084 | 14.7742 | 14.8446 | 14.9108 | 14.9856 | 15.0554 | 15.1295 | 15.2027 | 15.5711 | 15.9395
| CORBALLY | 10 | 1 | Conservative [MW] |  |  | 6.876 | 6.9018 | 6.9304 | 6.9618 | 6.9917 | 7.02 | 7.052 | 7.0863 | 7.1229 | 7.1571 | 7.1935 | 7.2319 | 7.2678 | 7.3057 | 7.3454 | 7.3869 | 7.5896 | 7.7926
|  |  |  | Best View [MW] |  |  | 6.876 | 6.9046 | 6.9316 | 6.9613 | 6.9939 | 7.0247 | 7.0682 | 7.1167 | 7.1656 | 7.2146 | 7.2635 | 7.3121 | 7.365 | 7.4219 | 7.4779 | 7.5328 | 7.8102 | 8.0874
|  |  |  | Base Case [MW] |  |  | 6.876 | 6.9156 | 6.9567 | 6.9945 | 7.0381 | 7.0827 | 7.1356 | 7.1919 | 7.2467 | 7.3091 | 7.3648 | 7.4276 | 7.4923 | 7.5587 | 7.6216 | 7.6901 | 8.0176 | 8.3461
|  |  |  | Aggressive [MW] |  |  | 6.876 | 6.9398 | 7.0046 | 7.0743 | 7.1436 | 7.2168 | 7.2826 | 7.3455 | 7.414 | 7.4833 | 7.5528 | 7.6221 | 7.7003 | 7.772 | 7.8517 | 7.9285 | 8.32 | 8.7111
| CORKERMORE | 20 | 1 | Conservative [MW] |  |  | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131
|  |  |  | Best View [MW] |  |  | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131
|  |  |  | Base Case [MW] |  |  | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131
|  |  |  | Aggressive [MW] |  |  | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1131 | 2.1132 | 2.1135 | 2.1137
| COURTLOUGH | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
| COW CROSS | 10 | 1 | Conservative [MW] |  |  | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321
|  |  |  | Best View [MW] |  |  | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321
|  |  |  | Base Case [MW] |  |  | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321
|  |  |  | Aggressive [MW] |  |  | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321 | 15.3321
| CRANE | 20 | 2 | Conservative [MW] |  |  | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975
|  |  |  | Best View [MW] |  |  | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975
|  |  |  | Base Case [MW] |  |  | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975
|  |  |  | Aggressive [MW] |  |  | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975 | 9.975
| CRANMORE | 10 | 1 | Conservative [MW] |  |  | 8.009 | 8.0334 | 8.0613 | 8.0879 | 8.1128 | 8.1361 | 8.1887 | 8.2405 | 8.2912 | 8.3406 | 8.3939 | 8.4452 | 8.4998 | 8.5465 | 8.6015 | 8.6532 | 8.9204 | 9.1871
|  |  |  | Best View [MW] |  |  | 8.009 | 8.0538 | 8.0994 | 8.1403 | 8.1868 | 8.2338 | 8.3003 | 8.3659 | 8.4351 | 8.5021 | 8.5715 | 8.6426 | 8.7091 | 8.7757 | 8.8413 | 8.9049 | 9.2283 | 9.5513
|  |  |  | Base Case [MW] |  |  | 8.009 | 8.0687 | 8.1259 | 8.1853 | 8.2467 | 8.3046 | 8.3853 | 8.4649 | 8.5476 | 8.6268 | 8.7069 | 8.7805 | 8.8575 | 8.9307 | 9.0039 | 9.0686 | 9.4147 | 9.7593
|  |  |  | Aggressive [MW] |  |  | 8.009 | 8.0955 | 8.1895 | 8.2789 | 8.3733 | 8.471 | 8.5722 | 8.6736 | 8.7721 | 8.8703 | 8.959 | 9.0453 | 9.1173 | 9.1826 | 9.2242 | 9.2315 | 9.3596 | 9.482
| CRANNY | 10 | 1 | Conservative [MW] |  |  | 1.5169 | 1.5204 | 1.5259 | 1.5291 | 1.5321 | 1.5371 | 1.5415 | 1.5478 | 1.5537 | 1.5593 | 1.5647 | 1.5718 | 1.5764 | 1.5828 | 1.5889 | 1.5968 | 1.6314 | 1.6663
|  |  |  | Best View [MW] |  |  | 1.5169 | 1.5218 | 1.5265 | 1.529 | 1.5334 | 1.5396 | 1.5459 | 1.5537 | 1.5631 | 1.5718 | 1.5798 | 1.5892 | 1.598 | 1.6081 | 1.6174 | 1.6258 | 1.6702 | 1.7144
|  |  |  | Base Case [MW] |  |  | 1.5169 | 1.5236 | 1.5298 | 1.5376 | 1.5449 | 1.5518 | 1.5599 | 1.5695 | 1.5783 | 1.5885 | 1.5977 | 1.6083 | 1.62 | 1.6307 | 1.6426 | 1.6534 | 1.7102 | 1.7669
|  |  |  | Aggressive [MW] |  |  | 1.5169 | 1.5289 | 1.5417 | 1.5529 | 1.5668 | 1.5811 | 1.592 | 1.6018 | 1.6129 | 1.625 | 1.6359 | 1.6478 | 1.6607 | 1.6744 | 1.6866 | 1.7019 | 1.77 | 1.8386
| CRATLOE | 20 | 1 | Conservative [MW] |  |  | 6.0657 | 6.0965 | 6.1256 | 6.1573 | 6.1916 | 6.2241 | 6.2589 | 6.2958 | 6.3346 | 6.3754 | 6.4132 | 6.4529 | 6.4941 | 6.5321 | 6.5764 | 6.6174 | 6.8312 | 7.0445
|  |  |  | Best View [MW] |  |  | 6.0657 | 6.0993 | 6.1309 | 6.1606 | 6.1927 | 6.2276 | 6.2746 | 6.3261 | 6.3773 | 6.4325 | 6.4871 | 6.5405 | 6.5973 | 6.6576 | 6.7159 | 6.7768 | 7.0744 | 7.3725
|  |  |  | Base Case [MW] |  |  | 6.0657 | 6.107 | 6.1539 | 6.1969 | 6.2453 | 6.2897 | 6.3475 | 6.4079 | 6.4707 | 6.5355 | 6.5971 | 6.6649 | 6.7334 | 6.8021 | 6.8706 | 6.9434 | 7.2958 | 7.649
|  |  |  | Aggressive [MW] |  |  | 6.0657 | 6.1373 | 6.2088 | 6.2836 | 6.357 | 6.4372 | 6.5087 | 6.5758 | 6.6474 | 6.7234 | 6.798 | 6.8754 | 6.9501 | 7.0315 | 7.1084 | 7.1905 | 7.5873 | 7.9849
| CREAGH | 20 | 1 | Conservative [MW] |  |  | 2.4472 | 2.4772 | 2.507 | 2.5366 | 2.5658 | 2.5961 | 2.646 | 2.6962 | 2.747 | 2.7966 | 2.8495 | 2.9011 | 2.9528 | 3.0061 | 3.0593 | 3.1122 | 3.3775 | 3.6427
|  |  |  | Best View [MW] |  |  | 2.4472 | 2.4926 | 2.5388 | 2.5857 | 2.6332 | 2.6814 | 2.7512 | 2.8233 | 2.8959 | 2.9688 | 3.0417 | 3.1178 | 3.1912 | 3.2673 | 3.3416 | 3.4156 | 3.7866 | 4.1574
|  |  |  | Base Case [MW] |  |  | 2.4472 | 2.5117 | 2.5776 | 2.6435 | 2.712 | 2.7801 | 2.8582 | 2.9361 | 3.0153 | 3.0955 | 3.176 | 3.2566 | 3.3366 | 3.4174 | 3.4963 | 3.5743 | 3.9667 | 4.359
|  |  |  | Aggressive [MW] |  |  | 2.4472 | 2.546 | 2.6471 | 2.7501 | 2.8556 | 2.9631 | 3.0525 | 3.14 | 3.2282 | 3.3167 | 3.4067 | 3.4932 | 3.5791 | 3.6609 | 3.7393 | 3.8126 | 4.1927 | 4.5719
| CREESLOUGH | 20 | 1 | Conservative [MW] |  |  | 3.9968 | 4.0039 | 4.0109 | 4.0178 | 4.0244 | 4.0308 | 4.0474 | 4.0629 | 4.0819 | 4.0976 | 4.1167 | 4.1346 | 4.1515 | 4.1716 | 4.1905 | 4.208 | 4.2995 | 4.3907
|  |  |  | Best View [MW] |  |  | 3.9968 | 4.0112 | 4.0249 | 4.04 | 4.0564 | 4.0719 | 4.0948 | 4.1202 | 4.1455 | 4.1709 | 4.1983 | 4.2255 | 4.2524 | 4.2811 | 4.3092 | 4.3389 | 4.483 | 4.6274
|  |  |  | Base Case [MW] |  |  | 3.9968 | 4.0132 | 4.0307 | 4.0472 | 4.0648 | 4.0834 | 4.111 | 4.1401 | 4.1707 | 4.2024 | 4.2352 | 4.2666 | 4.301 | 4.3359 | 4.3711 | 4.4086 | 4.5899 | 4.7716
|  |  |  | Aggressive [MW] |  |  | 3.9968 | 4.0224 | 4.0479 | 4.0751 | 4.104 | 4.1324 | 4.1676 | 4.2029 | 4.2403 | 4.2795 | 4.318 | 4.3599 | 4.4028 | 4.4461 | 4.4894 | 4.5348 | 4.7562 | 4.978
| CREGG ROAD | 10 | 1 | Conservative [MW] |  |  | 2.6135 | 2.631 | 2.6474 | 2.6576 | 2.6768 | 2.6897 | 2.7099 | 2.733 | 2.7538 | 2.7721 | 2.7934 | 2.8175 | 2.8388 | 2.8571 | 2.878 | 2.9014 | 3.0119 | 3.1227
|  |  |  | Best View [MW] |  |  | 2.6135 | 2.6297 | 2.6496 | 2.6681 | 2.6851 | 2.7005 | 2.7282 | 2.7569 | 2.7865 | 2.8112 | 2.8416 | 2.8722 | 2.9026 | 2.9325 | 2.9616 | 2.9893 | 3.1316 | 3.2737
|  |  |  | Base Case [MW] |  |  | 2.6135 | 2.6375 | 2.659 | 2.6831 | 2.7045 | 2.7284 | 2.7582 | 2.7881 | 2.823 | 2.8518 | 2.8852 | 2.9173 | 2.9475 | 2.9812 | 3.0121 | 3.0457 | 3.2067 | 3.3681
|  |  |  | Aggressive [MW] |  |  | 2.6135 | 2.6473 | 2.6852 | 2.722 | 2.757 | 2.7952 | 2.8305 | 2.8634 | 2.8992 | 2.9374 | 2.9718 | 3.0073 | 3.0436 | 3.0731 | 3.1079 | 3.1405 | 3.3095 | 3.478
| CROSSMOLINA | 10 | 1 | Conservative [MW] |  |  | 1.2582 | 1.2664 | 1.2744 | 1.2826 | 1.2909 | 1.2995 | 1.3268 | 1.3549 | 1.3834 | 1.4126 | 1.4418 | 1.472 | 1.5022 | 1.5329 | 1.5639 | 1.5954 | 1.7515 | 1.9076
|  |  |  | Best View [MW] |  |  | 1.2582 | 1.2766 | 1.2951 | 1.314 | 1.333 | 1.3523 | 1.3878 | 1.4242 | 1.4614 | 1.4992 | 1.5376 | 1.5768 | 1.6164 | 1.6563 | 1.6968 | 1.7373 | 1.9398 | 2.1423
|  |  |  | Base Case [MW] |  |  | 1.2582 | 1.2826 | 1.3078 | 1.3331 | 1.3591 | 1.3852 | 1.4283 | 1.4721 | 1.5167 | 1.5622 | 1.6088 | 1.6558 | 1.7036 | 1.7516 | 1.7998 | 1.8485 | 2.0909 | 2.3333
|  |  |  | Aggressive [MW] |  |  | 1.2582 | 1.3052 | 1.3538 | 1.4041 | 1.4555 | 1.5085 | 1.5684 | 1.6302 | 1.6926 | 1.7561 | 1.8196 | 1.8833 | 1.9459 | 2.0069 | 2.0648 | 2.1192 | 2.4004 | 2.681
| CRUMLIN | 10 | 1 | Conservative [MW] |  |  | 13.6523 | 13.7134 | 13.7791 | 13.8447 | 13.91 | 13.9834 | 14.0434 | 14.1081 | 14.173 | 14.2423 | 14.3117 | 14.3808 | 14.4538 | 14.5261 | 14.5977 | 14.6776 | 15.055 | 15.4338
|  |  |  | Best View [MW] |  |  | 13.6523 | 13.7266 | 13.7994 | 13.8793 | 13.9571 | 14.0369 | 14.1121 | 14.1821 | 14.2597 | 14.3361 | 14.4155 | 14.4977 | 14.578 | 14.6605 | 14.7495 | 14.8358 | 15.2746 | 15.713
|  |  |  | Base Case [MW] |  |  | 13.6523 | 13.7368 | 13.8263 | 13.9163 | 14.0104 | 14.1045 | 14.1866 | 14.2666 | 14.3533 | 14.4376 | 14.5276 | 14.6146 | 14.707 | 14.8043 | 14.9024 | 15.0001 | 15.4895 | 15.9788
|  |  |  | Aggressive [MW] |  |  | 13.6523 | 13.7945 | 13.9485 | 14.1121 | 14.2835 | 14.4603 | 14.5453 | 14.6321 | 14.7208 | 14.8108 | 14.9062 | 14.9983 | 15.0949 | 15.1963 | 15.2927 | 15.3978 | 15.9002 | 16.404
| CULLION | 10 | 1 | Conservative [MW] |  |  | 6.9518 | 6.9728 | 6.9932 | 7.0128 | 7.0318 | 7.0499 | 7.0949 | 7.1402 | 7.1858 | 7.2369 | 7.2827 | 7.3282 | 7.3785 | 7.4282 | 7.4773 | 7.525 | 7.7674 | 8.0095
|  |  |  | Best View [MW] |  |  | 6.9518 | 6.9947 | 7.039 | 7.0793 | 7.1259 | 7.168 | 7.2368 | 7.3004 | 7.3692 | 7.437 | 7.5034 | 7.5731 | 7.64 | 7.7031 | 7.773 | 7.8375 | 8.1744 | 8.5104
|  |  |  | Base Case [MW] |  |  | 6.9518 | 6.9982 | 7.0504 | 7.0974 | 7.1445 | 7.1914 | 7.2687 | 7.3472 | 7.4263 | 7.5048 | 7.5873 | 7.6674 | 7.7432 | 7.8193 | 7.8942 | 7.9667 | 8.3357 | 8.7043
|  |  |  | Aggressive [MW] |  |  | 6.9518 | 7.0245 | 7.0965 | 7.1719 | 7.245 | 7.3201 | 7.4109 | 7.5068 | 7.5954 | 7.6861 | 7.7766 | 7.8651 | 7.9492 | 8.0323 | 8.1048 | 8.1702 | 8.5161 | 8.8609
| CURRA | 10 | 1 | Conservative [MW] |  |  | 3.7443 | 3.7526 | 3.7587 | 3.7646 | 3.7724 | 3.78 | 3.7914 | 3.8044 | 3.8147 | 3.8286 | 3.8418 | 3.8544 | 3.8662 | 3.8816 | 3.8942 | 3.9081 | 3.9741 | 4.0403
|  |  |  | Best View [MW] |  |  | 3.7443 | 3.7561 | 3.7655 | 3.7763 | 3.7887 | 3.8007 | 3.8166 | 3.8353 | 3.8529 | 3.8712 | 3.8903 | 3.9101 | 3.9305 | 3.9514 | 3.9729 | 3.9948 | 4.1033 | 4.2118
|  |  |  | Base Case [MW] |  |  | 3.7443 | 3.7606 | 3.7759 | 3.7902 | 3.8076 | 3.824 | 3.8438 | 3.8622 | 3.8831 | 3.9046 | 3.9264 | 3.9487 | 3.9711 | 3.9959 | 4.0207 | 4.0456 | 4.1699 | 4.2943
|  |  |  | Aggressive [MW] |  |  | 3.7443 | 3.7687 | 3.7909 | 3.8169 | 3.8423 | 3.8693 | 3.8918 | 3.9166 | 3.9413 | 3.9659 | 3.9925 | 4.0187 | 4.0466 | 4.076 | 4.1047 | 4.1346 | 4.2809 | 4.4273
| CURRAGLASS | 10 | 1 | Conservative [MW] |  |  | 3.6677 | 3.6758 | 3.6855 | 3.6929 | 3.7019 | 3.7125 | 3.7209 | 3.7308 | 3.7404 | 3.7495 | 3.7602 | 3.7704 | 3.7822 | 3.7915 | 3.8022 | 3.8145 | 3.8718 | 3.9294
|  |  |  | Best View [MW] |  |  | 3.6677 | 3.677 | 3.6859 | 3.6944 | 3.7045 | 3.714 | 3.7269 | 3.7389 | 3.7543 | 3.7668 | 3.7804 | 3.7952 | 3.8111 | 3.826 | 3.842 | 3.859 | 3.9412 | 4.0236
|  |  |  | Base Case [MW] |  |  | 3.6677 | 3.6796 | 3.6928 | 3.7052 | 3.7188 | 3.7335 | 3.745 | 3.7597 | 3.7736 | 3.7887 | 3.8028 | 3.8179 | 3.8341 | 3.8514 | 3.8676 | 3.8846 | 3.9675 | 4.0505
|  |  |  | Aggressive [MW] |  |  | 3.6677 | 3.6838 | 3.7025 | 3.7216 | 3.7391 | 3.7608 | 3.774 | 3.7884 | 3.8037 | 3.8201 | 3.8376 | 3.8539 | 3.8711 | 3.8891 | 3.908 | 3.9256 | 4.0169 | 4.1081
| CURRALEIGH | 20 | 1 | Conservative [MW] |  |  | 1.7696 | 1.8095 | 1.8485 | 1.8884 | 1.9293 | 8.2507 | 8.2962 | 8.3443 | 8.3924 | 8.4417 | 8.4923 | 8.5429 | 8.596 | 8.6504 | 8.7047 | 8.7601 | 9.034 | 9.3081
|  |  |  | Best View [MW] |  |  | 1.7696 | 1.812 | 1.8535 | 1.8951 | 1.9385 | 8.2639 | 8.3255 | 8.3909 | 8.4576 | 8.5255 | 8.596 | 8.669 | 8.7431 | 8.8196 | 8.8985 | 8.9799 | 9.3801 | 9.7807
|  |  |  | Base Case [MW] |  |  | 1.7696 | 1.8269 | 1.8843 | 1.9426 | 2.0028 | 8.356 | 8.4215 | 8.4895 | 8.5587 | 8.6304 | 8.7047 | 8.78 | 8.8576 | 8.9378 | 9.0203 | 9.1051 | 9.523 | 9.9412
|  |  |  | Aggressive [MW] |  |  | 1.7696 | 1.8482 | 1.928 | 2.0106 | 2.0961 | 8.4924 | 8.563 | 8.6362 | 8.7118 | 8.7885 | 8.8674 | 8.9505 | 9.0342 | 9.1201 | 9.2099 | 9.3001 | 9.7498 | 10.1996
| DALLOW | 20 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| DALTON | 20 | 1 | Conservative [MW] |  |  | 3.9335 | 3.968 | 4.0031 | 4.0387 | 4.0745 | 4.111 | 4.174 | 4.2395 | 4.3058 | 4.3739 | 4.4427 | 4.5141 | 4.5861 | 4.66 | 4.7352 | 4.8123 | 5.1927 | 5.5734
|  |  |  | Best View [MW] |  |  | 3.9335 | 3.9835 | 4.0345 | 4.0861 | 4.1387 | 4.1923 | 4.2818 | 4.3733 | 4.4685 | 4.5655 | 4.6656 | 4.7689 | 4.8744 | 4.9831 | 5.0947 | 5.2093 | 5.7745 | 6.3402
|  |  |  | Base Case [MW] |  |  | 3.9335 | 3.9986 | 4.0649 | 4.1329 | 4.2025 | 4.2738 | 4.3768 | 4.4826 | 4.5919 | 4.7052 | 4.8218 | 4.9417 | 5.0655 | 5.1934 | 5.3239 | 5.4589 | 6.1218 | 6.7854
|  |  |  | Aggressive [MW] |  |  | 3.9335 | 4.0423 | 4.1558 | 4.2739 | 4.3968 | 4.5242 | 4.6588 | 4.7979 | 4.9431 | 5.0934 | 5.2487 | 5.409 | 5.5748 | 5.7464 | 5.9227 | 6.1043 | 6.9983 | 7.8931
| DEANSGRANGE | 10 | 1 | Conservative [MW] |  |  | 12.2799 | 12.3304 | 12.386 | 12.4423 | 12.4994 | 12.5569 | 12.6057 | 12.6523 | 12.6964 | 12.7466 | 12.7988 | 12.8481 | 12.8994 | 12.952 | 13.0063 | 13.0576 | 13.3221 | 13.586
|  |  |  | Best View [MW] |  |  | 12.2799 | 12.3398 | 12.4034 | 12.4668 | 12.5337 | 12.6042 | 12.6602 | 12.7171 | 12.7708 | 12.8296 | 12.8892 | 12.9536 | 13.0141 | 13.0797 | 13.1451 | 13.2107 | 13.5381 | 13.8655
|  |  |  | Base Case [MW] |  |  | 12.2799 | 12.3463 | 12.4191 | 12.4907 | 12.5685 | 12.6486 | 12.7097 | 12.7753 | 12.8408 | 12.906 | 12.9753 | 13.0483 | 13.1207 | 13.1965 | 13.2711 | 13.3489 | 13.7293 | 14.1102
|  |  |  | Aggressive [MW] |  |  | 12.2799 | 12.3781 | 12.4851 | 12.5962 | 12.7108 | 12.8359 | 12.897 | 12.9625 | 13.028 | 13.0978 | 13.1673 | 13.2364 | 13.3092 | 13.3857 | 13.461 | 13.5398 | 13.9244 | 14.3097
| DEERPARK | 10 | 1 | Conservative [MW] |  |  | 6.3077 | 6.3371 | 6.3606 | 6.3918 | 6.4169 | 18.9145 | 18.9567 | 19.005 | 19.0511 | 19.0991 | 19.1488 | 19.1966 | 19.2499 | 19.3009 | 19.3577 | 19.4115 | 19.6885 | 19.965
|  |  |  | Best View [MW] |  |  | 6.3077 | 6.3376 | 6.3702 | 6.4009 | 6.4343 | 18.9342 | 18.9957 | 19.0614 | 19.1272 | 19.1969 | 19.2665 | 19.3393 | 19.4116 | 19.4914 | 19.5699 | 19.6516 | 20.0515 | 20.452
|  |  |  | Base Case [MW] |  |  | 6.3077 | 6.35 | 6.3892 | 6.434 | 6.4754 | 18.996 | 19.0686 | 19.1404 | 19.2114 | 19.2892 | 19.3701 | 19.4531 | 19.5385 | 19.6262 | 19.7196 | 19.8144 | 20.2847 | 20.7553
|  |  |  | Aggressive [MW] |  |  | 6.3077 | 6.3716 | 6.4368 | 6.5029 | 6.5737 | 19.1465 | 19.2306 | 19.3163 | 19.4077 | 19.5 | 19.5968 | 19.698 | 19.8037 | 19.9126 | 20.0251 | 20.1403 | 20.7091 | 21.2784
| DELVIN | 10 | 1 | Conservative [MW] |  |  | 3.6725 | 3.6852 | 3.6995 | 18.3456 | 18.361 | 18.3763 | 18.4124 | 18.443 | 18.4799 | 18.5145 | 18.5517 | 18.5903 | 18.631 | 18.6733 | 18.7139 | 18.7595 | 18.9741 | 19.1896
|  |  |  | Best View [MW] |  |  | 3.6725 | 3.6897 | 3.7061 | 18.36 | 18.3798 | 18.403 | 18.4386 | 18.4799 | 18.5189 | 18.5632 | 18.6087 | 18.6518 | 18.7 | 18.7489 | 18.8025 | 18.8534 | 19.115 | 19.3763
|  |  |  | Base Case [MW] |  |  | 3.6725 | 3.7049 | 3.7384 | 18.418 | 18.4596 | 18.503 | 18.5464 | 18.5909 | 18.6366 | 18.6873 | 18.735 | 18.7869 | 18.8439 | 18.8971 | 18.9589 | 19.0168 | 19.3165 | 19.6157
|  |  |  | Aggressive [MW] |  |  | 3.6725 | 3.7181 | 3.7638 | 18.4665 | 18.5261 | 18.5922 | 18.6432 | 18.6984 | 18.7576 | 18.8163 | 18.8786 | 18.9481 | 19.0127 | 19.0841 | 19.162 | 19.2381 | 19.6233 | 20.0083
| DENNEHYS CROSS | 10 | 1 | Conservative [MW] |  |  | 22.6081 | 22.7273 | 22.85 | 22.976 | 23.1016 | 23.2299 | 23.3556 | 23.4841 | 23.6153 | 23.7483 | 23.8788 | 24.0148 | 24.1515 | 24.2888 | 24.4261 | 24.563 | 25.2485 | 25.934
|  |  |  | Best View [MW] |  |  | 22.6081 | 22.7357 | 22.866 | 22.9948 | 23.1299 | 23.2669 | 23.4369 | 23.6096 | 23.7892 | 23.9691 | 24.1494 | 24.3331 | 24.5189 | 24.7059 | 24.8922 | 25.0817 | 26.0208 | 26.9604
|  |  |  | Base Case [MW] |  |  | 22.6081 | 22.7838 | 22.9621 | 23.1419 | 23.327 | 23.5201 | 23.6957 | 23.8722 | 24.0537 | 24.2394 | 24.4228 | 24.608 | 24.7982 | 24.9871 | 25.1777 | 25.3649 | 26.3099 | 27.2544
|  |  |  | Aggressive [MW] |  |  | 22.6081 | 22.8225 | 23.0462 | 23.2772 | 23.51 | 23.7507 | 23.9752 | 24.2082 | 24.4429 | 24.6815 | 24.9213 | 25.1594 | 25.3977 | 25.6365 | 25.8723 | 26.0999 | 27.2597 | 28.4182
| DERRYBEG | 10 | 1 | Conservative [MW] |  |  | 6.5449 | 6.5549 | 6.5687 | 6.5781 | 6.5914 | 6.6045 | 6.6308 | 6.6597 | 6.6913 | 6.7211 | 6.7537 | 6.7844 | 6.8131 | 6.8487 | 6.8823 | 6.9138 | 7.0768 | 7.2395
|  |  |  | Best View [MW] |  |  | 6.5449 | 6.57 | 6.5937 | 6.6204 | 6.6458 | 6.674 | 6.7182 | 6.7591 | 6.8052 | 6.8474 | 6.8947 | 6.9422 | 6.9898 | 7.0421 | 7.094 | 7.1456 | 7.4044 | 7.6631
|  |  |  | Base Case [MW] |  |  | 6.5449 | 6.5709 | 6.6038 | 6.6305 | 6.6641 | 6.6959 | 6.7439 | 6.7959 | 6.8471 | 6.9018 | 6.9597 | 7.016 | 7.075 | 7.1362 | 7.1994 | 7.2643 | 7.5842 | 7.9045
|  |  |  | Aggressive [MW] |  |  | 6.5449 | 6.5862 | 6.6322 | 6.6826 | 6.7285 | 6.7785 | 6.8423 | 6.9033 | 6.9699 | 7.0373 | 7.1095 | 7.1812 | 7.2566 | 7.3305 | 7.4116 | 7.4944 | 7.9038 | 8.3136
| DERRYCRAMPH | 10 | 1 | Conservative [MW] |  |  | 5.9909 | 6.0165 | 6.0443 | 6.0742 | 6.1033 | 4.936 | 4.9768 | 5.0187 | 5.0617 | 5.1057 | 5.1507 | 5.1967 | 5.2436 | 5.2892 | 5.3376 | 5.3869 | 5.631 | 5.8752
|  |  |  | Best View [MW] |  |  | 5.9909 | 6.0246 | 6.0601 | 6.0972 | 6.1359 | 4.9782 | 5.0359 | 5.0959 | 5.156 | 5.2182 | 5.2823 | 5.3459 | 5.4134 | 5.4824 | 5.5526 | 5.6237 | 5.9769 | 6.3302
|  |  |  | Base Case [MW] |  |  | 5.9909 | 6.0348 | 6.0795 | 6.1253 | 6.1715 | 5.027 | 5.0921 | 5.1569 | 5.2254 | 5.2954 | 5.3687 | 5.443 | 5.5179 | 5.5956 | 5.6731 | 5.7553 | 6.1538 | 6.5531
|  |  |  | Aggressive [MW] |  |  | 5.9909 | 6.058 | 6.129 | 6.2038 | 6.2787 | 5.1646 | 5.2486 | 5.3325 | 5.4205 | 5.5121 | 5.6045 | 5.6994 | 5.7962 | 5.8968 | 5.9976 | 6.1008 | 6.6104 | 7.1204
| DINGLE | 20 | 1 | Conservative [MW] |  |  | 5.6389 | 5.6542 | 5.669 | 5.6834 | 5.7017 | 5.7151 | 5.7498 | 5.7782 | 5.8136 | 5.8427 | 5.8785 | 5.9121 | 5.9481 | 5.9819 | 6.0177 | 6.0556 | 6.2396 | 6.4239
|  |  |  | Best View [MW] |  |  | 5.6389 | 5.6639 | 5.6917 | 5.7225 | 5.7514 | 5.7788 | 5.8203 | 5.8628 | 5.9064 | 5.9555 | 6.0006 | 6.0462 | 6.0923 | 6.1432 | 6.1943 | 6.2451 | 6.5 | 6.7548
|  |  |  | Base Case [MW] |  |  | 5.6389 | 5.6699 | 5.699 | 5.7305 | 5.7644 | 5.8005 | 5.8425 | 5.8893 | 5.9368 | 5.9889 | 6.0363 | 6.0882 | 6.1396 | 6.195 | 6.2496 | 6.308 | 6.5898 | 6.8723
|  |  |  | Aggressive [MW] |  |  | 5.6389 | 5.6854 | 5.7359 | 5.7859 | 5.8438 | 5.8963 | 5.9546 | 6.0156 | 6.0786 | 6.1436 | 6.2055 | 6.2731 | 6.3462 | 6.4194 | 6.4923 | 6.5689 | 6.9421 | 7.3159
| DOCK ROAD | 10 | 1 | Conservative [MW] |  |  | 2.4713 | 2.5016 | 14.9805 | 15.0158 | 15.0511 | 15.0877 | 15.1288 | 15.1703 | 15.2142 | 15.2584 | 15.3025 | 15.3494 | 15.3964 | 15.4447 | 15.4931 | 15.5441 | 15.7922 | 16.0408
|  |  |  | Best View [MW] |  |  | 2.4713 | 2.5019 | 14.9821 | 15.0176 | 15.0543 | 15.0922 | 15.1474 | 15.2053 | 15.2646 | 15.3267 | 15.3889 | 15.4538 | 15.5216 | 15.5907 | 15.6627 | 15.7359 | 16.0986 | 16.4616
|  |  |  | Base Case [MW] |  |  | 2.4713 | 2.514 | 15.0084 | 15.0588 | 15.1107 | 15.1628 | 15.2297 | 15.2994 | 15.3706 | 15.4447 | 15.5216 | 15.6012 | 15.6836 | 15.7687 | 15.8565 | 15.9469 | 16.392 | 16.8376
|  |  |  | Aggressive [MW] |  |  | 2.4713 | 2.5402 | 15.0695 | 15.1536 | 15.2419 | 15.3345 | 15.413 | 15.4959 | 15.5817 | 15.6701 | 15.7627 | 15.8579 | 15.9572 | 16.0606 | 16.1664 | 16.2777 | 16.8192 | 17.3618
| DODDER ROAD | 10 | 1 | Conservative [MW] |  |  | 7.8445 | 7.88 | 7.9172 | 7.954 | 7.9926 | 8.0327 | 8.0691 | 8.1053 | 8.1414 | 8.1794 | 8.2189 | 8.2582 | 8.2988 | 8.341 | 8.3823 | 8.425 | 8.6348 | 8.8447
|  |  |  | Best View [MW] |  |  | 7.8445 | 7.8869 | 7.9281 | 7.9723 | 8.0193 | 8.0646 | 8.1048 | 8.1464 | 8.189 | 8.233 | 8.2779 | 8.3235 | 8.3698 | 8.4169 | 8.4664 | 8.5163 | 8.7649 | 9.0136
|  |  |  | Base Case [MW] |  |  | 7.8445 | 7.8922 | 7.9439 | 7.9952 | 8.0479 | 8.1039 | 8.1483 | 8.1954 | 8.2431 | 8.2911 | 8.3415 | 8.3918 | 8.4442 | 8.4983 | 8.5518 | 8.6068 | 8.8778 | 9.149
|  |  |  | Aggressive [MW] |  |  | 7.8445 | 7.9263 | 8.0142 | 8.1048 | 8.2034 | 8.3045 | 8.353 | 8.4018 | 8.4508 | 8.502 | 8.553 | 8.6061 | 8.6607 | 8.717 | 8.7722 | 8.8284 | 9.1067 | 9.3852
| DONEGAL | 10 | 1 | Conservative [MW] |  |  | 7.9355 | 7.9659 | 7.9952 | 8.0256 | 8.0571 | 8.0875 | 8.1593 | 8.232 | 8.3055 | 8.381 | 8.4587 | 8.5356 | 8.6159 | 8.6967 | 8.7778 | 8.8606 | 9.2702 | 9.68
|  |  |  | Best View [MW] |  |  | 7.9355 | 7.9991 | 8.0636 | 8.1307 | 8.197 | 8.2656 | 8.3695 | 8.4764 | 8.5858 | 8.6978 | 8.8122 | 8.9286 | 9.0462 | 9.166 | 9.2886 | 9.4121 | 10.0271 | 10.6422
|  |  |  | Base Case [MW] |  |  | 7.9355 | 8.0083 | 8.0832 | 8.1593 | 8.2372 | 8.3157 | 8.4396 | 8.5671 | 8.6977 | 8.8314 | 8.9694 | 9.1079 | 9.2511 | 9.3952 | 9.5431 | 9.6929 | 10.4368 | 11.181
|  |  |  | Aggressive [MW] |  |  | 7.9355 | 8.0478 | 8.1615 | 8.2811 | 8.4028 | 8.5281 | 8.6791 | 8.8353 | 8.9956 | 9.1581 | 9.3248 | 9.4952 | 9.6683 | 9.8461 | 10.0277 | 10.2127 | 11.1286 | 12.0451
| DONNYBROOK | 10 | 1 | Conservative [MW] |  |  | 15.41 | 15.5033 | 15.5972 | 15.6957 | 15.7943 | 15.8968 | 13.4402 | 13.5345 | 13.6328 | 13.7321 | 13.8316 | 13.9348 | 14.038 | 14.1409 | 14.2462 | 14.3539 | 14.8859 | 15.4183
|  |  |  | Best View [MW] |  |  | 15.41 | 15.5165 | 15.6296 | 15.7442 | 15.8649 | 15.9803 | 13.5386 | 13.6467 | 13.7573 | 13.8701 | 13.9848 | 14.0978 | 14.2151 | 14.3361 | 14.4538 | 14.5746 | 15.1703 | 15.7665
|  |  |  | Base Case [MW] |  |  | 15.41 | 15.5332 | 15.6677 | 15.7991 | 15.9367 | 16.0776 | 13.6514 | 13.7707 | 13.8937 | 14.0173 | 14.1441 | 14.2699 | 14.4008 | 14.5297 | 14.6625 | 14.7954 | 15.4596 | 16.1238
|  |  |  | Aggressive [MW] |  |  | 15.41 | 15.6223 | 15.8522 | 16.0861 | 16.3335 | 16.5817 | 14.1712 | 14.2943 | 14.4166 | 14.5412 | 14.6679 | 14.7919 | 14.9203 | 15.0444 | 15.171 | 15.2954 | 15.9233 | 16.5509
| DONORE ROAD | 10 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914 | 20.0914
| DOUGLAS | 10 | 1 | Conservative [MW] |  |  | 13.0064 | 13.074 | 13.1456 | 13.2168 | 13.2876 | 13.3621 | 13.4356 | 13.5127 | 13.5889 | 13.6638 | 13.7467 | 13.8234 | 13.9077 | 13.9898 | 14.0747 | 14.1568 | 14.5748 | 14.9923
|  |  |  | Best View [MW] |  |  | 13.0064 | 13.0779 | 13.1531 | 13.2273 | 13.3052 | 13.3862 | 13.4819 | 13.5863 | 13.6895 | 13.7956 | 13.904 | 14.0147 | 14.1318 | 14.2448 | 14.3631 | 14.4807 | 15.0708 | 15.6607
|  |  |  | Base Case [MW] |  |  | 13.0064 | 13.1066 | 13.2057 | 13.3126 | 13.4221 | 13.5341 | 13.6373 | 13.7392 | 13.8484 | 13.9597 | 14.073 | 14.1874 | 14.3024 | 14.422 | 14.5407 | 14.6629 | 15.2647 | 15.867
|  |  |  | Aggressive [MW] |  |  | 13.0064 | 13.1284 | 13.2575 | 13.3884 | 13.5245 | 13.6696 | 13.8029 | 13.9405 | 14.0821 | 14.2313 | 14.3766 | 14.532 | 14.6856 | 14.8412 | 15.0017 | 15.1606 | 15.9596 | 16.7582
| DROMTHACKER | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35
|  |  |  | Best View [MW] |  |  | 0 | 0 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35 | 12.35
| DRUMBEAR | 10 | 1 | Conservative [MW] |  |  | 6.842 | 6.8737 | 6.9035 | 6.9363 | 13.2542 | 13.2928 | 12.349 | 12.4023 | 12.4571 | 12.5099 | 12.5669 | 12.625 | 12.684 | 12.7438 | 12.8047 | 12.8691 | 13.1819 | 13.4952
|  |  |  | Best View [MW] |  |  | 6.842 | 6.8834 | 6.9219 | 6.9621 | 13.2965 | 13.3419 | 12.4217 | 12.4956 | 12.5721 | 12.651 | 12.732 | 12.8182 | 12.9033 | 12.9929 | 13.0841 | 13.1794 | 13.6452 | 14.1116
|  |  |  | Base Case [MW] |  |  | 6.842 | 6.8907 | 6.9395 | 6.993 | 13.3409 | 13.4025 | 12.4923 | 12.5756 | 12.6634 | 12.7527 | 12.8462 | 12.9406 | 13.0387 | 13.1432 | 13.2477 | 13.3548 | 13.8833 | 14.4122
|  |  |  | Aggressive [MW] |  |  | 6.842 | 6.917 | 6.9952 | 7.0757 | 13.4768 | 13.5758 | 12.6915 | 12.7997 | 12.9127 | 13.03 | 13.1547 | 13.2824 | 13.416 | 13.5516 | 13.6949 | 13.8419 | 14.5673 | 15.2933
| DRUMCONDRA | 10 | 1 | Conservative [MW] |  |  | 14.1501 | 14.2127 | 14.2752 | 14.3384 | 14.4012 | 14.4682 | 14.5297 | 14.592 | 14.6545 | 14.7218 | 14.7889 | 14.8563 | 14.9236 | 14.9949 | 15.0701 | 15.1401 | 15.5041 | 15.8672
|  |  |  | Best View [MW] |  |  | 14.1501 | 14.2224 | 14.2933 | 14.3673 | 14.4483 | 14.5272 | 14.596 | 14.6643 | 14.7407 | 14.8117 | 14.8904 | 14.9675 | 15.0478 | 15.1307 | 15.2115 | 15.299 | 15.7187 | 16.1396
|  |  |  | Base Case [MW] |  |  | 14.1501 | 14.2335 | 14.318 | 14.4078 | 14.498 | 14.5921 | 14.669 | 14.7486 | 14.8261 | 14.9103 | 14.9964 | 15.0842 | 15.1734 | 15.2684 | 15.3593 | 15.4594 | 15.9355 | 16.4131
|  |  |  | Aggressive [MW] |  |  | 14.1501 | 14.2923 | 14.4389 | 14.5963 | 14.7626 | 14.9355 | 15.0161 | 15.0991 | 15.1885 | 15.2753 | 15.3638 | 15.4576 | 15.5522 | 15.6476 | 15.7429 | 15.8425 | 16.3291 | 16.8165
| DRUMLINE | 20 | 1 | Conservative [MW] |  |  | 7.8466 | 7.8855 | 7.9211 | 7.9601 | 7.9952 | 8.0325 | 8.0675 | 8.1015 | 8.1264 | 8.1554 | 8.1733 | 8.1866 | 8.2009 | 8.2 | 8.1975 | 8.1752 | 8.1164 | 8.0543
|  |  |  | Best View [MW] |  |  | 7.8466 | 7.8897 | 7.9233 | 7.9656 | 7.9972 | 8.0371 | 8.0844 | 8.1248 | 8.1555 | 8.1812 | 8.2 | 8.1999 | 8.1847 | 8.1483 | 8.0933 | 7.9893 | 7.6 | 7.2025
|  |  |  | Base Case [MW] |  |  | 7.8466 | 7.9015 | 7.9566 | 8.005 | 8.0514 | 8.0953 | 8.1384 | 8.1756 | 8.1952 | 8.1996 | 8.1914 | 8.146 | 8.0678 | 7.929 | 7.7188 | 7.3391 | 5.8927 | 4.418
|  |  |  | Aggressive [MW] |  |  | 7.8466 | 7.9329 | 8.0137 | 8.0846 | 8.1468 | 8.1856 | 8.1983 | 8.1983 | 8.1597 | 8.0854 | 7.9451 | 7.708 | 7.2909 | 5.7785 | 5.7911 | 5.7966 | 5.8433 | 5.8887
| DRUMQUIN | 10 | 1 | Conservative [MW] |  |  | 4.063 | 4.0753 | 4.089 | 4.1023 | 4.1169 | 4.1309 | 4.149 | 4.1701 | 4.1878 | 4.2085 | 4.2301 | 4.2502 | 4.2711 | 4.2927 | 4.3149 | 4.3377 | 4.4501 | 4.5626
|  |  |  | Best View [MW] |  |  | 4.063 | 4.0767 | 4.0919 | 4.1062 | 4.1219 | 4.1391 | 4.1647 | 4.1922 | 4.2215 | 4.2502 | 4.2803 | 4.3095 | 4.3424 | 4.3739 | 4.4064 | 4.4396 | 4.6037 | 4.7679
|  |  |  | Base Case [MW] |  |  | 4.063 | 4.0861 | 4.1093 | 4.135 | 4.1585 | 4.1842 | 4.2153 | 4.2454 | 4.2787 | 4.3107 | 4.3456 | 4.3811 | 4.4168 | 4.4525 | 4.4903 | 4.5277 | 4.7157 | 4.9037
|  |  |  | Aggressive [MW] |  |  | 4.063 | 4.1039 | 4.1452 | 4.1911 | 4.2365 | 4.2856 | 4.3205 | 4.3555 | 4.3928 | 4.4321 | 4.4706 | 4.5106 | 4.5516 | 4.5933 | 4.6353 | 4.6797 | 4.8955 | 5.1117
| DRYBRIDGE | 10 | 1 | Conservative [MW] |  |  | 18.3094 | 18.3712 | 18.4381 | 18.5021 | 18.5715 | 18.2454 | 18.3348 | 18.4309 | 18.5253 | 18.6222 | 18.725 | 18.8259 | 18.9319 | 19.0391 | 19.1519 | 19.2649 | 19.8291 | 20.3935
|  |  |  | Best View [MW] |  |  | 18.3094 | 18.3826 | 18.4595 | 18.5407 | 18.6219 | 18.3064 | 18.4249 | 18.5428 | 18.668 | 18.7956 | 18.9253 | 19.0604 | 19.197 | 19.3418 | 19.4911 | 19.6398 | 20.3849 | 21.1299
|  |  |  | Base Case [MW] |  |  | 18.3094 | 18.4151 | 18.5251 | 18.6385 | 18.7557 | 18.4804 | 18.6247 | 18.773 | 18.9274 | 19.0837 | 19.2489 | 19.4222 | 19.5985 | 19.7768 | 19.9646 | 20.1609 | 21.1199 | 22.0803
|  |  |  | Aggressive [MW] |  |  | 18.3094 | 18.4511 | 18.6022 | 18.7618 | 18.9247 | 18.7034 | 18.8926 | 19.0959 | 19.3073 | 19.5243 | 19.7531 | 19.9925 | 20.2399 | 20.4966 | 20.7606 | 21.0367 | 22.3849 | 23.7352
| DULEEK | 20 | 1 | Conservative [MW] |  |  | 0.96416 | 1.0052 | 1.0465 | 1.0886 | 1.1315 | 1.1752 | 1.2303 | 0.67197 | 0.73142 | 0.79173 | 0.8527 | 0.91498 | 0.97847 | 1.0424 | 1.1074 | 1.1735 | 1.5012 | 1.829
|  |  |  | Best View [MW] |  |  | 0.96416 | 1.0121 | 1.0617 | 1.1114 | 1.1627 | 1.2141 | 1.2855 | 0.74264 | 0.81823 | 0.89583 | 0.97404 | 1.0546 | 1.1361 | 1.2182 | 1.3022 | 1.387 | 1.8088 | 2.2308
|  |  |  | Base Case [MW] |  |  | 0.96416 | 1.0322 | 1.1014 | 1.173 | 1.2462 | 1.3218 | 1.4087 | 0.88218 | 0.97491 | 1.0693 | 1.1649 | 1.2631 | 1.3624 | 1.4615 | 1.5615 | 1.6621 | 2.1635 | 2.6651
|  |  |  | Aggressive [MW] |  |  | 0.96416 | 1.0557 | 1.1514 | 1.2498 | 1.3512 | 1.4561 | 1.5717 | 1.075 | 1.1974 | 1.3221 | 1.4476 | 1.5749 | 1.7017 | 1.827 | 1.9485 | 2.0642 | 2.6582 | 3.2512
| DUN LAOGHAIRE | 10 | 1 | Conservative [MW] |  |  | 13.9716 | 14.0324 | 14.0978 | 14.1628 | 14.232 | 14.3008 | 14.3536 | 14.408 | 14.4678 | 14.5249 | 14.5827 | 14.6418 | 14.7018 | 14.7628 | 14.8245 | 14.887 | 15.1973 | 15.5077
|  |  |  | Best View [MW] |  |  | 13.9716 | 14.0424 | 14.1202 | 14.1963 | 14.2751 | 14.3559 | 14.4201 | 14.4846 | 14.5536 | 14.6226 | 14.6911 | 14.7638 | 14.8357 | 14.9118 | 14.9865 | 15.0649 | 15.4472 | 15.8301
|  |  |  | Base Case [MW] |  |  | 13.9716 | 14.0536 | 14.1371 | 14.2261 | 14.3155 | 14.4055 | 14.4796 | 14.5572 | 14.6334 | 14.7128 | 14.7904 | 14.8751 | 14.9576 | 15.0422 | 15.1331 | 15.2207 | 15.6676 | 16.114
|  |  |  | Aggressive [MW] |  |  | 13.9716 | 14.0886 | 14.2157 | 14.3435 | 14.4843 | 14.6231 | 14.7003 | 14.7763 | 14.8512 | 14.9296 | 15.0105 | 15.0941 | 15.1759 | 15.2643 | 15.3501 | 15.4425 | 15.8867 | 16.3321
| DUNDALK | 10 | 1 | Conservative [MW] |  |  | 11.6499 | 11.7083 | 11.7678 | 11.8283 | 11.8897 | 11.952 | 12.0192 | 12.0897 | 12.1607 | 12.2348 | 12.309 | 12.3832 | 12.4605 | 12.5406 | 12.6203 | 12.6994 | 13.0967 | 13.4939
|  |  |  | Best View [MW] |  |  | 11.6499 | 11.7129 | 11.7792 | 11.8463 | 11.9164 | 11.9872 | 12.0841 | 12.1792 | 12.2809 | 12.383 | 12.4885 | 12.5969 | 12.7079 | 12.8243 | 12.9393 | 13.0591 | 13.6453 | 14.2323
|  |  |  | Base Case [MW] |  |  | 11.6499 | 11.7416 | 11.8399 | 11.9418 | 12.0443 | 12.1496 | 12.2614 | 12.3783 | 12.4972 | 12.6203 | 12.744 | 12.8745 | 13.0044 | 13.1398 | 13.2803 | 13.4215 | 14.1257 | 14.8301
|  |  |  | Aggressive [MW] |  |  | 11.6499 | 11.7769 | 11.9095 | 12.0499 | 12.1944 | 12.3452 | 12.4825 | 12.6246 | 12.7705 | 12.9229 | 13.0772 | 13.2396 | 13.402 | 13.57 | 13.7424 | 13.9212 | 14.7979 | 15.6758
| DUNDRUM | 10 | 1 | Conservative [MW] |  |  | 12.0178 | 12.0945 | 12.1784 | 12.2601 | 12.3442 | 12.4343 | 12.4991 | 12.5682 | 12.6372 | 12.7109 | 12.7797 | 12.8525 | 12.9294 | 13.0055 | 13.0808 | 13.1594 | 13.5437 | 13.9285
|  |  |  | Best View [MW] |  |  | 12.0178 | 12.1097 | 12.2022 | 12.299 | 12.3999 | 12.5005 | 12.5803 | 12.6633 | 12.749 | 12.8324 | 12.9176 | 13.0049 | 13.0941 | 13.1845 | 13.2808 | 13.3731 | 13.845 | 14.3163
|  |  |  | Base Case [MW] |  |  | 12.0178 | 12.1184 | 12.2259 | 12.3358 | 12.447 | 12.5638 | 12.6588 | 12.7504 | 12.8471 | 12.9444 | 13.0415 | 13.1427 | 13.2432 | 13.3472 | 13.4541 | 13.5639 | 14.1052 | 14.647
|  |  |  | Aggressive [MW] |  |  | 12.0178 | 12.1669 | 12.3243 | 12.4884 | 12.6571 | 12.8385 | 12.9289 | 13.0203 | 13.1172 | 13.2098 | 13.307 | 13.4088 | 13.5097 | 13.6097 | 13.7132 | 13.8194 | 14.3431 | 14.8673
| DUNGLOE | 10 | 1 | Conservative [MW] |  |  | 4.2503 | 4.2605 | 4.2703 | 4.2822 | 4.2914 | 4.3025 | 4.3258 | 4.3495 | 4.3734 | 4.3974 | 4.424 | 4.448 | 4.4744 | 4.5005 | 4.5264 | 4.5518 | 4.68 | 4.8081
|  |  |  | Best View [MW] |  |  | 4.2503 | 4.2737 | 4.2953 | 4.3152 | 4.3381 | 4.3615 | 4.3956 | 4.4301 | 4.4646 | 4.4989 | 4.5352 | 4.5709 | 4.6081 | 4.6438 | 4.6804 | 4.7176 | 4.9021 | 5.0867
|  |  |  | Base Case [MW] |  |  | 4.2503 | 4.2761 | 4.2996 | 4.3256 | 4.3515 | 4.3774 | 4.4179 | 4.4593 | 4.5011 | 4.5429 | 4.5841 | 4.627 | 4.6711 | 4.713 | 4.7548 | 4.7957 | 5.0025 | 5.2091
|  |  |  | Aggressive [MW] |  |  | 4.2503 | 4.289 | 4.327 | 4.3668 | 4.4054 | 4.445 | 4.4932 | 4.5441 | 4.5914 | 4.6425 | 4.691 | 4.7414 | 4.79 | 4.8382 | 4.8815 | 4.9244 | 5.1401 | 5.3557
| DUNLEER | 10 | 1 | Conservative [MW] |  |  | 1.4621 | 1.4955 | 1.5299 | 1.5645 | 1.6 | 1.6365 | 1.6752 | 1.7156 | 1.7562 | 1.7984 | 1.8409 | 1.8843 | 1.9286 | 1.9739 | 2.0191 | 2.0661 | 2.2965 | 2.5271
|  |  |  | Best View [MW] |  |  | 1.4621 | 1.4994 | 1.5378 | 1.5765 | 1.6162 | 1.6569 | 1.7114 | 1.7677 | 1.825 | 1.8843 | 1.9454 | 2.0075 | 2.0713 | 2.1367 | 2.2039 | 2.2726 | 2.6121 | 2.9519
|  |  |  | Base Case [MW] |  |  | 1.4621 | 1.5162 | 1.5723 | 1.6298 | 1.6893 | 1.7509 | 1.8145 | 1.8815 | 1.9494 | 2.0191 | 2.0915 | 2.1655 | 2.241 | 2.3188 | 2.3991 | 2.4802 | 2.8836 | 3.2872
|  |  |  | Aggressive [MW] |  |  | 1.4621 | 1.5355 | 1.6122 | 1.6922 | 1.7761 | 1.8624 | 1.9415 | 2.0228 | 2.1066 | 2.1929 | 2.2824 | 2.3741 | 2.4686 | 2.5657 | 2.6638 | 2.765 | 3.2628 | 3.7611
| DUNMANWAY | 10 | 1 | Conservative [MW] |  |  | 7.4372 | 7.4579 | 7.4798 | 7.5004 | 7.5243 | 7.545 | 7.5674 | 7.5907 | 7.6151 | 7.6383 | 7.6643 | 7.6892 | 7.7149 | 7.7413 | 7.7684 | 7.7942 | 7.9266 | 8.0587
|  |  |  | Best View [MW] |  |  | 7.4372 | 7.4599 | 7.4816 | 7.5041 | 7.5275 | 7.5517 | 7.5819 | 7.6143 | 7.6466 | 7.6808 | 7.7149 | 7.7507 | 7.7862 | 7.8232 | 7.8618 | 7.9017 | 8.0978 | 8.2941
|  |  |  | Base Case [MW] |  |  | 7.4372 | 7.4681 | 7.4988 | 7.5314 | 7.564 | 7.5982 | 7.6293 | 7.6625 | 7.6956 | 7.7304 | 7.7669 | 7.8051 | 7.8427 | 7.8818 | 7.9222 | 7.9617 | 8.1617 | 8.3615
|  |  |  | Aggressive [MW] |  |  | 7.4372 | 7.4804 | 7.5216 | 7.5668 | 7.6137 | 7.6641 | 7.6978 | 7.7334 | 7.7706 | 7.8091 | 7.8471 | 7.8864 | 7.929 | 7.9706 | 8.0131 | 8.0585 | 8.2779 | 8.4977
|  | 20 | 1 | Conservative [MW] |  |  | 1.7712 | 1.7867 | 1.8026 | 1.8189 | 1.8357 | 1.8528 | 1.8701 | 1.8877 | 1.9056 | 1.924 | 1.9428 | 1.9621 | 1.9819 | 2.0019 | 2.0226 | 2.0437 | 2.148 | 2.2524
|  |  |  | Best View [MW] |  |  | 1.7712 | 1.7876 | 1.8045 | 1.8218 | 1.8395 | 1.8577 | 1.8811 | 1.905 | 1.9298 | 1.9554 | 1.9819 | 2.009 | 2.0371 | 2.0659 | 2.0956 | 2.1263 | 2.277 | 2.428
|  |  |  | Base Case [MW] |  |  | 1.7712 | 1.7937 | 1.8171 | 1.8413 | 1.8664 | 1.8922 | 1.9167 | 1.9419 | 1.9679 | 1.9947 | 2.0223 | 2.0509 | 2.0803 | 2.1105 | 2.1415 | 2.1737 | 2.3315 | 2.4895
|  |  |  | Aggressive [MW] |  |  | 1.7712 | 1.8024 | 1.8351 | 1.8694 | 1.9053 | 1.9429 | 1.9696 | 1.9968 | 2.0251 | 2.0542 | 2.0842 | 2.1151 | 2.1471 | 2.1799 | 2.2138 | 2.2487 | 2.4203 | 2.5922
| EAST ATHLONE | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
| EAST GALWAY | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309 | 19.6309
| EAST WALL ROAD | 10 | 1 | Conservative [MW] |  |  | 15.2676 | 15.3485 | 15.4314 | 15.521 | 15.6079 | 15.6961 | 15.7813 | 15.8645 | 15.9453 | 16.033 | 16.1226 | 16.2093 | 16.3021 | 16.3914 | 16.4864 | 16.5819 | 17.0579 | 17.5341
|  |  |  | Best View [MW] |  |  | 15.2676 | 15.3606 | 15.4622 | 15.5632 | 15.6679 | 15.7708 | 15.8661 | 15.9617 | 16.0581 | 16.1545 | 16.2555 | 16.3557 | 16.4597 | 16.5667 | 16.6721 | 16.7798 | 17.3123 | 17.8451
|  |  |  | Base Case [MW] |  |  | 15.2676 | 15.3767 | 15.4913 | 15.6112 | 15.7351 | 15.8581 | 15.9643 | 16.0648 | 16.173 | 16.2836 | 16.3963 | 16.506 | 16.6215 | 16.7424 | 16.8579 | 16.982 | 17.5796 | 18.1785
|  |  |  | Aggressive [MW] |  |  | 15.2676 | 15.4564 | 15.6539 | 15.8658 | 16.0847 | 16.3145 | 16.4218 | 16.5265 | 16.6386 | 16.7521 | 16.867 | 16.9818 | 17.0961 | 17.2149 | 17.3316 | 17.4511 | 18.0412 | 18.6317
| EDENDERRY | 20 | 1 | Conservative [MW] |  |  | 12.884 | 12.9479 | 13.0131 | 13.0743 | 13.1406 | 13.2073 | 13.2946 | 13.3795 | 13.4665 | 13.5549 | 13.6447 | 13.7402 | 13.8318 | 13.9284 | 14.0205 | 14.117 | 14.5877 | 15.0592
|  |  |  | Best View [MW] |  |  | 12.884 | 12.9648 | 13.0447 | 13.1269 | 13.2119 | 13.2946 | 13.4094 | 13.521 | 13.6381 | 13.7599 | 13.8811 | 14.0014 | 14.1292 | 14.2542 | 14.3859 | 14.518 | 15.1774 | 15.8369
|  |  |  | Base Case [MW] |  |  | 12.884 | 12.9807 | 13.0743 | 13.176 | 13.2739 | 13.3795 | 13.5078 | 13.6463 | 13.7809 | 13.9233 | 14.0686 | 14.2153 | 14.3632 | 14.515 | 14.6692 | 14.8244 | 15.5975 | 16.3707
|  |  |  | Aggressive [MW] |  |  | 12.884 | 13.007 | 13.1301 | 13.2601 | 13.3923 | 13.5262 | 13.6873 | 13.8543 | 14.0255 | 14.1987 | 14.3734 | 14.5554 | 14.738 | 14.9229 | 15.1069 | 15.2905 | 16.2095 | 17.1285
| EDGEWORTHSTOWN | 20 | 1 | Conservative [MW] |  |  | 3.297 | 3.3168 | 3.3369 | 3.3572 | 3.3778 | 3.3986 | 3.4476 | 3.4976 | 3.5491 | 3.6019 | 3.6557 | 3.7111 | 3.7677 | 3.8259 | 3.8854 | 3.9463 | 4.2472 | 4.5484
|  |  |  | Best View [MW] |  |  | 3.297 | 3.3362 | 3.3764 | 3.4171 | 3.4589 | 3.5018 | 3.5624 | 3.6249 | 3.6894 | 3.7554 | 3.8232 | 3.8933 | 3.9653 | 4.0393 | 4.1153 | 4.1937 | 4.5792 | 4.9652
|  |  |  | Base Case [MW] |  |  | 3.297 | 3.3432 | 3.3908 | 3.4394 | 3.4893 | 3.5403 | 3.617 | 3.6967 | 3.7791 | 3.8645 | 3.9526 | 4.0444 | 4.1387 | 4.2367 | 4.3379 | 4.4423 | 4.9558 | 5.4698
|  |  |  | Aggressive [MW] |  |  | 3.297 | 3.3715 | 3.449 | 3.5294 | 3.613 | 3.7 | 3.8018 | 3.9076 | 4.0184 | 4.1337 | 4.2539 | 4.379 | 4.5091 | 4.6444 | 4.7854 | 4.9318 | 5.6493 | 6.3677
| EMYVALE | 20 | 1 | Conservative [MW] |  |  | 3.6319 | 3.6474 | 3.6625 | 3.6769 | 3.6924 | 3.7091 | 3.7307 | 3.7528 | 3.7772 | 3.8002 | 3.8236 | 3.8474 | 3.8734 | 3.8977 | 3.9241 | 3.9486 | 4.0761 | 4.2032
|  |  |  | Best View [MW] |  |  | 3.6319 | 3.6509 | 3.6707 | 3.6914 | 3.711 | 3.7314 | 3.7618 | 3.7933 | 3.826 | 3.8595 | 3.8939 | 3.9289 | 3.9623 | 3.9999 | 4.0355 | 4.073 | 4.2556 | 4.4384
|  |  |  | Base Case [MW] |  |  | 3.6319 | 3.6553 | 3.6808 | 3.7049 | 3.7308 | 3.7569 | 3.7921 | 3.8278 | 3.8639 | 3.9 | 3.94 | 3.9776 | 4.0187 | 4.0587 | 4.0996 | 4.1409 | 4.3462 | 4.5517
|  |  |  | Aggressive [MW] |  |  | 3.6319 | 3.6683 | 3.7082 | 3.7479 | 3.7888 | 3.8308 | 3.8753 | 3.92 | 3.9666 | 4.0146 | 4.0636 | 4.113 | 4.1643 | 4.2147 | 4.268 | 4.3188 | 4.5794 | 4.8397
| ENNIS NORTH | 10 | 1 | Conservative [MW] |  |  | 6.48 | 6.5085 | 6.5403 | 6.5702 | 6.5987 | 6.6299 | 6.6699 | 6.7114 | 6.7543 | 6.7938 | 6.8391 | 6.8807 | 6.928 | 6.9712 | 7.0201 | 7.0645 | 7.2984 | 7.5316
|  |  |  | Best View [MW] |  |  | 6.48 | 6.5106 | 6.5439 | 6.5752 | 6.6092 | 6.6409 | 6.6992 | 6.7603 | 6.8192 | 6.8804 | 6.9435 | 7.0082 | 7.0738 | 7.1454 | 7.2121 | 7.2785 | 7.6113 | 7.944
|  |  |  | Base Case [MW] |  |  | 6.48 | 6.5323 | 6.5842 | 6.6357 | 6.6865 | 6.7456 | 6.8067 | 6.8738 | 6.9415 | 7.0142 | 7.0816 | 7.1583 | 7.2281 | 7.3063 | 7.3814 | 7.4582 | 7.8379 | 8.2178
|  |  |  | Aggressive [MW] |  |  | 6.48 | 6.5688 | 6.6611 | 6.7553 | 6.8552 | 6.9543 | 7.031 | 7.1058 | 7.1834 | 7.2625 | 7.3428 | 7.4234 | 7.5087 | 7.5868 | 7.673 | 7.7548 | 8.1754 | 8.5953
| ENNISCRONE | 20 | 1 | Conservative [MW] |  |  | 0.30777 | 0.31686 | 0.32578 | 0.33499 | 0.3442 | 0.35352 | 0.38407 | 0.41538 | 0.44765 | 0.48086 | 0.51481 | 0.54968 | 0.58517 | 0.62181 | 0.65902 | 0.6968 | 0.88419 | 1.0717
|  |  |  | Best View [MW] |  |  | 0.30777 | 0.32804 | 0.34863 | 0.36945 | 0.3907 | 0.41228 | 0.4527 | 0.49449 | 0.5376 | 0.58193 | 0.62744 | 0.67416 | 0.72213 | 0.77162 | 0.82232 | 0.87419 | 1.1304 | 1.3868
|  |  |  | Base Case [MW] |  |  | 0.30777 | 0.33499 | 0.36257 | 0.39097 | 0.41975 | 0.44956 | 0.49905 | 0.54986 | 0.6025 | 0.65698 | 0.71331 | 0.77119 | 0.83101 | 0.89237 | 0.95592 | 1.0214 | 1.3436 | 1.6661
|  |  |  | Aggressive [MW] |  |  | 0.30777 | 0.35985 | 0.4141 | 0.47104 | 0.53065 | 0.5926 | 0.66442 | 0.73905 | 0.81704 | 0.89816 | 0.98243 | 1.0701 | 1.161 | 1.2538 | 1.3493 | 1.4475 | 1.9312 | 2.4154
| ENNISKEANE | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| ENNISTYMON | 10 | 1 | Conservative [MW] |  |  | 2.0778 | 2.1172 | 2.156 | 2.1958 | 2.2365 | 14.919 | 14.9894 | 15.0609 | 15.1336 | 15.209 | 15.2857 | 15.3633 | 15.4439 | 15.5253 | 15.6077 | 15.6947 | 16.1176 | 16.5412
|  |  |  | Best View [MW] |  |  | 2.0778 | 2.1207 | 2.1643 | 2.2075 | 2.2527 | 14.9454 | 15.0448 | 15.1482 | 15.2538 | 15.3633 | 15.4767 | 15.5938 | 15.7126 | 15.8369 | 15.9645 | 16.0972 | 16.7471 | 17.3979
|  |  |  | Base Case [MW] |  |  | 2.0778 | 2.1456 | 2.2144 | 2.2858 | 2.3569 | 15.1191 | 15.232 | 15.3504 | 15.4724 | 15.5978 | 15.7286 | 15.8623 | 16.0027 | 16.1457 | 16.2932 | 16.4469 | 17.1989 | 17.9519
|  |  |  | Aggressive [MW] |  |  | 2.0778 | 2.1971 | 2.32 | 2.4455 | 2.5737 | 15.4952 | 15.6309 | 15.7694 | 15.9146 | 16.064 | 16.2175 | 16.3768 | 16.5418 | 16.7118 | 16.889 | 17.0705 | 17.9665 | 18.8632
| ERRIGAL | 10 | 1 | Conservative [MW] |  |  | 7.1756 | 7.1978 | 7.219 | 7.2416 | 7.2651 | 7.2879 | 7.3211 | 7.3524 | 7.386 | 7.4217 | 7.4573 | 7.4929 | 7.5282 | 7.5675 | 7.6043 | 7.6429 | 7.831 | 8.0195
|  |  |  | Best View [MW] |  |  | 7.1756 | 7.2045 | 7.2318 | 7.2619 | 7.2903 | 7.3214 | 7.3657 | 7.4126 | 7.4599 | 7.5092 | 7.5607 | 7.6119 | 7.6647 | 7.719 | 7.7765 | 7.8329 | 8.118 | 8.4029
|  |  |  | Base Case [MW] |  |  | 7.1756 | 7.2097 | 7.2457 | 7.2816 | 7.319 | 7.3582 | 7.4087 | 7.4611 | 7.5147 | 7.5715 | 7.6293 | 7.6875 | 7.7483 | 7.8112 | 7.8758 | 7.9419 | 8.2683 | 8.5949
|  |  |  | Aggressive [MW] |  |  | 7.1756 | 7.2304 | 7.2858 | 7.3436 | 7.4036 | 7.4673 | 7.5322 | 7.6001 | 7.6703 | 7.7448 | 7.8183 | 7.8972 | 7.9786 | 8.0617 | 8.1457 | 8.2346 | 8.6659 | 9.098
|  | 20 | 1 | Conservative [MW] |  |  | 5.9075 | 5.9362 | 5.9656 | 5.9948 | 6.0253 | 6.0556 | 6.0985 | 6.1416 | 6.1858 | 6.2301 | 6.2763 | 6.3236 | 6.3707 | 6.4196 | 6.4684 | 6.5188 | 6.7665 | 7.0145
|  |  |  | Best View [MW] |  |  | 5.9075 | 5.9444 | 5.9818 | 6.0206 | 6.0597 | 6.099 | 6.1579 | 6.2192 | 6.2817 | 6.3452 | 6.4106 | 6.4778 | 6.5467 | 6.617 | 6.6886 | 6.7623 | 7.1255 | 7.489
|  |  |  | Base Case [MW] |  |  | 5.9075 | 5.9533 | 6 | 6.0489 | 6.0976 | 6.1481 | 6.2144 | 6.2836 | 6.3536 | 6.4259 | 6.4995 | 6.5762 | 6.6539 | 6.7329 | 6.8145 | 6.8981 | 7.3106 | 7.7235
|  |  |  | Aggressive [MW] |  |  | 5.9075 | 5.9783 | 6.0526 | 6.1297 | 6.2087 | 6.2913 | 6.3757 | 6.4633 | 6.5538 | 6.648 | 6.7431 | 6.8421 | 6.9431 | 7.0452 | 7.1504 | 7.2558 | 7.7821 | 8.3085
|  |  | 2 | Conservative [MW] |  |  | 0 | 0 | 0 | 3.9517 | 3.9516 | 3.9516 | 3.9516 | 3.9513 | 3.9511 | 3.951 | 3.9511 | 3.951 | 3.9508 | 3.9507 | 3.9507 | 3.9505 | 3.9498 | 3.9491
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 3.9516 | 3.9516 | 3.9516 | 3.9512 | 3.951 | 3.9511 | 3.9509 | 3.9507 | 3.9506 | 3.9504 | 3.9502 | 3.95 | 3.9498 | 3.949 | 3.9481
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 3.9516 | 3.9515 | 3.9513 | 3.9511 | 3.9511 | 3.9509 | 3.9507 | 3.9506 | 3.9503 | 3.9501 | 3.9498 | 3.9497 | 3.9494 | 3.9483 | 3.9472
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 3.9514 | 3.9515 | 3.9511 | 3.9508 | 3.9507 | 3.9504 | 3.9501 | 3.9498 | 3.9496 | 3.9493 | 3.9487 | 3.9481 | 3.9478 | 3.9454 | 3.9431
| FACTORY CROSS | 10 | 1 | Conservative [MW] |  |  | 13.5139 | 13.5455 | 13.5795 | 13.6121 | 13.6475 | 13.6811 | 13.7145 | 13.7506 | 13.7846 | 13.8215 | 13.8603 | 13.9017 | 13.9413 | 13.9788 | 14.0229 | 14.0646 | 14.2796 | 14.4942
|  |  |  | Best View [MW] |  |  | 13.5139 | 13.5464 | 13.5814 | 13.6189 | 13.6547 | 13.6888 | 13.7372 | 13.7868 | 13.8334 | 13.8851 | 13.9375 | 13.9949 | 14.0486 | 14.1069 | 14.1655 | 14.2284 | 14.5315 | 14.8353
|  |  |  | Base Case [MW] |  |  | 13.5139 | 13.5618 | 13.6068 | 13.6565 | 13.7073 | 13.7586 | 13.8068 | 13.8597 | 13.9096 | 13.9642 | 14.0195 | 14.0796 | 14.1358 | 14.1964 | 14.2569 | 14.3216 | 14.6337 | 14.9466
|  |  |  | Aggressive [MW] |  |  | 13.5139 | 13.5711 | 13.6319 | 13.6918 | 13.7587 | 13.8243 | 13.8883 | 13.955 | 14.0288 | 14.1006 | 14.1746 | 14.2547 | 14.3361 | 14.4186 | 14.506 | 14.598 | 15.0458 | 15.4943
| FAIRHILL | 10 | 1 | Conservative [MW] |  |  | 8.1607 | 8.1964 | 8.2316 | 8.2689 | 8.3061 | 8.3449 | 8.381 | 8.4218 | 8.4593 | 8.501 | 8.5418 | 8.582 | 8.6235 | 8.6665 | 8.7107 | 8.7538 | 8.9723 | 9.1906
|  |  |  | Best View [MW] |  |  | 8.1607 | 8.1984 | 8.2355 | 8.2743 | 8.3147 | 8.3545 | 8.4062 | 8.458 | 8.5136 | 8.5682 | 8.6242 | 8.6813 | 8.7413 | 8.7997 | 8.8605 | 8.9236 | 9.2329 | 9.5427
|  |  |  | Base Case [MW] |  |  | 8.1607 | 8.2125 | 8.2636 | 8.3184 | 8.3746 | 8.4317 | 8.485 | 8.5381 | 8.5943 | 8.6518 | 8.71 | 8.7689 | 8.8304 | 8.892 | 8.9534 | 9.0188 | 9.3351 | 9.6521
|  |  |  | Aggressive [MW] |  |  | 8.1607 | 8.2233 | 8.289 | 8.3578 | 8.4271 | 8.5008 | 8.5709 | 8.6422 | 8.7169 | 8.7929 | 8.8696 | 8.949 | 9.0301 | 9.1122 | 9.1946 | 9.2812 | 9.703 | 10.1255
| FAIRVIEW | 10 | 1 | Conservative [MW] |  |  | 12.4156 | 12.4831 | 12.5538 | 12.6231 | 12.6951 | 12.7699 | 12.8357 | 12.9052 | 12.9736 | 13.0427 | 13.115 | 13.1877 | 13.2608 | 13.3364 | 13.4116 | 13.4889 | 13.87 | 14.2515
|  |  |  | Best View [MW] |  |  | 12.4156 | 12.4958 | 12.5749 | 12.6596 | 12.7445 | 12.8319 | 12.9057 | 12.984 | 13.0615 | 13.1431 | 13.2232 | 13.3068 | 13.3885 | 13.4752 | 13.5618 | 13.6498 | 14.086 | 14.5225
|  |  |  | Base Case [MW] |  |  | 12.4156 | 12.5068 | 12.6013 | 12.7 | 12.7985 | 12.9026 | 12.9855 | 13.0709 | 13.1584 | 13.2457 | 13.3373 | 13.4298 | 13.5229 | 13.6161 | 13.7135 | 13.8099 | 14.2947 | 14.7793
|  |  |  | Aggressive [MW] |  |  | 12.4156 | 12.572 | 12.7355 | 12.906 | 13.0847 | 13.2724 | 13.3581 | 13.446 | 13.5354 | 13.6259 | 13.7171 | 13.8082 | 13.9017 | 13.9963 | 14.0894 | 14.1846 | 14.655 | 15.1257
| FERMOY NORTH | 10 | 1 | Conservative [MW] |  |  | 8.4954 | 8.5323 | 8.5744 | 8.5996 | 8.6364 | 7.9274 | 7.9537 | 7.9751 | 7.9966 | 8.0037 | 8.0088 | 8.0019 | 7.9814 | 7.9488 | 7.8948 | 7.8124 | 7.4761 | 7.1351
|  |  |  | Best View [MW] |  |  | 8.4954 | 8.5335 | 8.5752 | 8.6049 | 8.6373 | 7.9365 | 7.9698 | 7.9955 | 8.0104 | 8.0034 | 7.9825 | 7.9302 | 7.8476 | 7.7098 | 7.4857 | 7.1302 | 5.7031 | 4.2541
|  |  |  | Base Case [MW] |  |  | 8.4954 | 8.5478 | 8.6026 | 8.6429 | 8.6815 | 7.9826 | 7.9989 | 8.008 | 7.9992 | 7.9644 | 7.8939 | 7.784 | 7.6133 | 7.3289 | 6.8294 | 5.6125 | 1.4409 | -0.0001
|  |  |  | Aggressive [MW] |  |  | 8.4954 | 8.5701 | 8.6371 | 8.682 | 8.7121 | 8.0094 | 7.9969 | 7.9547 | 7.8883 | 7.7599 | 7.5693 | 7.267 | 6.6498 | 5.6133 | 5.6257 | 5.6307 | 5.6755 | 5.7191
| FERNS | 20 | 1 | Conservative [MW] |  |  | 3.0322 | 3.0431 | 3.053 | 3.0638 | 3.0744 | 3.086 | 3.111 | 3.1373 | 3.164 | 3.1909 | 3.2192 | 3.2477 | 3.2762 | 3.306 | 3.3369 | 3.3678 | 3.5222 | 3.6766
|  |  |  | Best View [MW] |  |  | 3.0322 | 3.0512 | 3.0691 | 3.0886 | 3.1077 | 3.1276 | 3.1563 | 3.1851 | 3.2152 | 3.2463 | 3.2774 | 3.3106 | 3.3437 | 3.3763 | 3.4109 | 3.4462 | 3.621 | 3.7958
|  |  |  | Base Case [MW] |  |  | 3.0322 | 3.0552 | 3.0778 | 3.1009 | 3.1255 | 3.1496 | 3.1821 | 3.2145 | 3.2489 | 3.2841 | 3.3189 | 3.3555 | 3.3926 | 3.4313 | 3.4689 | 3.5091 | 3.7033 | 3.8979
|  |  |  | Aggressive [MW] |  |  | 3.0322 | 3.0679 | 3.1045 | 3.1419 | 3.1808 | 3.2202 | 3.2675 | 3.3166 | 3.3671 | 3.4186 | 3.4722 | 3.526 | 3.5823 | 3.6391 | 3.6974 | 3.7546 | 4.0437 | 4.3325
| FINISKLIN | 10 | 1 | Conservative [MW] |  |  | 8.543 | 8.5687 | 8.5979 | 8.6203 | 8.6464 | 8.6759 | 8.7256 | 8.7795 | 8.8264 | 8.8825 | 8.9313 | 8.9831 | 9.0379 | 9.0898 | 9.1382 | 9.1885 | 9.4351 | 9.682
|  |  |  | Best View [MW] |  |  | 8.543 | 8.5863 | 8.6354 | 8.6797 | 8.7242 | 8.7687 | 8.8395 | 8.9084 | 8.975 | 9.044 | 9.1092 | 9.181 | 9.2473 | 9.3124 | 9.3756 | 9.4357 | 9.7445 | 10.0527
|  |  |  | Base Case [MW] |  |  | 8.543 | 8.6044 | 8.6627 | 8.7229 | 8.7848 | 8.8426 | 8.9244 | 9.0041 | 9.0861 | 9.1632 | 9.2401 | 9.3208 | 9.3916 | 9.4627 | 9.5257 | 9.5828 | 9.884 | 10.1843
|  |  |  | Aggressive [MW] |  |  | 8.543 | 8.6368 | 8.7264 | 8.8214 | 8.9145 | 9.0097 | 9.1107 | 9.2098 | 9.3096 | 9.4011 | 9.4921 | 9.5648 | 9.6292 | 9.6739 | 9.6961 | 9.6815 | 9.7067 | 9.7257
| FINNEA | 20 | 1 | Conservative [MW] |  |  | 3.9148 | 3.9349 | 3.9563 | 3.9775 | 3.9987 | 4.0199 | 4.0706 | 4.1219 | 4.1762 | 4.2286 | 4.2832 | 4.3381 | 4.3933 | 4.4485 | 4.5056 | 4.5625 | 4.8474 | 5.1324
|  |  |  | Best View [MW] |  |  | 3.9148 | 3.9564 | 3.9976 | 4.0397 | 4.0828 | 4.127 | 4.1893 | 4.2526 | 4.3158 | 4.3804 | 4.4463 | 4.5134 | 4.5814 | 4.6502 | 4.7196 | 4.7892 | 5.1367 | 5.4842
|  |  |  | Base Case [MW] |  |  | 3.9148 | 3.9625 | 4.0125 | 4.0633 | 4.1133 | 4.1663 | 4.2441 | 4.3226 | 4.4031 | 4.4854 | 4.5693 | 4.6542 | 4.7398 | 4.8278 | 4.9157 | 5.0026 | 5.4396 | 5.8764
|  |  |  | Aggressive [MW] |  |  | 3.9148 | 3.9927 | 4.0732 | 4.1547 | 4.2408 | 4.3262 | 4.4264 | 4.5264 | 4.6313 | 4.7363 | 4.8429 | 4.9499 | 5.0561 | 5.1645 | 5.2686 | 5.3706 | 5.8861 | 6.4013
| FOXHOLE | 20 | 1 | Conservative [MW] |  |  | 3.7673 | 3.8444 | 3.9233 | 4.0026 | 4.0843 | 4.167 | 4.2504 | 4.3348 | 4.421 | 4.5088 | 4.5983 | 4.6882 | 4.7797 | 4.8726 | 4.9669 | 5.0634 | 5.5402 | 6.0174
|  |  |  | Best View [MW] |  |  | 3.7673 | 3.8492 | 3.9316 | 4.0164 | 4.1024 | 4.1901 | 4.3033 | 4.4184 | 4.5359 | 4.6567 | 4.7785 | 4.9045 | 5.0311 | 5.1613 | 5.293 | 5.426 | 6.0873 | 6.7489
|  |  |  | Base Case [MW] |  |  | 3.7673 | 3.8783 | 3.9922 | 4.1099 | 4.2292 | 4.3523 | 4.4703 | 4.5898 | 4.7124 | 4.837 | 4.9646 | 5.0948 | 5.2263 | 5.3598 | 5.496 | 5.6324 | 6.3136 | 6.9949
|  |  |  | Aggressive [MW] |  |  | 3.7673 | 3.9211 | 4.0808 | 4.2464 | 4.4173 | 4.5946 | 4.7208 | 4.8489 | 4.9798 | 5.1132 | 5.2478 | 5.3852 | 5.5253 | 5.6653 | 5.8071 | 5.952 | 6.6682 | 7.385
| FOYNES | 10 | 1 | Conservative [MW] |  |  | 2.6083 | 2.6307 | 2.6541 | 2.6775 | 2.701 | 2.7255 | 2.7523 | 2.7792 | 2.8071 | 2.835 | 2.8639 | 2.8929 | 2.9227 | 2.9526 | 2.9834 | 3.0151 | 3.1713 | 3.3277
|  |  |  | Best View [MW] |  |  | 2.6083 | 2.6319 | 2.6555 | 2.6802 | 2.7049 | 2.7306 | 2.7664 | 2.8023 | 2.8402 | 2.879 | 2.9179 | 2.9586 | 2.9993 | 3.0419 | 3.0853 | 3.1296 | 3.3487 | 3.568
|  |  |  | Base Case [MW] |  |  | 2.6083 | 2.6388 | 2.6711 | 2.7036 | 2.7371 | 2.7716 | 2.8136 | 2.8566 | 2.9005 | 2.9464 | 2.9932 | 3.0418 | 3.0913 | 3.1415 | 3.1935 | 3.2471 | 3.5108 | 3.7748
|  |  |  | Aggressive [MW] |  |  | 2.6083 | 2.6555 | 2.7048 | 2.7563 | 2.8097 | 2.8652 | 2.9129 | 2.9635 | 3.014 | 3.0673 | 3.1213 | 3.177 | 3.2344 | 3.2932 | 3.3546 | 3.4161 | 3.7236 | 4.031
| GARRANACANTY | 20 | 1 | Conservative [MW] |  |  | 14.6721 | 14.7432 | 14.8141 | 14.8836 | 14.9521 | 15.0246 | 15.1192 | 15.2171 | 15.3125 | 15.4054 | 15.4999 | 15.5963 | 15.6937 | 15.7861 | 15.8777 | 15.9672 | 16.4203 | 16.8731
|  |  |  | Best View [MW] |  |  | 14.6721 | 14.7582 | 14.8408 | 14.9299 | 15.0149 | 15.1008 | 15.2368 | 15.3723 | 15.5119 | 15.6482 | 15.779 | 15.9138 | 16.0378 | 16.1616 | 16.2818 | 16.3887 | 16.9589 | 17.5268
|  |  |  | Base Case [MW] |  |  | 14.6721 | 14.7865 | 14.901 | 15.0146 | 15.1318 | 15.2462 | 15.3912 | 15.5362 | 15.6791 | 15.8228 | 15.9583 | 16.0953 | 16.2247 | 16.3425 | 16.4505 | 16.552 | 17.077 | 17.6008
|  |  |  | Aggressive [MW] |  |  | 14.6721 | 14.8497 | 15.0298 | 15.2093 | 15.3904 | 15.57 | 15.719 | 15.8694 | 16.0173 | 16.1541 | 16.2879 | 16.4072 | 16.5136 | 16.6031 | 16.6798 | 16.7253 | 17.0359 | 17.3413
| GARRYCASTLE | 10 | 1 | Conservative [MW] |  |  | 20.5647 | 20.6125 | 20.6628 | 20.7156 | 20.7667 | 20.8165 | 20.9023 | 20.988 | 21.0769 | 21.1696 | 21.2611 | 21.3554 | 21.4529 | 21.5488 | 21.6472 | 21.7479 | 22.2455 | 22.7434
|  |  |  | Best View [MW] |  |  | 20.5647 | 20.6415 | 20.7183 | 20.7992 | 20.8805 | 20.9655 | 21.0876 | 21.2167 | 21.3435 | 21.4811 | 21.6153 | 21.7597 | 21.904 | 22.0525 | 22.2046 | 22.3597 | 23.1273 | 23.8954
|  |  |  | Base Case [MW] |  |  | 20.5647 | 20.674 | 20.7832 | 20.9015 | 21.0192 | 21.1405 | 21.2774 | 21.4193 | 21.5653 | 21.7192 | 21.8711 | 22.0301 | 22.1944 | 22.3642 | 22.5337 | 22.7106 | 23.5755 | 24.4415
|  |  |  | Aggressive [MW] |  |  | 20.5647 | 20.7289 | 20.9033 | 21.087 | 21.2746 | 21.4688 | 21.6358 | 21.8037 | 21.9745 | 22.1526 | 22.3368 | 22.5259 | 22.7185 | 22.9186 | 23.1244 | 23.3301 | 24.3588 | 25.3875
| GARRYOWEN | 10 | 1 | Conservative [MW] |  |  | 19.9525 | 20.0142 | 20.0734 | 20.1381 | 20.2041 | 20.2714 | 20.3455 | 20.4205 | 20.4992 | 20.5783 | 20.6616 | 20.7444 | 20.827 | 20.9138 | 21.0038 | 21.0932 | 21.5421 | 21.9908
|  |  |  | Best View [MW] |  |  | 19.9525 | 20.0157 | 20.0801 | 20.1455 | 20.2126 | 20.2801 | 20.3812 | 20.4831 | 20.5946 | 20.7022 | 20.8186 | 20.9351 | 21.0509 | 21.1749 | 21.3019 | 21.4314 | 22.0721 | 22.7133
|  |  |  | Base Case [MW] |  |  | 19.9525 | 20.0367 | 20.1281 | 20.2182 | 20.3105 | 20.4091 | 20.5281 | 20.6541 | 20.782 | 20.9156 | 21.0505 | 21.1948 | 21.3389 | 21.4869 | 21.6424 | 21.7998 | 22.5817 | 23.3638
|  |  |  | Aggressive [MW] |  |  | 19.9525 | 20.0917 | 20.2373 | 20.3927 | 20.5522 | 20.7156 | 20.8603 | 21.0085 | 21.1595 | 21.3167 | 21.4755 | 21.6433 | 21.8151 | 21.9942 | 22.1753 | 22.3623 | 23.2818 | 24.2022
| GARRYSPILLANE | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.0053725 | 0.038961 | 0.13193 | 0.22958
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.026146 | 0.062352 | 0.099231 | 0.13689 | 0.32312 | 0.50947
| GARVILLE AVENUE | 10 | 1 | Conservative [MW] |  |  | 8.3024 | 8.3471 | 8.3949 | 8.4408 | 8.4895 | 8.5407 | 8.5845 | 8.6292 | 8.677 | 8.7231 | 8.772 | 8.8191 | 8.8686 | 8.9204 | 8.9698 | 9.0212 | 9.2728 | 9.5248
|  |  |  | Best View [MW] |  |  | 8.3024 | 8.3558 | 8.4106 | 8.4647 | 8.522 | 8.5804 | 8.6319 | 8.6834 | 8.7366 | 8.7894 | 8.844 | 8.8997 | 8.9566 | 9.012 | 9.0705 | 9.1294 | 9.4227 | 9.7161
|  |  |  | Base Case [MW] |  |  | 8.3024 | 8.364 | 8.4276 | 8.4928 | 8.5593 | 8.629 | 8.6842 | 8.7429 | 8.8 | 8.86 | 8.9203 | 8.9828 | 9.0451 | 9.109 | 9.1717 | 9.238 | 9.56 | 9.8826
|  |  |  | Aggressive [MW] |  |  | 8.3024 | 8.4062 | 8.5168 | 8.6319 | 8.7521 | 8.8773 | 8.9355 | 8.9941 | 9.053 | 9.1142 | 9.1753 | 9.2356 | 9.2999 | 9.3627 | 9.426 | 9.4897 | 9.8071 | 10.1246
| GILLOGUE | 10 | 1 | Conservative [MW] |  |  | 6.3091 | 6.3387 | 6.3706 | 6.4013 | 6.4307 | 6.4622 | 6.4971 | 6.1381 | 6.1765 | 6.2134 | 6.2518 | 6.2917 | 6.3299 | 6.3727 | 6.4136 | 6.4558 | 6.6632 | 6.8709
|  |  |  | Best View [MW] |  |  | 6.3091 | 6.3409 | 6.3716 | 6.401 | 6.4325 | 6.4662 | 6.5145 | 6.1679 | 6.2204 | 6.2731 | 6.3259 | 6.3819 | 6.4377 | 6.4928 | 6.5507 | 6.6111 | 6.9064 | 7.2022
|  |  |  | Base Case [MW] |  |  | 6.3091 | 6.3506 | 6.3932 | 6.4369 | 6.4814 | 6.5304 | 6.5866 | 6.2501 | 6.3116 | 6.3719 | 6.4375 | 6.5014 | 6.57 | 6.6363 | 6.7068 | 6.7777 | 7.1311 | 7.4846
|  |  |  | Aggressive [MW] |  |  | 6.3091 | 6.3787 | 6.449 | 6.5196 | 6.5972 | 6.6738 | 6.7402 | 6.4139 | 6.4861 | 6.5587 | 6.6315 | 6.7109 | 6.7857 | 6.8663 | 6.9487 | 7.0282 | 7.4334 | 7.8381
| GLASMORE | 20 | 1 | Conservative [MW] |  |  | 8.8903 | 8.0558 | 8.1189 | 8.1849 | 8.2514 | 7.6018 | 7.6423 | 7.6843 | 7.7259 | 7.769 | 7.8137 | 7.8578 | 7.9034 | 7.9505 | 7.9969 | 8.0448 | 8.2802 | 8.5159
|  |  |  | Best View [MW] |  |  | 8.8903 | 8.0615 | 8.132 | 8.2052 | 8.2809 | 7.6398 | 7.6876 | 7.7346 | 7.7852 | 7.8351 | 7.8861 | 7.9387 | 7.9924 | 8.0475 | 8.1037 | 8.1611 | 8.445 | 8.7291
|  |  |  | Base Case [MW] |  |  | 8.8903 | 8.0692 | 8.1447 | 8.227 | 8.3114 | 7.6787 | 7.7336 | 7.7876 | 7.8449 | 7.9034 | 7.9629 | 8.0234 | 8.0873 | 8.1498 | 8.2153 | 8.284 | 8.6191 | 8.9547
|  |  |  | Aggressive [MW] |  |  | 8.8903 | 8.0848 | 8.1817 | 8.2817 | 8.3893 | 7.7808 | 7.8307 | 7.882 | 7.9346 | 7.9885 | 8.0437 | 8.1001 | 8.1554 | 8.2142 | 8.2741 | 8.3349 | 8.6367 | 8.9387
| GLASNEVIN | 10 | 1 | Conservative [MW] |  |  | 7.9165 | 7.9551 | 7.9934 | 8.033 | 8.0742 | 8.1145 | 8.1517 | 8.1907 | 8.2293 | 8.2695 | 8.3114 | 8.3525 | 8.3949 | 8.4385 | 8.4811 | 8.527 | 8.7478 | 8.9692
|  |  |  | Best View [MW] |  |  | 7.9165 | 7.9612 | 8.0067 | 8.0527 | 8.1013 | 8.1498 | 8.1921 | 8.2354 | 8.2798 | 8.3249 | 8.373 | 8.4195 | 8.4687 | 8.5179 | 8.5696 | 8.6212 | 8.8792 | 9.1373
|  |  |  | Base Case [MW] |  |  | 7.9165 | 7.9676 | 8.0204 | 8.0744 | 8.1316 | 8.1895 | 8.2372 | 8.2854 | 8.3359 | 8.3864 | 8.4389 | 8.491 | 8.5472 | 8.6022 | 8.6585 | 8.7178 | 9.0064 | 9.2956
|  |  |  | Aggressive [MW] |  |  | 7.9165 | 8.003 | 8.0947 | 8.1921 | 8.2944 | 8.4015 | 8.4503 | 8.5014 | 8.5545 | 8.6072 | 8.6615 | 8.7173 | 8.772 | 8.8301 | 8.8865 | 8.9458 | 9.2346 | 9.5239
| GLEBE | 10 | 1 | Conservative [MW] |  |  | 15.8855 | 15.9289 | 15.9663 | 16.0066 | 16.0454 | 16.0875 | 16.1818 | 16.276 | 16.3753 | 16.4737 | 16.5709 | 16.6714 | 16.7748 | 16.8759 | 16.979 | 17.0838 | 17.6034 | 18.1232
|  |  |  | Best View [MW] |  |  | 15.8855 | 15.9655 | 16.0443 | 16.1213 | 16.2015 | 16.2843 | 16.3975 | 16.5152 | 16.6325 | 16.7535 | 16.8725 | 16.9931 | 17.1154 | 17.2376 | 17.3595 | 17.4845 | 18.1015 | 18.719
|  |  |  | Base Case [MW] |  |  | 15.8855 | 15.9806 | 16.0722 | 16.1638 | 16.261 | 16.3577 | 16.5025 | 16.6483 | 16.7934 | 16.9422 | 17.0978 | 17.2482 | 17.3971 | 17.5521 | 17.7003 | 17.8456 | 18.5799 | 19.3137
|  |  |  | Aggressive [MW] |  |  | 15.8855 | 16.0356 | 16.1825 | 16.3392 | 16.494 | 16.6553 | 16.8356 | 17.0199 | 17.2057 | 17.3896 | 17.5776 | 17.755 | 17.9342 | 18.1088 | 18.267 | 18.4122 | 19.1729 | 19.9314
| GLENAMADDY | 20 | 1 | Conservative [MW] |  |  | 0.36112 | 0.37666 | 0.39247 | 0.40846 | 0.4247 | 0.44098 | 0.46935 | 0.49818 | 0.52753 | 0.55709 | 0.58717 | 0.61765 | 0.64916 | 0.6802 | 0.71129 | 0.74292 | 0.89964 | 1.0564
|  |  |  | Best View [MW] |  |  | 0.36112 | 0.38361 | 0.40656 | 0.4299 | 0.45356 | 0.47755 | 0.51691 | 0.55709 | 0.59811 | 0.63957 | 0.68255 | 0.72507 | 0.76838 | 0.81229 | 0.85631 | 0.90066 | 1.1215 | 1.3425
|  |  |  | Base Case [MW] |  |  | 0.36112 | 0.39039 | 0.42041 | 0.45096 | 0.48198 | 0.51366 | 0.55849 | 0.60433 | 0.65177 | 0.69885 | 0.74676 | 0.79556 | 0.84484 | 0.8944 | 0.944 | 0.9934 | 1.2409 | 1.4884
|  |  |  | Aggressive [MW] |  |  | 0.36112 | 0.41031 | 0.46126 | 0.51366 | 0.56744 | 0.62201 | 0.67965 | 0.73717 | 0.79601 | 0.85569 | 0.91546 | 0.97543 | 1.0347 | 1.0923 | 1.1482 | 1.2005 | 1.4715 | 1.742
| GLENGARRIFF | 20 | 1 | Conservative [MW] |  |  | 3.5535 | 3.5585 | 3.5651 | 3.5716 | 3.5778 | 3.5838 | 3.5897 | 3.5954 | 3.6027 | 3.6098 | 3.6166 | 3.6232 | 3.6313 | 3.6373 | 3.6449 | 3.6522 | 3.6894 | 3.7266
|  |  |  | Best View [MW] |  |  | 3.5535 | 3.5599 | 3.566 | 3.572 | 3.5776 | 3.585 | 3.5932 | 3.603 | 3.6123 | 3.6211 | 3.6313 | 3.6411 | 3.6503 | 3.6608 | 3.6727 | 3.6841 | 3.7424 | 3.8005
|  |  |  | Base Case [MW] |  |  | 3.5535 | 3.5623 | 3.5707 | 3.5785 | 3.5879 | 3.5986 | 3.6061 | 3.6152 | 3.6257 | 3.6357 | 3.645 | 3.6559 | 3.6661 | 3.6777 | 3.6886 | 3.7009 | 3.7586 | 3.8166
|  |  |  | Aggressive [MW] |  |  | 3.5535 | 3.5653 | 3.5762 | 3.59 | 3.6029 | 3.6165 | 3.6267 | 3.6364 | 3.6454 | 3.6579 | 3.6677 | 3.6788 | 3.6913 | 3.7031 | 3.7161 | 3.7284 | 3.7919 | 3.8552
| GLENGOOLE | 10 | 1 | Conservative [MW] |  |  | 0.15044 | 0.18585 | 0.22179 | 0.25803 | 0.2948 | 0.3319 | 0.05355 | 0.1044 | 0.15593 | 0.20818 | 0.26117 | 0.31475 | 0.36896 | 0.42367 | 0.47899 | 0.53467 | 0.8121 | 1.0896
|  |  |  | Best View [MW] |  |  | 0.15044 | 0.1934 | 0.23701 | 0.28119 | 0.32601 | 0.37143 | 0.11584 | 0.1901 | 0.26582 | 0.34278 | 0.42094 | 0.50021 | 0.58039 | 0.66036 | 0.7411 | 0.82285 | 1.2289 | 1.6351
|  |  |  | Base Case [MW] |  |  | 0.15044 | 0.20787 | 0.26648 | 0.32611 | 0.38677 | 0.44869 | 0.19953 | 0.2802 | 0.36241 | 0.44603 | 0.53073 | 0.61602 | 0.70125 | 0.78787 | 0.87482 | 0.96147 | 1.3955 | 1.8295
|  |  |  | Aggressive [MW] |  |  | 0.15044 | 0.24043 | 0.33318 | 0.4287 | 0.52656 | 0.62695 | 0.38618 | 0.47472 | 0.56465 | 0.65466 | 0.74548 | 0.83717 | 0.92906 | 1.02 | 1.1099 | 1.1975 | 1.6416 | 2.0854
| GLENTIES | 10 | 1 | Conservative [MW] |  |  | 4.2797 | 4.2873 | 4.2969 | 4.3063 | 4.3154 | 4.3264 | 4.3467 | 4.3701 | 4.3916 | 4.4161 | 4.4385 | 4.4614 | 4.4846 | 4.5105 | 4.5341 | 4.5578 | 4.6762 | 4.7945
|  |  |  | Best View [MW] |  |  | 4.2797 | 4.2984 | 4.3181 | 4.3388 | 4.3603 | 4.3803 | 4.4123 | 4.443 | 4.4769 | 4.5092 | 4.5444 | 4.5774 | 4.6131 | 4.6486 | 4.6836 | 4.7206 | 4.9005 | 5.0806
|  |  |  | Base Case [MW] |  |  | 4.2797 | 4.3022 | 4.3253 | 4.3489 | 4.3704 | 4.3947 | 4.4317 | 4.4707 | 4.5113 | 4.5508 | 4.5913 | 4.6324 | 4.6736 | 4.7147 | 4.7577 | 4.8022 | 5.0207 | 5.2395
|  |  |  | Aggressive [MW] |  |  | 4.2797 | 4.3138 | 4.3484 | 4.3856 | 4.4228 | 4.4595 | 4.5051 | 4.5501 | 4.5987 | 4.6454 | 4.6946 | 4.743 | 4.7925 | 4.8422 | 4.8938 | 4.9407 | 5.1877 | 5.4339
| GLOUCESTER PLACE | 10 | 1 | Conservative [MW] |  |  | 15.7312 | 15.8264 | 15.9221 | 16.0178 | 16.1228 | 15.833 | 15.9248 | 16.0219 | 16.115 | 16.213 | 16.3106 | 16.4124 | 16.5133 | 16.613 | 16.715 | 16.8197 | 17.3362 | 17.8531
|  |  |  | Best View [MW] |  |  | 15.7312 | 15.8392 | 15.9538 | 16.0695 | 16.1864 | 15.9185 | 16.0218 | 16.1323 | 16.2409 | 16.3469 | 16.459 | 16.5724 | 16.6859 | 16.8036 | 16.9161 | 17.0312 | 17.5997 | 18.1686
|  |  |  | Base Case [MW] |  |  | 15.7312 | 15.8599 | 15.9908 | 16.1276 | 16.2651 | 16.0177 | 16.1334 | 16.2491 | 16.3694 | 16.4939 | 16.6167 | 16.7414 | 16.8629 | 16.9899 | 17.1165 | 17.2472 | 17.8898 | 18.5331
|  |  |  | Aggressive [MW] |  |  | 15.7312 | 15.9465 | 16.1741 | 16.4141 | 16.6572 | 16.5253 | 16.6455 | 16.7642 | 16.8813 | 17.0007 | 17.1213 | 17.2432 | 17.3645 | 17.4847 | 17.6021 | 17.7227 | 18.3172 | 18.9122
| GORESBRIDGE | 10 | 1 | Conservative [MW] |  |  | 3.2591 | 3.2816 | 3.3041 | 3.3267 | 3.3503 | 15.8034 | 15.8419 | 15.8817 | 15.9217 | 15.963 | 16.0058 | 16.0486 | 16.0943 | 16.1398 | 16.1855 | 16.234 | 16.4689 | 16.7042
|  |  |  | Best View [MW] |  |  | 3.2591 | 3.286 | 3.314 | 3.342 | 3.3711 | 15.8327 | 15.885 | 15.94 | 15.9966 | 16.0546 | 16.114 | 16.1764 | 16.24 | 16.3066 | 16.3746 | 16.4453 | 16.7914 | 17.1381
|  |  |  | Base Case [MW] |  |  | 3.2591 | 3.2915 | 3.3239 | 3.3585 | 3.3922 | 15.8634 | 15.9277 | 15.9935 | 16.0623 | 16.1338 | 16.2068 | 16.284 | 16.364 | 16.4466 | 16.5322 | 16.6219 | 17.0592 | 17.4973
|  |  |  | Aggressive [MW] |  |  | 3.2591 | 3.3127 | 3.3684 | 3.4265 | 3.4858 | 15.9981 | 16.082 | 16.1703 | 16.2627 | 16.3595 | 16.4603 | 16.5652 | 16.6755 | 16.7913 | 16.9127 | 17.0392 | 17.6581 | 18.2778
| GORT | 10 | 1 | Conservative [MW] |  |  | 5.8522 | 5.8726 | 5.8923 | 5.9112 | 5.9336 | 5.9552 | 5.9893 | 6.0257 | 6.0598 | 6.0958 | 6.1339 | 6.1694 | 6.2114 | 6.2507 | 6.2869 | 6.3294 | 6.5252 | 6.7221
|  |  |  | Best View [MW] |  |  | 5.8522 | 5.8825 | 5.9152 | 5.9461 | 5.9794 | 6.0151 | 6.0643 | 6.1133 | 6.1664 | 6.2188 | 6.2748 | 6.3345 | 6.3877 | 6.4489 | 6.508 | 6.5692 | 6.8697 | 7.1706
|  |  |  | Base Case [MW] |  |  | 5.8522 | 5.897 | 5.9424 | 5.9884 | 6.0346 | 6.0856 | 6.1404 | 6.1986 | 6.2549 | 6.3139 | 6.3752 | 6.4387 | 6.5035 | 6.5698 | 6.6368 | 6.7043 | 7.0405 | 7.3768
|  |  |  | Aggressive [MW] |  |  | 5.8522 | 5.9179 | 5.9878 | 6.0617 | 6.1388 | 6.2184 | 6.2838 | 6.3503 | 6.4174 | 6.4895 | 6.5609 | 6.6365 | 6.7102 | 6.7867 | 6.8651 | 6.9445 | 7.3387 | 7.7332
| GORTLEE | 10 | 1 | Conservative [MW] |  |  | 14.1401 | 14.1641 | 14.1876 | 14.2105 | 14.2371 | 14.2591 | 14.3169 | 14.3761 | 14.4363 | 14.4969 | 14.5587 | 14.6207 | 14.6835 | 14.7512 | 14.8188 | 14.8867 | 15.2254 | 15.5641
|  |  |  | Best View [MW] |  |  | 14.1401 | 14.1944 | 14.246 | 14.299 | 14.3536 | 14.4096 | 14.4921 | 14.5807 | 14.6706 | 14.7618 | 14.8535 | 14.9503 | 15.0467 | 15.1475 | 15.2517 | 15.3594 | 15.8886 | 16.4184
|  |  |  | Base Case [MW] |  |  | 14.1401 | 14.199 | 14.2589 | 14.3196 | 14.381 | 14.4428 | 14.5421 | 14.6443 | 14.7497 | 14.8614 | 14.9751 | 15.0895 | 15.2089 | 15.3326 | 15.455 | 15.5848 | 16.2142 | 16.8448
|  |  |  | Aggressive [MW] |  |  | 14.1401 | 14.2293 | 14.3192 | 14.4136 | 14.5082 | 14.6108 | 14.7302 | 14.8571 | 14.9867 | 15.122 | 15.2575 | 15.4012 | 15.548 | 15.7013 | 15.8545 | 16.0116 | 16.7867 | 17.5626
| GRAIGUE | 10 | 1 | Conservative [MW] |  |  | 12.9217 | 12.9677 | 13.0119 | 13.0584 | 13.103 | 13.0121 | 12.6878 | 12.3596 | 12.4339 | 12.508 | 12.5821 | 12.6595 | 12.7363 | 12.8162 | 12.8986 | 12.9805 | 13.3913 | 13.802
|  |  |  | Best View [MW] |  |  | 12.9217 | 12.9765 | 13.0325 | 13.086 | 13.1448 | 13.0671 | 12.7637 | 12.4647 | 12.5649 | 12.6686 | 12.7725 | 12.8794 | 12.989 | 13.1046 | 13.2186 | 13.3339 | 13.9071 | 14.4805
|  |  |  | Base Case [MW] |  |  | 12.9217 | 12.9886 | 13.0519 | 13.1195 | 13.1871 | 13.1213 | 12.838 | 12.5597 | 12.6812 | 12.8066 | 12.932 | 13.064 | 13.2017 | 13.3411 | 13.4814 | 13.6287 | 14.3465 | 15.0655
|  |  |  | Aggressive [MW] |  |  | 12.9217 | 13.029 | 13.142 | 13.2566 | 13.3719 | 13.358 | 13.1127 | 12.8699 | 13.0262 | 13.19 | 13.3604 | 13.5354 | 13.714 | 13.8978 | 14.0849 | 14.273 | 15.2106 | 16.1484
| GRAIGUENAMANAGH | 10 | 1 | Conservative [MW] |  |  | 2.3942 | 2.4049 | 2.4151 | 2.4294 | 2.443 | 2.4559 | 2.4712 | 2.4897 | 2.5066 | 2.5268 | 2.5452 | 2.5668 | 2.5864 | 2.6041 | 2.6248 | 2.6486 | 2.7592 | 2.8703
|  |  |  | Best View [MW] |  |  | 2.3942 | 2.4073 | 2.4243 | 2.4354 | 2.4504 | 2.4692 | 2.4938 | 2.5154 | 2.544 | 2.5692 | 2.5961 | 2.6193 | 2.649 | 2.6745 | 2.7063 | 2.7335 | 2.8817 | 3.0292
|  |  |  | Base Case [MW] |  |  | 2.3942 | 2.4094 | 2.4282 | 2.4455 | 2.4613 | 2.4805 | 2.5091 | 2.5384 | 2.5732 | 2.6032 | 2.6331 | 2.6679 | 2.702 | 2.7351 | 2.7667 | 2.8019 | 2.9685 | 3.1356
|  |  |  | Aggressive [MW] |  |  | 2.3942 | 2.4211 | 2.4491 | 2.4826 | 2.5119 | 2.5414 | 2.5785 | 2.6185 | 2.6557 | 2.7001 | 2.7405 | 2.7815 | 2.8222 | 2.8678 | 2.9056 | 2.9463 | 3.142 | 3.3383
| GRANAGH | 10 | 1 | Conservative [MW] |  |  | 3.1341 | 3.1684 | 3.2042 | 3.2411 | 3.2777 | 3.3153 | 3.3639 | 3.4132 | 3.4632 | 3.5139 | 3.5652 | 3.6186 | 3.6708 | 3.7251 | 3.7796 | 3.8342 | 4.1069 | 4.3796
|  |  |  | Best View [MW] |  |  | 3.1341 | 3.1722 | 3.2118 | 3.2525 | 3.2942 | 3.3354 | 3.3972 | 3.461 | 3.5247 | 3.59 | 3.6567 | 3.7246 | 3.7936 | 3.8654 | 3.936 | 4.007 | 4.3609 | 4.7149
|  |  |  | Base Case [MW] |  |  | 3.1341 | 3.18 | 3.2258 | 3.2739 | 3.3229 | 3.3726 | 3.445 | 3.5186 | 3.5949 | 3.6718 | 3.7511 | 3.8305 | 3.9134 | 3.9957 | 4.0789 | 4.1626 | 4.5795 | 4.9966
|  |  |  | Aggressive [MW] |  |  | 3.1341 | 3.2069 | 3.2815 | 3.3591 | 3.4376 | 3.5202 | 3.6102 | 3.7031 | 3.7987 | 3.8943 | 3.9933 | 4.0931 | 4.1949 | 4.2956 | 4.3962 | 4.4974 | 5.0018 | 5.5063
| GRANBY ROW | 10 | 1 | Conservative [MW] |  |  | 11.8802 | 11.9358 | 11.9939 | 12.0541 | 12.1144 | 12.1764 | 11.8404 | 11.8977 | 11.9577 | 12.0177 | 12.08 | 12.1425 | 12.2067 | 12.2729 | 12.3386 | 12.4077 | 12.7442 | 13.0812
|  |  |  | Best View [MW] |  |  | 11.8802 | 11.9457 | 12.0144 | 12.0838 | 12.1562 | 12.2301 | 11.8997 | 11.9656 | 12.0349 | 12.1033 | 12.1749 | 12.2453 | 12.3204 | 12.3958 | 12.4713 | 12.5508 | 12.9376 | 13.3251
|  |  |  | Base Case [MW] |  |  | 11.8802 | 11.9551 | 12.0354 | 12.1165 | 12.2027 | 12.2903 | 11.9681 | 12.041 | 12.1182 | 12.1955 | 12.2746 | 12.3553 | 12.4372 | 12.522 | 12.6075 | 12.6953 | 13.1284 | 13.5619
|  |  |  | Aggressive [MW] |  |  | 11.8802 | 12.009 | 12.1485 | 12.2942 | 12.4469 | 12.6096 | 12.2925 | 12.3703 | 12.4482 | 12.5294 | 12.6099 | 12.6934 | 12.7799 | 12.8667 | 12.9533 | 13.042 | 13.4798 | 13.918
| GRANGE (DR) | 10 | 1 | Conservative [MW] |  |  | 13.7131 | 13.8325 | 13.9557 | 14.0792 | 14.2059 | 13.357 | 13.4355 | 13.5096 | 13.5868 | 13.667 | 13.7422 | 13.8244 | 13.9049 | 13.9838 | 14.0649 | 14.148 | 14.558 | 14.9684
|  |  |  | Best View [MW] |  |  | 13.7131 | 13.8451 | 13.978 | 14.117 | 14.2603 | 13.4252 | 13.5123 | 13.601 | 13.6914 | 13.783 | 13.8757 | 13.9649 | 14.0588 | 14.1528 | 14.2464 | 14.3442 | 14.8222 | 15.3008
|  |  |  | Base Case [MW] |  |  | 13.7131 | 13.8604 | 14.0052 | 14.1569 | 14.3132 | 13.5005 | 13.5994 | 13.6979 | 13.7999 | 13.9051 | 14.009 | 14.1113 | 14.2193 | 14.325 | 14.4319 | 14.5395 | 15.0754 | 15.6115
|  |  |  | Aggressive [MW] |  |  | 13.7131 | 13.8911 | 14.0741 | 14.2616 | 14.4594 | 13.6857 | 13.7745 | 13.8681 | 13.9585 | 14.0537 | 14.1448 | 14.2398 | 14.3346 | 14.4286 | 14.5261 | 14.6218 | 15.105 | 15.5879
| GRANGE (SR) | 10 | 1 | Conservative [MW] |  |  | 6.4278 | 6.4544 | 6.4797 | 6.5035 | 6.5305 | 6.5606 | 6.5937 | 6.6334 | 6.6705 | 6.7049 | 6.7458 | 6.7839 | 6.8236 | 6.8649 | 6.9076 | 6.947 | 7.153 | 7.3584
|  |  |  | Best View [MW] |  |  | 6.4278 | 6.4572 | 6.4851 | 6.5156 | 6.5444 | 6.576 | 6.6211 | 6.6666 | 6.7123 | 6.7628 | 6.8131 | 6.8633 | 6.9175 | 6.9711 | 7.0283 | 7.0845 | 7.3683 | 7.6519
|  |  |  | Base Case [MW] |  |  | 6.4278 | 6.4593 | 6.4927 | 6.5282 | 6.5659 | 6.6013 | 6.6534 | 6.7092 | 6.7682 | 6.8256 | 6.8856 | 6.948 | 7.0079 | 7.074 | 7.1415 | 7.2097 | 7.549 | 7.8884
|  |  |  | Aggressive [MW] |  |  | 6.4278 | 6.4816 | 6.5343 | 6.5897 | 6.648 | 6.7085 | 6.7758 | 6.8477 | 6.9193 | 6.9947 | 7.0734 | 7.1497 | 7.2328 | 7.3167 | 7.4008 | 7.4891 | 7.9194 | 8.3504
| GREENHILLS | 10 | 1 | Conservative [MW] |  |  | 7.7818 | 7.8138 | 7.8477 | 7.8837 | 7.9194 | 7.9549 | 7.9883 | 8.0216 | 8.0572 | 8.0927 | 8.1281 | 8.1654 | 8.2025 | 8.2414 | 8.2797 | 8.3197 | 8.5152 | 8.711
|  |  |  | Best View [MW] |  |  | 7.7818 | 7.8199 | 7.8591 | 7.8993 | 7.943 | 7.9853 | 8.0235 | 8.0612 | 8.1005 | 8.1412 | 8.1832 | 8.2265 | 8.2687 | 8.3141 | 8.3581 | 8.4051 | 8.6323 | 8.8599
|  |  |  | Base Case [MW] |  |  | 7.7818 | 7.8264 | 7.8733 | 7.9203 | 7.9692 | 8.0199 | 8.0633 | 8.1057 | 8.149 | 8.1952 | 8.242 | 8.2894 | 8.3369 | 8.3869 | 8.4391 | 8.4909 | 8.7509 | 9.0108
|  |  |  | Aggressive [MW] |  |  | 7.7818 | 7.8567 | 7.939 | 8.0235 | 8.1133 | 8.2074 | 8.252 | 8.2972 | 8.3453 | 8.3918 | 8.4408 | 8.4901 | 8.5417 | 8.5931 | 8.6463 | 8.7013 | 8.9717 | 9.2424
| GREYSTONES | 10 | 1 | Conservative [MW] |  |  | 12.009 | 12.1074 | 12.2099 | 12.3117 | 12.417 | 12.5204 | 12.6041 | 12.6855 | 12.7688 | 12.8539 | 12.9411 | 13.0249 | 13.1098 | 13.1958 | 13.2877 | 13.3748 | 13.8228 | 14.2701
|  |  |  | Best View [MW] |  |  | 12.009 | 12.1239 | 12.2394 | 12.3602 | 12.4802 | 12.6041 | 12.7017 | 12.7987 | 12.8997 | 12.9993 | 13.0972 | 13.1977 | 13.3005 | 13.4053 | 13.506 | 13.6136 | 14.133 | 14.6535
|  |  |  | Base Case [MW] |  |  | 12.009 | 12.1392 | 12.2712 | 12.4046 | 12.5429 | 12.68 | 12.7931 | 12.9023 | 13.0127 | 13.128 | 13.2374 | 13.3563 | 13.4677 | 13.5874 | 13.7047 | 13.8176 | 14.3941 | 14.9697
|  |  |  | Aggressive [MW] |  |  | 12.009 | 12.1947 | 12.3872 | 12.5877 | 12.7933 | 13.005 | 13.1112 | 13.2191 | 13.3223 | 13.4306 | 13.5441 | 13.652 | 13.7639 | 13.8729 | 13.9784 | 14.0909 | 14.6348 | 15.1798
| GURRANEBANE | 20 | 1 | Conservative [MW] |  |  | 6.6875 | 6.7207 | 6.7513 | 6.7849 | 6.8159 | 6.4631 | 6.5086 | 6.5584 | 6.6126 | 6.6612 | 6.7136 | 6.7599 | 6.8147 | 6.8629 | 6.9139 | 6.9676 | 7.2288 | 7.4905
|  |  |  | Best View [MW] |  |  | 6.6875 | 6.7256 | 6.7653 | 6.8065 | 6.8442 | 6.4977 | 6.5681 | 6.6383 | 6.707 | 6.7742 | 6.8439 | 6.9157 | 6.9833 | 7.0568 | 7.1251 | 7.1865 | 7.5119 | 7.8361
|  |  |  | Base Case [MW] |  |  | 6.6875 | 6.7418 | 6.7991 | 6.8546 | 6.918 | 6.5881 | 6.6547 | 6.7247 | 6.7979 | 6.8686 | 6.9357 | 7.0037 | 7.0722 | 7.14 | 7.2061 | 7.2752 | 7.6127 | 7.9507
|  |  |  | Aggressive [MW] |  |  | 6.6875 | 6.767 | 6.8475 | 6.9336 | 7.0133 | 6.7128 | 6.7946 | 6.8796 | 6.961 | 7.0384 | 7.1204 | 7.1949 | 7.2713 | 7.3419 | 7.4099 | 7.4691 | 7.7887 | 8.1067
| GURTEEN | 10 | 1 | Conservative [MW] |  |  | 0.25953 | 0.26529 | 0.27117 | 0.27714 | 0.28317 | 0.28768 | 0.29942 | 0.31146 | 0.32379 | 0.33639 | 0.3493 | 0.36255 | 0.37609 | 0.39002 | 0.40425 | 0.41879 | 0.49066 | 0.56258
|  |  |  | Best View [MW] |  |  | 0.25953 | 0.26943 | 0.27959 | 0.28992 | 0.30056 | 0.30968 | 0.32599 | 0.34278 | 0.36015 | 0.37807 | 0.39653 | 0.41559 | 0.43521 | 0.45544 | 0.47629 | 0.49777 | 0.60349 | 0.70932
|  |  |  | Base Case [MW] |  |  | 0.25953 | 0.27263 | 0.28613 | 0.30002 | 0.31429 | 0.32727 | 0.3471 | 0.3677 | 0.38909 | 0.41124 | 0.43423 | 0.458 | 0.48265 | 0.50819 | 0.5346 | 0.56188 | 0.69595 | 0.83016
|  |  |  | Aggressive [MW] |  |  | 0.25953 | 0.27983 | 0.30103 | 0.32313 | 0.34625 | 0.36853 | 0.39593 | 0.42458 | 0.45455 | 0.48582 | 0.51861 | 0.55282 | 0.58856 | 0.6258 | 0.66468 | 0.70519 | 0.90341 | 1.1019
| GWEEDORE | 20 | 1 | Conservative [MW] |  |  | 3.9108 | 3.9185 | 3.9261 | 3.9335 | 3.9406 | 3.9476 | 3.9646 | 3.9828 | 4.002 | 4.02 | 4.0391 | 4.0591 | 4.0779 | 4.0976 | 4.1181 | 4.1395 | 4.2441 | 4.3489
|  |  |  | Best View [MW] |  |  | 3.9108 | 3.9262 | 3.9429 | 3.9588 | 3.9759 | 3.992 | 4.0179 | 4.0437 | 4.0715 | 4.099 | 4.126 | 4.1548 | 4.1852 | 4.2147 | 4.2456 | 4.2777 | 4.4349 | 4.5924
|  |  |  | Base Case [MW] |  |  | 3.9108 | 3.9277 | 3.9478 | 3.9667 | 3.9844 | 4.0052 | 4.0345 | 4.065 | 4.0988 | 4.131 | 4.1663 | 4.202 | 4.2378 | 4.2737 | 4.3116 | 4.3488 | 4.5367 | 4.7245
|  |  |  | Aggressive [MW] |  |  | 3.9108 | 3.9392 | 3.9671 | 3.9966 | 4.0252 | 4.0573 | 4.0946 | 4.1313 | 4.1719 | 4.2137 | 4.2564 | 4.2995 | 4.3426 | 4.3902 | 4.437 | 4.4847 | 4.7209 | 4.9573
| HARTNETTS CROSS | 20 | 2 | Conservative [MW] |  |  | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525
|  |  |  | Best View [MW] |  |  | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525
|  |  |  | Base Case [MW] |  |  | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525
|  |  |  | Aggressive [MW] |  |  | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525 | 6.0525
| HEADFORD | 10 | 1 | Conservative [MW] |  |  | 7.401 | 11.3008 | 11.3046 | 11.3076 | 11.3103 | 11.3187 | 11.3177 | 11.3169 | 11.3138 | 11.3105 | 11.3073 | 11.3013 | 11.2949 | 11.2853 | 11.275 | 11.2637 | 11.21 | 11.1561
|  |  |  | Best View [MW] |  |  | 7.401 | 11.3008 | 11.3036 | 11.3051 | 11.308 | 11.3133 | 11.3133 | 11.3087 | 11.3047 | 11.2983 | 11.2889 | 11.2763 | 11.2625 | 11.2445 | 11.2218 | 11.1961 | 11.0757 | 10.9548
|  |  |  | Base Case [MW] |  |  | 7.401 | 11.3016 | 11.3044 | 11.3047 | 11.308 | 11.3099 | 11.305 | 11.2993 | 11.2894 | 11.2774 | 11.2604 | 11.2397 | 11.2125 | 11.1801 | 11.1821 | 11.1805 | 11.1819 | 11.1828
|  |  |  | Aggressive [MW] |  |  | 7.401 | 11.3007 | 11.3004 | 11.298 | 11.2928 | 11.285 | 11.2691 | 11.2464 | 11.2159 | 11.1787 | 11.1516 | 11.1424 | 11.0118 | 10.8566 | 10.6688 | 10.4467 | 9.4275 | 8.4026
| HEADFORD ROAD | 10 | 1 | Conservative [MW] |  |  | 14.4087 | 14.4561 | 14.5013 | 14.5488 | 14.5985 | 14.6461 | 14.713 | 14.7802 | 14.8474 | 14.919 | 14.9899 | 15.0651 | 15.1396 | 15.2133 | 15.2903 | 15.3663 | 15.749 | 16.1315
|  |  |  | Best View [MW] |  |  | 14.4087 | 14.4694 | 14.527 | 14.5853 | 14.6446 | 14.709 | 14.8048 | 14.9003 | 15.0001 | 15.1034 | 15.2101 | 15.3146 | 15.4261 | 15.5395 | 15.654 | 15.7735 | 16.3576 | 16.9426
|  |  |  | Base Case [MW] |  |  | 14.4087 | 14.4832 | 14.5566 | 14.6332 | 14.7127 | 14.7909 | 14.8973 | 15.006 | 15.1207 | 15.2368 | 15.3533 | 15.4743 | 15.599 | 15.727 | 15.8568 | 15.9884 | 16.6416 | 17.2951
|  |  |  | Aggressive [MW] |  |  | 14.4087 | 14.5257 | 14.6427 | 14.7677 | 14.8954 | 15.0249 | 15.1543 | 15.29 | 15.4265 | 15.5671 | 15.711 | 15.8611 | 16.012 | 16.1724 | 16.3305 | 16.4944 | 17.2984 | 18.1034
| HOLYCROSS ROAD | 10 | 1 | Conservative [MW] |  |  | 6.053 | 18.6533 | 18.6954 | 18.7396 | 18.786 | 18.8311 | 18.8922 | 18.9544 | 19.0209 | 19.0852 | 19.1539 | 19.2233 | 19.2938 | 19.3649 | 19.4367 | 19.5126 | 19.8812 | 20.2505
|  |  |  | Best View [MW] |  |  | 6.053 | 18.6619 | 18.7154 | 18.7672 | 18.8238 | 18.8788 | 18.9692 | 19.0651 | 19.1594 | 19.2586 | 19.3629 | 19.4686 | 19.5749 | 19.6889 | 19.8031 | 19.9213 | 20.5015 | 21.0824
|  |  |  | Base Case [MW] |  |  | 6.053 | 18.68 | 18.7501 | 18.8238 | 18.8978 | 18.9753 | 19.0762 | 19.1785 | 19.2848 | 19.3954 | 19.5063 | 19.6242 | 19.7453 | 19.8727 | 19.9991 | 20.1348 | 20.7884 | 21.4435
|  |  |  | Aggressive [MW] |  |  | 6.053 | 18.7198 | 18.8326 | 18.9508 | 19.0747 | 19.2037 | 19.3171 | 19.4342 | 19.5541 | 19.6801 | 19.8078 | 19.9448 | 20.083 | 20.2253 | 20.3753 | 20.5246 | 21.273 | 22.0213
| HOWTH JUNCTION | 10 | 1 | Conservative [MW] |  |  | 12.9373 | 13.0147 | 13.0982 | 13.1834 | 13.27 | 13.357 | 13.4124 | 13.465 | 13.5193 | 13.5708 | 13.6282 | 13.6825 | 13.7426 | 13.7997 | 13.8622 | 13.9212 | 14.2256 | 14.5294
|  |  |  | Best View [MW] |  |  | 12.9373 | 13.0236 | 13.114 | 13.2094 | 13.3042 | 13.4059 | 13.4678 | 13.5304 | 13.5896 | 13.6535 | 13.7221 | 13.7866 | 13.8556 | 13.9248 | 13.9939 | 14.0674 | 14.4231 | 14.7795
|  |  |  | Base Case [MW] |  |  | 12.9373 | 13.0314 | 13.1321 | 13.2358 | 13.3457 | 13.4558 | 13.5238 | 13.5959 | 13.6675 | 13.7429 | 13.8175 | 13.8954 | 13.9721 | 14.0516 | 14.1341 | 14.2148 | 14.623 | 15.0309
|  |  |  | Aggressive [MW] |  |  | 12.9373 | 13.0543 | 13.1773 | 13.3105 | 13.4439 | 13.5881 | 13.6479 | 13.7175 | 13.7827 | 13.8481 | 13.9179 | 13.9876 | 14.0572 | 14.1309 | 14.204 | 14.2811 | 14.6561 | 15.0318
| INCH | 20 | 1 | Conservative [MW] |  |  | 6.1527 | 6.1646 | 6.1722 | 6.1835 | 6.1906 | 6.2016 | 6.2211 | 6.2398 | 6.2615 | 6.2823 | 6.3023 | 6.3251 | 6.3471 | 6.3679 | 6.3917 | 6.4144 | 6.5309 | 6.6471
|  |  |  | Best View [MW] |  |  | 6.1527 | 6.1721 | 6.1867 | 6.2046 | 6.2256 | 6.242 | 6.2698 | 6.2961 | 6.3208 | 6.3479 | 6.3772 | 6.4088 | 6.4385 | 6.4704 | 6.5043 | 6.536 | 6.7006 | 6.8648
|  |  |  | Base Case [MW] |  |  | 6.1527 | 6.1726 | 6.1914 | 6.2135 | 6.2345 | 6.2544 | 6.2823 | 6.3124 | 6.3405 | 6.3707 | 6.4029 | 6.437 | 6.4689 | 6.5025 | 6.5376 | 6.5744 | 6.7539 | 6.9337
|  |  |  | Aggressive [MW] |  |  | 6.1527 | 6.1823 | 6.2137 | 6.2466 | 6.2811 | 6.3129 | 6.3493 | 6.3869 | 6.4294 | 6.4685 | 6.5125 | 6.5569 | 6.6014 | 6.6459 | 6.6944 | 6.7467 | 6.9979 | 7.2498
| INCHICORE | 10 | 1 | Conservative [MW] |  |  | 7.641 | 7.681 | 7.7242 | 7.7661 | 7.8106 | 7.8577 | 7.8828 | 7.9109 | 7.9375 | 7.967 | 7.9952 | 8.0241 | 8.0536 | 8.0835 | 8.1143 | 8.1454 | 8.3 | 8.4546
|  |  |  | Best View [MW] |  |  | 7.641 | 7.6854 | 7.732 | 7.7808 | 7.8293 | 7.8817 | 7.9121 | 7.9429 | 7.9761 | 8.0096 | 8.0411 | 8.0772 | 8.1111 | 8.1472 | 8.1833 | 8.2192 | 8.3992 | 8.5792
|  |  |  | Base Case [MW] |  |  | 7.641 | 7.6891 | 7.7408 | 7.7937 | 7.8497 | 7.9062 | 7.9418 | 7.9793 | 8.0144 | 8.0536 | 8.0923 | 8.1305 | 8.1703 | 8.2117 | 8.2545 | 8.2962 | 8.5076 | 8.7188
|  |  |  | Aggressive [MW] |  |  | 7.641 | 7.7005 | 7.7652 | 7.8305 | 7.9001 | 7.9733 | 8.0049 | 8.0389 | 8.073 | 8.1073 | 8.1437 | 8.1803 | 8.2167 | 8.2527 | 8.2908 | 8.3286 | 8.5186 | 8.7085
|  |  | 2 | Conservative [MW] |  |  | 13.4282 | 13.4471 | 13.4626 | 13.4769 | 13.3321 | 13.4465 | 13.4655 | 13.5029 | 13.5434 | 13.5806 | 13.6206 | 13.6604 | 13.6994 | 13.741 | 13.7816 | 13.8213 | 14.0223 | 14.2232
|  |  |  | Best View [MW] |  |  | 13.4282 | 13.448 | 13.4679 | 13.4814 | 13.3355 | 13.4644 | 13.5055 | 13.5489 | 13.5914 | 13.6359 | 13.6788 | 13.7232 | 13.7695 | 13.8137 | 13.8591 | 13.9088 | 14.146 | 14.3838
|  |  |  | Base Case [MW] |  |  | 13.4282 | 13.4522 | 13.4727 | 13.4905 | 13.34 | 13.5035 | 13.5489 | 13.5956 | 13.6434 | 13.6925 | 13.7419 | 13.7886 | 13.8392 | 13.8902 | 13.9422 | 13.998 | 14.2666 | 14.5359
|  |  |  | Aggressive [MW] |  |  | 13.4282 | 13.4668 | 13.4947 | 13.5152 | 13.3446 | 13.7063 | 13.7525 | 13.7998 | 13.8443 | 13.8944 | 13.9453 | 14.0001 | 14.0519 | 14.1041 | 14.16 | 14.2118 | 14.4819 | 14.7512
| JENKINSTOWN | 20 | 1 | Conservative [MW] |  |  | 6.2247 | 6.2498 | 6.2777 | 6.3083 | 6.3373 | 6.3647 | 6.3992 | 6.4317 | 6.4622 | 6.4993 | 6.5342 | 6.5666 | 6.6056 | 6.6421 | 6.6805 | 6.7162 | 6.9019 | 7.0872
|  |  |  | Best View [MW] |  |  | 6.2247 | 6.2519 | 6.286 | 6.3182 | 6.3483 | 6.3807 | 6.4267 | 6.4731 | 6.5197 | 6.5665 | 6.6177 | 6.6686 | 6.7236 | 6.7777 | 6.8307 | 6.8871 | 7.16 | 7.4335
|  |  |  | Base Case [MW] |  |  | 6.2247 | 6.2663 | 6.3126 | 6.359 | 6.4097 | 6.4602 | 6.5125 | 6.5639 | 6.623 | 6.6805 | 6.7408 | 6.7987 | 6.8632 | 6.9293 | 6.992 | 7.0603 | 7.3866 | 7.7139
|  |  |  | Aggressive [MW] |  |  | 6.2247 | 6.2849 | 6.3465 | 6.4132 | 6.48 | 6.5509 | 6.6165 | 6.6829 | 6.7497 | 6.8209 | 6.8959 | 6.9743 | 7.0506 | 7.1338 | 7.2182 | 7.303 | 7.7258 | 8.1487
| JOHNSTOWN | 10 | 1 | Conservative [MW] |  |  | 14.6267 | 14.7329 | 14.8367 | 14.9478 | 15.0558 | 15.1694 | 15.2558 | 15.3416 | 15.4284 | 15.5163 | 15.6043 | 15.6922 | 15.7804 | 15.8728 | 15.9594 | 16.0495 | 16.4906 | 16.9322
|  |  |  | Best View [MW] |  |  | 14.6267 | 14.7477 | 14.8721 | 14.9995 | 15.1284 | 15.2586 | 15.3556 | 15.4586 | 15.5643 | 15.6663 | 15.7698 | 15.8737 | 15.9777 | 16.0812 | 16.1886 | 16.2888 | 16.8089 | 17.3277
|  |  |  | Base Case [MW] |  |  | 14.6267 | 14.7618 | 14.9012 | 15.0486 | 15.1929 | 15.3371 | 15.4523 | 15.5651 | 15.6811 | 15.8001 | 15.9157 | 16.0328 | 16.1493 | 16.2653 | 16.3794 | 16.4901 | 17.0525 | 17.6144
|  |  |  | Aggressive [MW] |  |  | 14.6267 | 14.8269 | 15.0326 | 15.2404 | 15.4549 | 15.672 | 15.7828 | 15.8903 | 16.0014 | 16.1095 | 16.2202 | 16.3314 | 16.4374 | 16.5421 | 16.6454 | 16.7447 | 17.2517 | 17.7581
| JULIANSTOWN | 20 | 1 | Conservative [MW] |  |  | 5.4863 | 5.5289 | 5.5768 | 5.6243 | 5.6713 | 5.7175 | 5.1986 | 4.2891 | 4.3521 | 4.4142 | 4.4747 | 4.5375 | 4.5936 | 4.655 | 4.7082 | 4.7613 | 5.0271 | 5.2928
|  |  |  | Best View [MW] |  |  | 5.4863 | 5.5412 | 5.5937 | 5.649 | 5.7011 | 5.7552 | 5.2561 | 4.3656 | 4.4401 | 4.5196 | 4.591 | 4.6652 | 4.7331 | 4.7969 | 4.8548 | 4.9092 | 5.1905 | 5.4712
|  |  |  | Base Case [MW] |  |  | 5.4863 | 5.5625 | 5.6394 | 5.7163 | 5.7915 | 5.8647 | 5.3773 | 4.5032 | 4.5927 | 4.674 | 4.7539 | 4.8296 | 4.8928 | 4.944 | 4.9836 | 4.9995 | 5.1423 | 5.2812
|  |  |  | Aggressive [MW] |  |  | 5.4863 | 5.5884 | 5.6885 | 5.7955 | 5.8956 | 5.9974 | 5.5324 | 4.6807 | 4.7818 | 4.8669 | 4.9423 | 4.9885 | 5.0028 | 4.9652 | 4.8504 | 4.5851 | 3.6599 | 2.7096
| KANTURK | 10 | 1 | Conservative [MW] |  |  | 2.0657 | 8.6079 | 8.6588 | 8.711 | 8.7627 | 8.8155 | 8.8946 | 8.9743 | 9.0546 | 9.1369 | 9.2214 | 9.3062 | 9.3928 | 9.4813 | 9.5698 | 9.6599 | 10.106 | 10.5524
|  |  |  | Best View [MW] |  |  | 2.0657 | 8.6201 | 8.6815 | 8.7455 | 8.8105 | 8.8748 | 8.9846 | 9.0973 | 9.211 | 9.3288 | 9.4489 | 9.5709 | 9.6967 | 9.8237 | 9.9536 | 10.0863 | 10.7425 | 11.3991
|  |  |  | Base Case [MW] |  |  | 2.0657 | 8.6455 | 8.7348 | 8.8276 | 8.9207 | 9.0156 | 9.1292 | 9.2455 | 9.3642 | 9.485 | 9.6078 | 9.734 | 9.8634 | 9.9938 | 10.1266 | 10.2614 | 10.9299 | 11.5987
|  |  |  | Aggressive [MW] |  |  | 2.0657 | 8.6828 | 8.8131 | 8.9471 | 9.0845 | 9.225 | 9.3627 | 9.5033 | 9.6481 | 9.7969 | 9.9468 | 10.1016 | 10.2585 | 10.4188 | 10.582 | 10.7445 | 11.5588 | 12.373
| KELLS | 10 | 1 | Conservative [MW] |  |  | 6.3146 | 6.3317 | 6.3479 | 6.3637 | 6.383 | 6.4018 | 6.4363 | 6.4766 | 6.514 | 6.557 | 6.5967 | 6.6375 | 6.6836 | 6.7259 | 6.7733 | 6.8211 | 7.059 | 7.2969
|  |  |  | Best View [MW] |  |  | 6.3146 | 6.3343 | 6.3572 | 6.3789 | 6.404 | 6.4278 | 6.4708 | 6.5143 | 6.5625 | 6.6064 | 6.6593 | 6.7074 | 6.7596 | 6.811 | 6.866 | 6.9243 | 7.2068 | 7.4899
|  |  |  | Base Case [MW] |  |  | 6.3146 | 6.3567 | 6.3991 | 6.4462 | 6.4932 | 6.5402 | 6.5872 | 6.6384 | 6.6891 | 6.7437 | 6.7973 | 6.8542 | 6.9097 | 6.9723 | 7.0328 | 7.0954 | 7.4028 | 7.7105
|  |  |  | Aggressive [MW] |  |  | 6.3146 | 6.3701 | 6.4351 | 6.5007 | 6.5664 | 6.636 | 6.6967 | 6.7596 | 6.8197 | 6.886 | 6.9532 | 7.021 | 7.0934 | 7.1652 | 7.2406 | 7.319 | 7.7029 | 8.0873
| KENMARE | 10 | 1 | Conservative [MW] |  |  | 3.8744 | 3.8848 | 3.8949 | 3.9066 | 3.9158 | 3.9267 | 3.9434 | 3.9612 | 3.9781 | 3.9939 | 4.013 | 4.031 | 4.0501 | 4.0679 | 4.0866 | 4.1064 | 4.2026 | 4.2989
|  |  |  | Best View [MW] |  |  | 3.8744 | 3.8864 | 3.9 | 3.9129 | 3.9252 | 3.939 | 3.9628 | 3.9868 | 4.011 | 4.0353 | 4.0618 | 4.0859 | 4.1144 | 4.1402 | 4.1703 | 4.1973 | 4.3405 | 4.4831
|  |  |  | Base Case [MW] |  |  | 3.8744 | 3.8922 | 3.9109 | 3.9304 | 3.9486 | 3.9698 | 3.9932 | 4.0167 | 4.0425 | 4.0682 | 4.0938 | 4.1214 | 4.1486 | 4.1776 | 4.206 | 4.2361 | 4.3818 | 4.5278
|  |  |  | Aggressive [MW] |  |  | 3.8744 | 3.8994 | 3.926 | 3.9544 | 3.9841 | 4.0131 | 4.0428 | 4.0717 | 4.1042 | 4.1354 | 4.1675 | 4.2003 | 4.2361 | 4.2723 | 4.3086 | 4.3448 | 4.5261 | 4.7073
|  | 20 | 1 | Conservative [MW] |  |  | 4.1093 | 4.1226 | 4.1353 | 4.1475 | 4.1612 | 4.1744 | 4.1923 | 4.2135 | 4.2332 | 4.2538 | 4.2728 | 4.2949 | 4.3154 | 4.339 | 4.3607 | 4.383 | 4.4931 | 4.6032
|  |  |  | Best View [MW] |  |  | 4.1093 | 4.125 | 4.1399 | 4.1561 | 4.1715 | 4.1882 | 4.2159 | 4.2431 | 4.2722 | 4.3006 | 4.3307 | 4.3598 | 4.3926 | 4.4241 | 4.4541 | 4.4875 | 4.6455 | 4.8041
|  |  |  | Base Case [MW] |  |  | 4.1093 | 4.132 | 4.1531 | 4.1768 | 4.1987 | 4.2232 | 4.2519 | 4.28 | 4.3098 | 4.3387 | 4.3691 | 4.4006 | 4.4333 | 4.4645 | 4.4989 | 4.5316 | 4.6996 | 4.8674
|  |  |  | Aggressive [MW] |  |  | 4.1093 | 4.1412 | 4.1719 | 4.2056 | 4.2399 | 4.2745 | 4.3079 | 4.344 | 4.3804 | 4.4167 | 4.4526 | 4.4928 | 4.5323 | 4.5707 | 4.6127 | 4.6526 | 4.8575 | 5.0621
| KILBARRY | 10 | 1 | Conservative [MW] |  |  | 21.3374 | 21.4411 | 21.5468 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72
|  |  |  | Best View [MW] |  |  | 21.3374 | 21.4494 | 21.5636 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72
|  |  |  | Base Case [MW] |  |  | 21.3374 | 21.4907 | 21.6482 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72
|  |  |  | Aggressive [MW] |  |  | 21.3374 | 21.5483 | 21.7673 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72 | 16.72
| KILCAR | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.0046801 | 0.015834 | 0.027784
| KILCARAGH | 20 | 1 | Conservative [MW] |  |  | 2.7131 | 2.7462 | 2.7803 | 2.8142 | 2.8493 | 2.8842 | 2.929 | 2.9748 | 3.0229 | 3.0703 | 3.1185 | 3.1674 | 3.2187 | 3.2689 | 3.3213 | 3.3724 | 3.6316 | 3.8906
|  |  |  | Best View [MW] |  |  | 2.7131 | 2.7501 | 2.7868 | 2.8246 | 2.8636 | 2.9021 | 2.9595 | 3.0189 | 3.0802 | 3.1418 | 3.2052 | 3.2703 | 3.3351 | 3.4013 | 3.4706 | 3.5391 | 3.8836 | 4.2279
|  |  |  | Base Case [MW] |  |  | 2.7131 | 2.7567 | 2.7999 | 2.8454 | 2.8906 | 2.9367 | 3.0052 | 3.0753 | 3.147 | 3.2199 | 3.2938 | 3.3703 | 3.4491 | 3.5282 | 3.6091 | 3.6894 | 4.0925 | 4.4956
|  |  |  | Aggressive [MW] |  |  | 2.7131 | 2.7816 | 2.8519 | 2.9239 | 2.999 | 3.0753 | 3.1601 | 3.2486 | 3.3387 | 3.4318 | 3.5256 | 3.6234 | 3.7206 | 3.8206 | 3.9205 | 4.0217 | 4.5242 | 5.0269
| KILCLOHER | 10 | 1 | Conservative [MW] |  |  | 3.8066 | 3.8216 | 3.8378 | 3.8553 | 3.8719 | 3.8877 | 3.9092 | 3.9332 | 3.9556 | 3.9785 | 4.0018 | 4.0253 | 4.0514 | 4.0754 | 4.1018 | 4.126 | 4.2529 | 4.3794
|  |  |  | Best View [MW] |  |  | 3.8066 | 3.8253 | 3.843 | 3.8616 | 3.8792 | 3.8979 | 3.9283 | 3.9599 | 3.9927 | 4.0242 | 4.0588 | 4.0917 | 4.1274 | 4.1633 | 4.1992 | 4.2349 | 4.4142 | 4.5933
|  |  |  | Base Case [MW] |  |  | 3.8066 | 3.8292 | 3.8542 | 3.8794 | 3.9028 | 3.9284 | 3.9641 | 3.9981 | 4.0346 | 4.0691 | 4.1078 | 4.144 | 4.184 | 4.2232 | 4.2633 | 4.3018 | 4.4986 | 4.6952
|  |  |  | Aggressive [MW] |  |  | 3.8066 | 3.8434 | 3.8821 | 3.9203 | 3.96 | 4.0008 | 4.0413 | 4.083 | 4.1234 | 4.1666 | 4.21 | 4.2532 | 4.2981 | 4.3441 | 4.3883 | 4.4351 | 4.6622 | 4.8896
| KILCOCK | 20 | 1 | Conservative [MW] |  |  | 11.8858 | 11.9941 | 12.1047 | 12.2171 | 12.3349 | 12.0578 | 11.3434 | 11.4128 | 11.4861 | 11.5557 | 11.6289 | 11.7056 | 11.7782 | 11.8539 | 11.9329 | 12.0111 | 12.4043 | 12.7973
|  |  |  | Best View [MW] |  |  | 11.8858 | 12.0025 | 12.1278 | 12.2519 | 12.3835 | 12.1212 | 11.4169 | 11.4982 | 11.5821 | 11.6684 | 11.7531 | 11.8397 | 11.9282 | 12.0142 | 12.106 | 12.1948 | 12.6466 | 13.098
|  |  |  | Base Case [MW] |  |  | 11.8858 | 12.0135 | 12.1516 | 12.2898 | 12.4322 | 12.1862 | 11.4949 | 11.5872 | 11.6844 | 11.7785 | 11.8768 | 11.9751 | 12.0777 | 12.1798 | 12.2809 | 12.389 | 12.9108 | 13.4338
|  |  |  | Aggressive [MW] |  |  | 11.8858 | 12.0472 | 12.2103 | 12.3866 | 12.5657 | 12.3586 | 11.6611 | 11.7463 | 11.8301 | 11.9195 | 12.0064 | 12.0953 | 12.1893 | 12.2803 | 12.3722 | 12.4643 | 12.9243 | 13.3843
| KILCOLGAN | 10 | 1 | Conservative [MW] |  |  | 3.7425 | 3.7496 | 3.7566 | 3.7634 | 3.77 | 3.7763 | 3.7872 | 3.7976 | 3.8095 | 3.8209 | 3.8337 | 3.8459 | 3.8575 | 3.8707 | 3.883 | 3.897 | 3.9624 | 4.0281
|  |  |  | Best View [MW] |  |  | 3.7425 | 3.7536 | 3.7622 | 3.7724 | 3.7842 | 3.7955 | 3.8115 | 3.8264 | 3.8443 | 3.861 | 3.8807 | 3.899 | 3.9181 | 3.9378 | 3.9583 | 3.9793 | 4.0827 | 4.1862
|  |  |  | Base Case [MW] |  |  | 3.7425 | 3.7566 | 3.7717 | 3.786 | 3.8014 | 3.8178 | 3.8361 | 3.8529 | 3.8725 | 3.8927 | 3.9134 | 3.9347 | 3.9563 | 3.9783 | 4.0026 | 4.025 | 4.142 | 4.2588
|  |  |  | Aggressive [MW] |  |  | 3.7425 | 3.7637 | 3.7869 | 3.8099 | 3.8346 | 3.861 | 3.8825 | 3.9043 | 3.9262 | 3.9503 | 3.9765 | 4.0004 | 4.0262 | 4.0538 | 4.083 | 4.1115 | 4.2559 | 4.4001
|  | 20 | 1 | Conservative [MW] |  |  | 4.4029 | 4.4175 | 4.4313 | 4.4467 | 4.4613 | 4.475 | 4.5005 | 4.5261 | 4.5516 | 4.5744 | 4.6021 | 4.627 | 4.6515 | 4.6781 | 4.704 | 4.7318 | 4.8659 | 5.0003
|  |  |  | Best View [MW] |  |  | 4.4029 | 4.4259 | 4.4469 | 4.4708 | 4.495 | 4.5169 | 4.5524 | 4.5877 | 4.6251 | 4.6594 | 4.6954 | 4.7327 | 4.7711 | 4.8075 | 4.8441 | 4.8801 | 5.0619 | 5.2436
|  |  |  | Base Case [MW] |  |  | 4.4029 | 4.4349 | 4.4655 | 4.4991 | 4.5333 | 4.5679 | 4.6056 | 4.6445 | 4.6844 | 4.722 | 4.7623 | 4.8022 | 4.8412 | 4.881 | 4.9185 | 4.9559 | 5.1431 | 5.3304
|  |  |  | Aggressive [MW] |  |  | 4.4029 | 4.4507 | 4.5014 | 4.5517 | 4.6035 | 4.6582 | 4.7018 | 4.7438 | 4.7895 | 4.8325 | 4.8744 | 4.9174 | 4.9579 | 4.9947 | 5.0334 | 5.0658 | 5.2446 | 5.4224
| KILCOOLE | 10 | 1 | Conservative [MW] |  |  | 12.3557 | 12.4089 | 12.4666 | 12.5251 | 12.5843 | 12.6477 | 12.6954 | 12.745 | 12.7964 | 12.8448 | 12.8952 | 12.9515 | 13.0047 | 13.0594 | 13.1155 | 13.1728 | 13.4562 | 13.7399
|  |  |  | Best View [MW] |  |  | 12.3557 | 12.4171 | 12.4864 | 12.555 | 12.6227 | 12.698 | 12.7518 | 12.8108 | 12.8704 | 12.9348 | 12.9956 | 13.0609 | 13.1264 | 13.1922 | 13.2619 | 13.3317 | 13.6803 | 14.0289
|  |  |  | Base Case [MW] |  |  | 12.3557 | 12.4267 | 12.5005 | 12.5803 | 12.6582 | 12.7416 | 12.8083 | 12.8746 | 12.9406 | 13.0147 | 13.084 | 13.1607 | 13.2365 | 13.3112 | 13.3928 | 13.4729 | 13.8773 | 14.2816
|  |  |  | Aggressive [MW] |  |  | 12.3557 | 12.4594 | 12.5716 | 12.687 | 12.809 | 12.9365 | 13.0028 | 13.0687 | 13.1384 | 13.2123 | 13.2813 | 13.3581 | 13.4341 | 13.5088 | 13.5868 | 13.6677 | 14.0645 | 14.4619
| KILCULLEN | 10 | 1 | Conservative [MW] |  |  | 6.1379 | 6.1526 | 6.1707 | 6.1843 | 6.2014 | 6.2139 | 6.2389 | 6.2627 | 6.2853 | 6.3108 | 6.335 | 6.3578 | 6.3833 | 6.4116 | 6.4384 | 6.4678 | 6.608 | 6.7486
|  |  |  | Best View [MW] |  |  | 6.1379 | 6.1589 | 6.175 | 6.1942 | 6.2127 | 6.2345 | 6.2635 | 6.2947 | 6.3239 | 6.355 | 6.3881 | 6.423 | 6.4596 | 6.4935 | 6.5291 | 6.5703 | 6.7614 | 6.9535
|  |  |  | Base Case [MW] |  |  | 6.1379 | 6.1598 | 6.1847 | 6.2082 | 6.2305 | 6.2556 | 6.2899 | 6.3295 | 6.3661 | 6.4039 | 6.4467 | 6.4859 | 6.5299 | 6.5743 | 6.6231 | 6.672 | 6.9164 | 7.1608
|  |  |  | Aggressive [MW] |  |  | 6.1379 | 6.1737 | 6.2107 | 6.2484 | 6.2869 | 6.3299 | 6.3788 | 6.4306 | 6.4853 | 6.5381 | 6.597 | 6.6576 | 6.7238 | 6.7906 | 6.8575 | 6.9285 | 7.2724 | 7.617
|  | 20 | 1 | Conservative [MW] |  |  | 7.5036 | 7.5204 | 7.5366 | 7.5541 | 7.571 | 7.5893 | 7.6162 | 7.6418 | 7.668 | 7.6947 | 7.7241 | 7.752 | 7.7823 | 7.811 | 7.842 | 7.8734 | 8.0292 | 8.1851
|  |  |  | Best View [MW] |  |  | 7.5036 | 7.5238 | 7.545 | 7.5654 | 7.5887 | 7.611 | 7.6442 | 7.677 | 7.7138 | 7.748 | 7.7858 | 7.8251 | 7.8636 | 7.9054 | 7.9462 | 7.99 | 8.2009 | 8.4124
|  |  |  | Base Case [MW] |  |  | 7.5036 | 7.5278 | 7.5546 | 7.5799 | 7.6078 | 7.636 | 7.6748 | 7.7163 | 7.7606 | 7.8031 | 7.8503 | 7.8978 | 7.945 | 7.9962 | 8.049 | 8.1032 | 8.3704 | 8.6378
|  |  |  | Aggressive [MW] |  |  | 7.5036 | 7.5423 | 7.5834 | 7.627 | 7.6726 | 7.7183 | 7.7735 | 7.8329 | 7.8921 | 7.9547 | 8.0203 | 8.0906 | 8.1609 | 8.2348 | 8.3117 | 8.3931 | 8.7882 | 9.1841
| KILDARE | 10 | 1 | Conservative [MW] |  |  | 18.7814 | 18.8591 | 18.9324 | 19.0111 | 19.0897 | 19.1693 | 19.274 | 19.3761 | 19.484 | 19.5939 | 19.7042 | 19.8205 | 19.9324 | 20.054 | 20.1751 | 20.2961 | 20.9014 | 21.5066
|  |  |  | Best View [MW] |  |  | 18.7814 | 18.8768 | 18.9745 | 19.0702 | 19.1726 | 19.2778 | 19.4129 | 19.5534 | 19.6947 | 19.8447 | 19.994 | 20.1513 | 20.306 | 20.4676 | 20.6345 | 20.8064 | 21.6526 | 22.4996
|  |  |  | Base Case [MW] |  |  | 18.7814 | 18.8938 | 19.0107 | 19.1271 | 19.2519 | 19.3761 | 19.5343 | 19.7019 | 19.8739 | 20.0491 | 20.2313 | 20.4149 | 20.6077 | 20.8039 | 21.002 | 21.2103 | 22.2248 | 23.241
|  |  |  | Aggressive [MW] |  |  | 18.7814 | 18.9276 | 19.0767 | 19.2329 | 19.3904 | 19.5579 | 19.7561 | 19.9592 | 20.1755 | 20.3931 | 20.6245 | 20.8578 | 21.0961 | 21.3464 | 21.6014 | 21.8565 | 23.1317 | 24.407
|  | 20 | 1 | Conservative [MW] |  |  | 2.2604 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2607 | 2.2607 | 2.2607 | 2.2607 | 2.2607
|  |  |  | Best View [MW] |  |  | 2.2604 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2607 | 2.2607 | 2.2607 | 2.2607 | 2.2607 | 2.2607 | 2.2607 | 2.2607
|  |  |  | Base Case [MW] |  |  | 2.2604 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2606 | 2.2607 | 2.2607 | 2.2607 | 2.2607 | 2.2607 | 2.261 | 2.2611 | 2.2622 | 2.2632
|  |  |  | Aggressive [MW] |  |  | 2.2604 | 2.2606 | 2.2606 | 2.2606 | 2.2607 | 2.2606 | 2.2606 | 2.2607 | 2.2607 | 2.2607 | 2.2607 | 2.2609 | 2.261 | 2.2613 | 2.2618 | 2.262 | 2.2638 | 2.2655
| KILFLYNN | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | 0.0038389 | 0.0089322 | 0.01407 | 0.019262 | 0.029073 | 0.039137 | 0.049449 | 0.060006 | 0.07081 | 0.081872 | 0.093182 | 0.10476 | 0.11663 | 0.12874 | 0.18868 | 0.24865
|  |  |  | Best View [MW] |  |  | -0.0001 | 0.0026842 | 0.01162 | 0.020752 | 0.030136 | 0.039717 | 0.053008 | 0.066665 | 0.080767 | 0.095313 | 0.11027 | 0.12569 | 0.14158 | 0.15792 | 0.17478 | 0.19212 | 0.27755 | 0.36306
|  |  |  | Base Case [MW] |  |  | -0.0001 | 0.0037434 | 0.013831 | 0.024122 | 0.034707 | 0.045586 | 0.060054 | 0.074968 | 0.090374 | 0.1063 | 0.12273 | 0.13972 | 0.15719 | 0.17528 | 0.19392 | 0.21314 | 0.30771 | 0.40237
|  |  |  | Aggressive [MW] |  |  | -0.0001 | 0.009314 | 0.025273 | 0.041933 | 0.059235 | 0.07719 | 0.096039 | 0.11571 | 0.13608 | 0.15728 | 0.17931 | 0.20217 | 0.22595 | 0.25059 | 0.27612 | 0.30258 | 0.43242 | 0.56241
| KILGARVAN | 20 | 1 | Conservative [MW] |  |  | 3.3191 | 3.3293 | 3.3384 | 3.3484 | 3.3583 | 3.3692 | 3.3839 | 3.3994 | 3.4146 | 3.4307 | 3.4476 | 3.4641 | 3.4814 | 3.4983 | 3.5172 | 3.5344 | 3.6252 | 3.7156
|  |  |  | Best View [MW] |  |  | 3.3191 | 3.3315 | 3.3426 | 3.3558 | 3.3677 | 3.3804 | 3.4015 | 3.4232 | 3.4453 | 3.4692 | 3.4923 | 3.517 | 3.5421 | 3.5675 | 3.5945 | 3.6216 | 3.7569 | 3.8922
|  |  |  | Base Case [MW] |  |  | 3.3191 | 3.3365 | 3.3535 | 3.3713 | 3.3887 | 3.4079 | 3.4294 | 3.4525 | 3.4761 | 3.5001 | 3.5246 | 3.5494 | 3.5758 | 3.6024 | 3.6291 | 3.6574 | 3.7946 | 3.9322
|  |  |  | Aggressive [MW] |  |  | 3.3191 | 3.3436 | 3.3684 | 3.3936 | 3.4213 | 3.4481 | 3.475 | 3.5033 | 3.5316 | 3.5625 | 3.592 | 3.6239 | 3.6569 | 3.6908 | 3.7241 | 3.7596 | 3.9312 | 4.1031
| KILKEE | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.006828 | 0.040458 | 0.1374 | 0.2388
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.016166 | 0.052807 | 0.090472 | 0.12925 | 0.32016 | 0.51126
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.031828 | 0.071208 | 0.11178 | 0.15351 | 0.1965 | 0.24063 | 0.28579 | 0.50885 | 0.73207
| KILLACLOYNE | 10 | 1 | Conservative [MW] |  |  | 8.0833 | 8.1269 | 8.1723 | 8.2183 | 8.2639 | 8.3008 | 7.5921 | 7.6312 | 7.6686 | 7.7031 | 7.7284 | 7.7549 | 7.776 | 7.7837 | 7.7897 | 7.7852 | 7.7906 | 7.7943
|  |  |  | Best View [MW] |  |  | 8.0833 | 8.1314 | 8.1803 | 8.2283 | 8.268 | 8.3098 | 7.6168 | 7.6651 | 7.7112 | 7.7469 | 7.7756 | 7.7883 | 7.7873 | 7.7746 | 7.7267 | 7.6554 | 7.3613 | 7.0633
|  |  |  | Base Case [MW] |  |  | 8.0833 | 8.1497 | 8.2115 | 8.2731 | 8.3324 | 8.3773 | 7.686 | 7.7261 | 7.76 | 7.779 | 7.7922 | 7.7824 | 7.7557 | 7.6985 | 7.6027 | 7.4571 | 6.8618 | 6.2582
|  |  |  | Aggressive [MW] |  |  | 8.0833 | 8.1735 | 8.2616 | 8.3428 | 8.4118 | 8.455 | 7.7603 | 7.7846 | 7.7943 | 7.7852 | 7.7479 | 7.6836 | 7.5824 | 7.4121 | 7.1519 | 6.685 | 4.9017 | 3.084
|  |  | 2 | Conservative [MW] |  |  | 9.8406 | 9.8865 | 9.9326 | 9.9761 | 10.0155 | 10.0537 | 10.0903 | 10.1212 | 10.1486 | 10.1755 | 10.194 | 10.2065 | 10.2111 | 10.2103 | 10.1982 | 10.1764 | 10.0933 | 10.0085
|  |  |  | Best View [MW] |  |  | 9.8406 | 9.8903 | 9.9363 | 9.9809 | 10.0231 | 10.0651 | 10.1102 | 10.1488 | 10.1797 | 10.2003 | 10.211 | 10.2081 | 10.1832 | 10.1376 | 10.0637 | 9.9454 | 9.4724 | 8.9919
|  |  |  | Base Case [MW] |  |  | 9.8406 | 9.9074 | 9.971 | 10.0268 | 10.0818 | 10.1274 | 10.164 | 10.1906 | 10.2079 | 10.2132 | 10.1983 | 10.1649 | 10.1067 | 10.0092 | 9.8669 | 9.6501 | 8.7649 | 7.8672
|  |  |  | Aggressive [MW] |  |  | 9.8406 | 9.931 | 10.0134 | 10.0887 | 10.1486 | 10.1912 | 10.2095 | 10.212 | 10.1951 | 10.1608 | 10.0932 | 9.9844 | 9.8263 | 9.5808 | 9.1934 | 8.439 | 5.6455 | 2.7909
| KILLESHANDRA | 10 | 1 | Conservative [MW] |  |  | 7.7908 | 7.8266 | 7.8649 | 7.9004 | 7.9333 | 7.9685 | 8.0231 | 8.0722 | 8.1256 | 8.1729 | 8.2295 | 8.2791 | 8.3324 | 8.3888 | 8.443 | 8.4943 | 8.7583 | 9.0219
|  |  |  | Best View [MW] |  |  | 7.7908 | 7.8391 | 7.8832 | 7.9278 | 7.9727 | 8.0232 | 8.0906 | 8.1625 | 8.2329 | 8.3065 | 8.3774 | 8.4501 | 8.524 | 8.5984 | 8.6661 | 8.7379 | 9.086 | 9.4348
|  |  |  | Base Case [MW] |  |  | 7.7908 | 7.8478 | 7.9034 | 7.9621 | 8.0186 | 8.0826 | 8.1554 | 8.2348 | 8.3148 | 8.3947 | 8.4733 | 8.5551 | 8.6331 | 8.712 | 8.7895 | 8.8644 | 9.2458 | 9.6268
|  |  |  | Aggressive [MW] |  |  | 7.7908 | 7.8811 | 7.9653 | 8.0574 | 8.1512 | 8.2457 | 8.3391 | 8.4354 | 8.5325 | 8.629 | 8.7221 | 8.8143 | 8.903 | 8.985 | 9.0568 | 9.1266 | 9.4812 | 9.8354
| KILLIN HILL | 20 | 1 | Conservative [MW] |  |  | 8.7375 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374
|  |  |  | Best View [MW] |  |  | 8.7375 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374
|  |  |  | Base Case [MW] |  |  | 8.7375 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374
|  |  |  | Aggressive [MW] |  |  | 8.7375 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7374 | 8.7372 | 8.7372 | 8.7372 | 8.7372 | 8.7372
| KILLINICK | 20 | 1 | Conservative [MW] |  |  | 5.444 | 5.48 | 5.5172 | 5.5544 | 5.5917 | 4.8165 | 4.9058 | 4.9972 | 5.0908 | 5.1874 | 5.286 | 5.3866 | 5.489 | 5.5943 | 5.7024 | 5.8121 | 6.3566 | 6.9013
|  |  |  | Best View [MW] |  |  | 5.444 | 5.5077 | 5.5726 | 5.6385 | 5.7055 | 4.962 | 5.0635 | 5.1672 | 5.2729 | 5.3826 | 5.4942 | 5.6086 | 5.7255 | 5.8463 | 5.9682 | 6.0935 | 6.7111 | 7.3293
|  |  |  | Base Case [MW] |  |  | 5.444 | 5.5227 | 5.6027 | 5.6838 | 5.7681 | 5.0418 | 5.1551 | 5.2715 | 5.3907 | 5.5138 | 5.6407 | 5.7702 | 5.9031 | 6.0392 | 6.1784 | 6.3204 | 7.0229 | 7.7258
|  |  |  | Aggressive [MW] |  |  | 5.444 | 5.5669 | 5.6945 | 5.8251 | 5.9622 | 5.2914 | 5.4588 | 5.6317 | 5.8108 | 5.9957 | 6.187 | 6.3838 | 6.5868 | 6.7951 | 7.009 | 7.2253 | 8.3002 | 9.3756
| KILLYBEGS | 20 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.15755 | 0.39078 | 0.62801 | 1.8035 | 2.9796
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.16161 | 0.48643 | 0.82008 | 1.1627 | 1.4566 | 1.6407 | 1.8324 | 2.7705 | 3.71
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.16229 | 0.54453 | 0.9384 | 1.3454 | 1.5839 | 1.8067 | 2.0384 | 2.2798 | 3.4611 | 4.644
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.10999 | 0.55343 | 1.0129 | 1.4439 | 1.6968 | 1.9615 | 2.2399 | 2.5319 | 2.8375 | 3.4521 | 5.7012 | 8.0018
| KILLYGARRY | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978 | 20.6978
| KILMACTHOMAS | 20 | 1 | Conservative [MW] |  |  | 0.84794 | 0.88449 | 0.92177 | 0.95974 | 0.99796 | 1.0369 | 1.0875 | 1.1384 | 1.1901 | 1.2431 | 1.2968 | 1.3513 | 1.4064 | 1.4621 | 1.519 | 1.5763 | 1.8618 | 2.1474
|  |  |  | Best View [MW] |  |  | 0.84794 | 0.88831 | 0.92994 | 0.97148 | 1.0141 | 1.0576 | 1.1215 | 1.1874 | 1.2542 | 1.3223 | 1.3924 | 1.4631 | 1.535 | 1.6078 | 1.6822 | 1.7576 | 2.1318 | 2.5061
|  |  |  | Base Case [MW] |  |  | 0.84794 | 0.8957 | 0.94441 | 0.99404 | 1.0445 | 1.0963 | 1.1715 | 1.2482 | 1.3269 | 1.4077 | 1.4896 | 1.5732 | 1.6583 | 1.7448 | 1.8324 | 1.9206 | 2.3602 | 2.7998
|  |  |  | Aggressive [MW] |  |  | 0.84794 | 0.92363 | 1.0015 | 1.0816 | 1.1641 | 1.2489 | 1.3432 | 1.44 | 1.5385 | 1.6397 | 1.7427 | 1.8478 | 1.9536 | 2.0602 | 2.1666 | 2.2729 | 2.8046 | 3.3364
| KILMAGIG | 10 | 1 | Conservative [MW] |  |  | 3.9109 | 3.9206 | 3.9319 | 3.9449 | 3.9551 | 3.9671 | 3.9841 | 4.0003 | 4.0154 | 4.0317 | 4.0492 | 4.0656 | 4.0854 | 4.1017 | 4.1213 | 4.1397 | 4.235 | 4.3301
|  |  |  | Best View [MW] |  |  | 3.9109 | 3.9234 | 3.9373 | 3.9526 | 3.967 | 3.9828 | 4.0034 | 4.0246 | 4.0483 | 4.0703 | 4.0947 | 4.1172 | 4.142 | 4.1668 | 4.1938 | 4.2207 | 4.3554 | 4.4901
|  |  |  | Base Case [MW] |  |  | 3.9109 | 3.9285 | 3.947 | 3.9641 | 3.9842 | 4.0049 | 4.0275 | 4.0522 | 4.079 | 4.1056 | 4.132 | 4.1602 | 4.1878 | 4.2168 | 4.2475 | 4.2793 | 4.4354 | 4.5916
|  |  |  | Aggressive [MW] |  |  | 3.9109 | 3.9347 | 3.9603 | 3.9857 | 4.0127 | 4.0413 | 4.0748 | 4.1086 | 4.1445 | 4.1824 | 4.2219 | 4.2628 | 4.3046 | 4.3468 | 4.3917 | 4.4384 | 4.6672 | 4.8962
| KILMALLOCK | 10 | 1 | Conservative [MW] |  |  | 6.4192 | 6.4408 | 6.4615 | 6.4814 | 6.5003 | 6.5225 | 6.5449 | 6.5705 | 6.5947 | 6.6179 | 6.6438 | 6.6685 | 6.6962 | 6.7224 | 6.7514 | 6.779 | 6.9208 | 7.0623
|  |  |  | Best View [MW] |  |  | 6.4192 | 6.4392 | 6.4626 | 6.485 | 6.5064 | 6.5266 | 6.5588 | 6.5891 | 6.6254 | 6.6553 | 6.6913 | 6.7292 | 6.7645 | 6.8014 | 6.8397 | 6.8794 | 7.0742 | 7.2693
|  |  |  | Base Case [MW] |  |  | 6.4192 | 6.4479 | 6.4751 | 6.5045 | 6.5322 | 6.5623 | 6.6 | 6.6392 | 6.6752 | 6.7167 | 6.759 | 6.8022 | 6.8462 | 6.8906 | 6.9396 | 6.9844 | 7.2197 | 7.4543
|  |  |  | Aggressive [MW] |  |  | 6.4192 | 6.4627 | 6.5066 | 6.5505 | 6.5984 | 6.6458 | 6.6873 | 6.7336 | 6.7759 | 6.8227 | 6.8737 | 6.9245 | 6.9747 | 7.0286 | 7.0858 | 7.1417 | 7.4247 | 7.7075
| KILMARTIN | 10 | 1 | Conservative [MW] |  |  | 4.4831 | 4.5057 | 4.5265 | 4.5479 | 4.5697 | 4.5897 | 4.6198 | 4.6462 | 4.674 | 4.703 | 4.7305 | 4.7589 | 4.7881 | 4.815 | 4.8422 | 4.8696 | 5.0061 | 5.1425
|  |  |  | Best View [MW] |  |  | 4.4831 | 4.511 | 4.5361 | 4.563 | 4.5919 | 4.6175 | 4.6549 | 4.6907 | 4.7275 | 4.7647 | 4.802 | 4.8388 | 4.8747 | 4.9089 | 4.9411 | 4.9732 | 5.1339 | 5.2946
|  |  |  | Base Case [MW] |  |  | 4.4831 | 4.5166 | 4.5502 | 4.5865 | 4.6198 | 4.6554 | 4.6958 | 4.7383 | 4.7793 | 4.8182 | 4.8571 | 4.8981 | 4.9347 | 4.9689 | 5.0019 | 5.0332 | 5.1943 | 5.355
|  |  |  | Aggressive [MW] |  |  | 4.4831 | 4.5288 | 4.5754 | 4.6227 | 4.6696 | 4.7186 | 4.7728 | 4.8254 | 4.8778 | 4.9282 | 4.9743 | 5.0162 | 5.0512 | 5.0789 | 5.0947 | 5.0915 | 5.1263 | 5.1579
| KILMEADEN | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| KILMONEY | 10 | 1 | Conservative [MW] |  |  | 2.091 | 2.1405 | 2.1905 | 2.241 | 1.6773 | 1.7298 | 1.7815 | 1.8334 | 1.886 | 1.9394 | 1.9926 | 2.0456 | 2.099 | 2.1525 | 2.2051 | 2.2584 | 2.5231 | 2.7879
|  |  |  | Best View [MW] |  |  | 2.091 | 2.1434 | 2.1964 | 2.2496 | 1.6892 | 1.7443 | 1.8144 | 1.8844 | 1.956 | 2.027 | 2.099 | 2.1703 | 2.2419 | 2.3121 | 2.3818 | 2.4506 | 2.7969 | 3.1432
|  |  |  | Base Case [MW] |  |  | 2.091 | 2.1627 | 2.2353 | 2.3093 | 1.7704 | 1.8475 | 1.9184 | 1.9894 | 2.0616 | 2.1334 | 2.2047 | 2.2756 | 2.3464 | 2.4156 | 2.4833 | 2.5491 | 2.8832 | 3.2169
|  |  |  | Aggressive [MW] |  |  | 2.091 | 2.19 | 2.2902 | 2.393 | 1.8855 | 1.9925 | 2.0654 | 2.1392 | 2.2117 | 2.2842 | 2.3557 | 2.426 | 2.4946 | 2.5617 | 2.6244 | 2.6835 | 2.9884 | 3.2928
| KILROSS ROAD | 10 | 1 | Conservative [MW] |  |  | 3.5183 | 3.5236 | 3.5268 | 3.5318 | 3.5348 | 3.5396 | 3.5458 | 3.5517 | 3.5593 | 3.5648 | 3.5719 | 3.5788 | 3.5854 | 3.5936 | 3.5996 | 3.6072 | 3.641 | 3.6751
|  |  |  | Best View [MW] |  |  | 3.5183 | 3.5241 | 3.5279 | 3.5334 | 3.5388 | 3.5458 | 3.5534 | 3.5625 | 3.5729 | 3.5829 | 3.5922 | 3.6029 | 3.6149 | 3.6263 | 3.637 | 3.6489 | 3.7053 | 3.7619
|  |  |  | Base Case [MW] |  |  | 3.5183 | 3.5254 | 3.5322 | 3.5387 | 3.5468 | 3.5545 | 3.5646 | 3.574 | 3.5847 | 3.5968 | 3.6081 | 3.6187 | 3.6306 | 3.6436 | 3.6578 | 3.6711 | 3.74 | 3.8087
|  |  |  | Aggressive [MW] |  |  | 3.5183 | 3.5292 | 3.5394 | 3.5525 | 3.5648 | 3.5761 | 3.5877 | 3.6005 | 3.6125 | 3.6257 | 3.638 | 3.6513 | 3.6658 | 3.6812 | 3.6955 | 3.7108 | 3.7847 | 3.8587
|  | 20 | 1 | Conservative [MW] |  |  | 0.6876 | 0.69755 | 0.70774 | 0.71812 | 0.7287 | 0.73933 | 0.75383 | 0.76873 | 0.78389 | 0.79932 | 0.81512 | 0.8313 | 0.8478 | 0.86457 | 0.88188 | 0.89948 | 0.98669 | 1.0739
|  |  |  | Best View [MW] |  |  | 0.6876 | 0.69968 | 0.71208 | 0.72474 | 0.73764 | 0.75079 | 0.77199 | 0.79397 | 0.81652 | 0.83984 | 0.86376 | 0.88849 | 0.91396 | 0.94028 | 0.96727 | 0.99496 | 1.1315 | 1.2682
|  |  |  | Base Case [MW] |  |  | 0.6876 | 0.70384 | 0.72047 | 0.73768 | 0.75526 | 0.77334 | 0.79665 | 0.82086 | 0.84579 | 0.87154 | 0.89818 | 0.9256 | 0.95397 | 0.98306 | 1.0129 | 1.044 | 1.1962 | 1.3486
|  |  |  | Aggressive [MW] |  |  | 0.6876 | 0.71306 | 0.73973 | 0.76747 | 0.79639 | 0.82648 | 0.85303 | 0.88054 | 0.90893 | 0.9383 | 0.96868 | 0.99989 | 1.0323 | 1.0656 | 1.1 | 1.1355 | 1.3099 | 1.4846
| KILRUSH | 10 | 1 | Conservative [MW] |  |  | 6.4493 | 6.4743 | 6.4981 | 6.5207 | 6.5466 | 6.5757 | 6.6101 | 6.6468 | 6.6811 | 6.7172 | 6.7554 | 6.7954 | 6.8327 | 6.8715 | 6.912 | 6.9538 | 7.1594 | 7.3651
|  |  |  | Best View [MW] |  |  | 6.4493 | 6.4733 | 6.5003 | 6.5303 | 6.5588 | 6.5857 | 6.6387 | 6.687 | 6.7392 | 6.7952 | 6.8502 | 6.9041 | 6.9655 | 7.0252 | 7.0826 | 7.1468 | 7.4496 | 7.7536
|  |  |  | Base Case [MW] |  |  | 6.4493 | 6.4907 | 6.5329 | 6.5803 | 6.6284 | 6.6721 | 6.7289 | 6.7887 | 6.8466 | 6.9069 | 6.9692 | 7.0381 | 7.1032 | 7.1693 | 7.2406 | 7.3117 | 7.6677 | 8.0237
|  |  |  | Aggressive [MW] |  |  | 6.4493 | 6.5241 | 6.6011 | 6.6838 | 6.7714 | 6.8584 | 6.9257 | 6.9895 | 7.0584 | 7.1323 | 7.2056 | 7.2777 | 7.3532 | 7.4312 | 7.5112 | 7.5922 | 7.9945 | 8.3971
| KILSARAN | 10 | 1 | Conservative [MW] |  |  | 3.5772 | 3.5884 | 3.5991 | 3.6113 | 3.623 | 3.6341 | 3.6473 | 3.6599 | 3.6738 | 3.687 | 3.7016 | 3.7154 | 3.7305 | 3.7448 | 3.7604 | 3.7772 | 3.8579 | 3.9388
|  |  |  | Best View [MW] |  |  | 3.5772 | 3.5903 | 3.6028 | 3.6146 | 3.6278 | 3.6404 | 3.6584 | 3.6774 | 3.6971 | 3.7154 | 3.7364 | 3.7579 | 3.7778 | 3.8002 | 3.8229 | 3.846 | 3.9604 | 4.0749
|  |  |  | Base Case [MW] |  |  | 3.5772 | 3.5947 | 3.613 | 3.6319 | 3.6515 | 3.6715 | 3.6932 | 3.7154 | 3.7379 | 3.7604 | 3.785 | 3.8097 | 3.8363 | 3.8626 | 3.8907 | 3.9181 | 4.0569 | 4.1956
|  |  |  | Aggressive [MW] |  |  | 3.5772 | 3.6018 | 3.626 | 3.6538 | 3.6807 | 3.7088 | 3.7348 | 3.7624 | 3.7915 | 3.8196 | 3.8511 | 3.8812 | 3.9142 | 3.9499 | 3.9836 | 4.0217 | 4.2005 | 4.38
| KILSHANNY | 10 | 1 | Conservative [MW] |  |  | 2.4646 | 2.4798 | 2.4986 | 2.5159 | 2.5318 | 2.5511 | 2.5697 | 2.5866 | 2.6068 | 2.6254 | 2.6422 | 2.6623 | 2.6803 | 2.7015 | 2.7207 | 2.743 | 2.8462 | 2.95
|  |  |  | Best View [MW] |  |  | 2.4646 | 2.4819 | 2.4978 | 2.517 | 2.5394 | 2.5552 | 2.5785 | 2.6039 | 2.6312 | 2.6553 | 2.6811 | 2.7085 | 2.7373 | 2.762 | 2.7877 | 2.8198 | 2.9632 | 3.1077
|  |  |  | Base Case [MW] |  |  | 2.4646 | 2.4877 | 2.5128 | 2.5399 | 2.5638 | 2.5894 | 2.6177 | 2.6429 | 2.6697 | 2.6929 | 2.7229 | 2.7487 | 2.7756 | 2.8033 | 2.8317 | 2.8607 | 3.0039 | 3.1473
|  |  |  | Aggressive [MW] |  |  | 2.4646 | 2.4995 | 2.5339 | 2.5673 | 2.6042 | 2.6445 | 2.6688 | 2.6946 | 2.7268 | 2.7549 | 2.7782 | 2.8076 | 2.8374 | 2.8674 | 2.8972 | 2.9265 | 3.0745 | 3.2223
| KILTIMAGH | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| KIMMAGE | 10 | 1 | Conservative [MW] |  |  | 13.0737 | 13.151 | 13.2306 | 13.3101 | 13.3916 | 13.477 | 13.5512 | 13.6305 | 13.7079 | 13.7874 | 13.8692 | 13.9505 | 14.0331 | 14.1196 | 14.2045 | 14.2901 | 14.7163 | 15.1427
|  |  |  | Best View [MW] |  |  | 13.6786 | 13.8001 | 13.925 | 14.055 | 14.19 | 14.3292 | 13.6324 | 13.7187 | 13.8079 | 13.8997 | 13.9914 | 14.0849 | 14.1798 | 14.2757 | 14.3722 | 14.4709 | 14.9587 | 15.4469
|  |  |  | Base Case [MW] |  |  | 13.0737 | 13.1775 | 13.2849 | 13.3952 | 13.5102 | 13.6267 | 13.7216 | 13.8179 | 13.9175 | 14.0176 | 14.1199 | 14.2239 | 14.3289 | 14.4346 | 14.5422 | 14.6516 | 15.194 | 15.7367
|  |  |  | Aggressive [MW] |  |  | 13.0737 | 13.2508 | 13.4376 | 13.6327 | 13.8348 | 14.0472 | 14.1432 | 14.2419 | 14.3427 | 14.4453 | 14.5468 | 14.6511 | 14.7555 | 14.859 | 14.9633 | 15.0678 | 15.5898 | 16.1119
| KINGSBRIDGE | 10 | 1 | Conservative [MW] |  |  | 15.2242 | 15.2867 | 15.3514 | 15.4141 | 15.478 | 14.4731 | 14.5342 | 14.5904 | 14.6485 | 14.7078 | 14.7612 | 14.8187 | 14.8689 | 14.922 | 14.9705 | 15.0134 | 15.2429 | 15.4715
|  |  |  | Best View [MW] |  |  | 15.2242 | 15.297 | 15.3726 | 15.4463 | 15.5171 | 14.5276 | 14.593 | 14.658 | 14.7221 | 14.7847 | 14.8452 | 14.9025 | 14.9564 | 15.0056 | 15.0562 | 15.0955 | 15.322 | 15.5467
|  |  |  | Base Case [MW] |  |  | 15.2242 | 15.3095 | 15.3966 | 15.4809 | 15.5645 | 14.5881 | 14.6582 | 14.7286 | 14.7952 | 14.8607 | 14.9206 | 14.9809 | 15.0333 | 15.0827 | 15.1247 | 15.1573 | 15.3454 | 15.5319
|  |  |  | Aggressive [MW] |  |  | 15.2242 | 15.3683 | 15.5113 | 15.6472 | 15.7804 | 14.8766 | 14.9353 | 14.9887 | 15.0395 | 15.0851 | 15.1253 | 15.1587 | 15.1797 | 15.1982 | 15.1995 | 15.1901 | 15.1717 | 15.1515
| KINGSCOURT | 10 | 1 | Conservative [MW] |  |  | 12.4773 | 12.5195 | 12.5601 | 12.6028 | 12.644 | 12.687 | 12.7348 | 12.7841 | 12.8352 | 12.8838 | 12.9377 | 12.9891 | 13.0453 | 13.0992 | 13.158 | 13.2138 | 13.5007 | 13.7872
|  |  |  | Best View [MW] |  |  | 12.4773 | 12.5236 | 12.5683 | 12.6145 | 12.6621 | 12.7113 | 12.7778 | 12.8475 | 12.9167 | 12.9889 | 13.0638 | 13.1415 | 13.2215 | 13.3036 | 13.3876 | 13.4735 | 13.8978 | 14.3225
|  |  |  | Base Case [MW] |  |  | 12.4773 | 12.5444 | 12.6112 | 12.6808 | 12.7533 | 12.8282 | 12.9034 | 12.988 | 13.0704 | 13.158 | 13.2465 | 13.3393 | 13.4365 | 13.5333 | 13.6376 | 13.7408 | 14.2599 | 14.7788
|  |  |  | Aggressive [MW] |  |  | 12.4773 | 12.568 | 12.6582 | 12.755 | 12.8577 | 12.9621 | 13.0608 | 13.1624 | 13.2665 | 13.3724 | 13.4874 | 13.6031 | 13.7269 | 13.8537 | 13.9832 | 14.1184 | 14.779 | 15.4406
|  | 20 | 1 | Conservative [MW] |  |  | 3.3908 | 3.3908 | 3.3906 | 3.3906 | 3.3906 | 3.3906 | 3.3906 | 3.3906 | 3.3906 | 3.3912 | 3.3917 | 3.3924 | 3.3931 | 3.3937 | 3.3945 | 3.3951 | 3.3987 | 3.4023
|  |  |  | Best View [MW] |  |  | 3.3908 | 3.3908 | 3.3906 | 3.3906 | 3.3906 | 3.3906 | 3.3906 | 3.3909 | 3.3918 | 3.3927 | 3.3936 | 3.3945 | 3.3955 | 3.3966 | 3.3978 | 3.399 | 3.4051 | 3.4111
|  |  |  | Base Case [MW] |  |  | 3.3908 | 3.3908 | 3.3906 | 3.3906 | 3.3906 | 3.3906 | 3.391 | 3.3918 | 3.3929 | 3.3939 | 3.3951 | 3.3961 | 3.3974 | 3.3988 | 3.4001 | 3.4015 | 3.4084 | 3.4153
|  |  |  | Aggressive [MW] |  |  | 3.3908 | 3.3906 | 3.3906 | 3.3906 | 3.3909 | 3.392 | 3.3932 | 3.3944 | 3.3957 | 3.3972 | 3.3988 | 3.4005 | 3.4023 | 3.4044 | 3.4066 | 3.4086 | 3.4193 | 3.4299
| KINSALE | 10 | 1 | Conservative [MW] |  |  | 2.3378 | 2.3842 | 2.4314 | 2.4793 | 2.5281 | 2.5775 | 2.6264 | 2.6759 | 2.726 | 2.778 | 2.829 | 2.8819 | 2.9351 | 2.9885 | 3.042 | 3.0954 | 3.3625 | 3.6296
|  |  |  | Best View [MW] |  |  | 2.3378 | 2.3867 | 2.4363 | 2.4866 | 2.539 | 2.5906 | 2.6571 | 2.7249 | 2.794 | 2.8641 | 2.9351 | 3.0069 | 3.0789 | 3.1511 | 3.2248 | 3.2999 | 3.6716 | 4.0436
|  |  |  | Base Case [MW] |  |  | 2.3378 | 2.4053 | 2.4732 | 2.5438 | 2.6157 | 2.6888 | 2.7573 | 2.8269 | 2.8975 | 2.9688 | 3.0406 | 3.1144 | 3.1882 | 3.2615 | 3.3361 | 3.4094 | 3.7793 | 4.149
|  |  |  | Aggressive [MW] |  |  | 2.3378 | 2.4302 | 2.5256 | 2.6253 | 2.7261 | 2.8304 | 2.9019 | 2.9741 | 3.0483 | 3.1226 | 3.1966 | 3.2719 | 3.3481 | 3.4229 | 3.4998 | 3.5742 | 3.953 | 4.3313
|  | 20 | 1 | Conservative [MW] |  |  | 6.9593 | 6.9673 | 6.9748 | 6.9842 | 6.9912 | 6.9998 | 7.0083 | 7.0166 | 7.0264 | 7.0359 | 7.045 | 7.0538 | 7.0641 | 7.074 | 7.0856 | 7.0948 | 7.147 | 7.1989
|  |  |  | Best View [MW] |  |  | 6.9593 | 6.9686 | 6.9755 | 6.9841 | 6.9941 | 7.0019 | 7.0138 | 7.0268 | 7.0392 | 7.0511 | 7.0642 | 7.0785 | 7.0921 | 7.1069 | 7.1211 | 7.1363 | 7.2094 | 7.2827
|  |  |  | Base Case [MW] |  |  | 6.9593 | 6.9699 | 6.9817 | 6.9947 | 7.0072 | 7.019 | 7.0317 | 7.0438 | 7.0572 | 7.0718 | 7.0857 | 7.0989 | 7.1134 | 7.1289 | 7.1456 | 7.1615 | 7.2429 | 7.3242
|  |  |  | Aggressive [MW] |  |  | 6.9593 | 6.9751 | 6.9916 | 7.0087 | 7.0266 | 7.0449 | 7.0579 | 7.0721 | 7.0857 | 7.1003 | 7.1161 | 7.1312 | 7.1473 | 7.1645 | 7.1808 | 7.2 | 7.2883 | 7.377
| KNOCKAPHUNTA | 10 | 1 | Conservative [MW] |  |  | 6.5189 | 6.5315 | 6.544 | 6.5515 | 6.5635 | 6.5738 | 6.6177 | 6.6626 | 6.7129 | 6.7591 | 6.8056 | 6.8524 | 6.9041 | 6.9559 | 7.0072 | 7.0581 | 7.3139 | 7.5697
|  |  |  | Best View [MW] |  |  | 6.5189 | 6.5439 | 6.5723 | 6.5993 | 6.6251 | 6.6525 | 6.7082 | 6.7673 | 6.8244 | 6.8844 | 6.9468 | 7.0063 | 7.0678 | 7.1355 | 7.1991 | 7.2635 | 7.5831 | 7.9029
|  |  |  | Base Case [MW] |  |  | 6.5189 | 6.5558 | 6.5949 | 6.6358 | 6.674 | 6.7121 | 6.7791 | 6.8509 | 6.9221 | 6.997 | 7.0751 | 7.1506 | 7.2332 | 7.3115 | 7.3951 | 7.4727 | 7.8766 | 8.2795
|  |  |  | Aggressive [MW] |  |  | 6.5189 | 6.5944 | 6.6728 | 6.7537 | 6.8356 | 6.9212 | 7.0162 | 7.1201 | 7.2216 | 7.3288 | 7.44 | 7.5476 | 7.6541 | 7.7626 | 7.8706 | 7.9795 | 8.5214 | 9.0635
| KNOCKMULLEN | 10 | 1 | Conservative [MW] |  |  | 8.1761 | 8.1975 | 8.219 | 8.2397 | 8.2595 | 8.281 | 8.3308 | 8.3805 | 8.4325 | 8.4864 | 8.5396 | 8.5943 | 8.6503 | 8.705 | 8.7629 | 8.821 | 9.111 | 9.401
|  |  |  | Best View [MW] |  |  | 8.1761 | 8.2136 | 8.2495 | 8.2877 | 8.3233 | 8.3608 | 8.4165 | 8.4732 | 8.5331 | 8.5913 | 8.652 | 8.7126 | 8.7752 | 8.8395 | 8.905 | 8.9688 | 9.2923 | 9.6156
|  |  |  | Base Case [MW] |  |  | 8.1761 | 8.2227 | 8.2665 | 8.3113 | 8.3591 | 8.405 | 8.4685 | 8.5316 | 8.5962 | 8.6622 | 8.7312 | 8.8006 | 8.8696 | 8.9405 | 9.0125 | 9.0876 | 9.4548 | 9.8226
|  |  |  | Aggressive [MW] |  |  | 8.1761 | 8.2465 | 8.318 | 8.3891 | 8.464 | 8.5421 | 8.6322 | 8.725 | 8.8219 | 8.9192 | 9.0175 | 9.1181 | 9.2218 | 9.3239 | 9.4274 | 9.528 | 10.0385 | 10.5486
|  | 20 | 1 | Conservative [MW] |  |  | 8.211 | 8.234 | 8.2548 | 8.2748 | 8.2957 | 8.3163 | 8.3666 | 8.417 | 8.4693 | 8.5235 | 8.5772 | 8.6321 | 8.6884 | 8.7454 | 8.8056 | 8.8637 | 9.1596 | 9.4553
|  |  |  | Best View [MW] |  |  | 8.211 | 8.2496 | 8.2866 | 8.3236 | 8.3594 | 8.3979 | 8.4539 | 8.5132 | 8.5709 | 8.6314 | 8.6923 | 8.7552 | 8.8174 | 8.8812 | 8.9461 | 9.0141 | 9.346 | 9.6783
|  |  |  | Base Case [MW] |  |  | 8.211 | 8.2562 | 8.3031 | 8.3487 | 8.394 | 8.4428 | 8.5063 | 8.5694 | 8.6364 | 8.7021 | 8.7707 | 8.8417 | 8.9125 | 8.9847 | 9.0582 | 9.1319 | 9.4996 | 9.8674
|  |  |  | Aggressive [MW] |  |  | 8.211 | 8.2814 | 8.3528 | 8.4284 | 8.502 | 8.5819 | 8.6733 | 8.7671 | 8.8621 | 8.962 | 9.0628 | 9.1632 | 9.2686 | 9.3723 | 9.4741 | 9.5771 | 10.0889 | 10.6008
| KNOCKNAGEE | 10 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.2598 | 18.1849 | 18.1372 | 18.116 | 18.0939 | 18.0706 | 18.048 | 18.0223 | 17.9953 | 17.9668 | 17.9389 | 17.798 | 17.6572
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.2521 | 18.1612 | 18.1064 | 18.0752 | 18.044 | 18.0086 | 17.9728 | 17.9345 | 17.8933 | 17.8492 | 17.8017 | 17.5732 | 17.3442
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.2333 | 18.1361 | 18.0741 | 18.037 | 17.9969 | 17.9535 | 17.9066 | 17.8558 | 17.8026 | 17.7434 | 17.6842 | 17.3882 | 17.0922
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.169 | 18.0582 | 17.9801 | 17.9228 | 17.8614 | 17.7932 | 17.72 | 17.6431 | 17.5557 | 17.4602 | 17.3509 | 16.8413 | 16.3293
| KYLEERAGH | 10 | 1 | Conservative [MW] |  |  | 7.8285 | 7.8105 | 7.7873 | 7.7584 | 7.7165 | 7.672 | 7.5823 | 7.47 | 7.3113 | 7.0916 | 6.7752 | 6.2481 | 5.1123 | 5.079 | 5.0434 | 5.0097 | 4.8361 | 4.6628
|  |  |  | Best View [MW] |  |  | 7.8285 | 7.8035 | 7.7727 | 7.7312 | 7.674 | 7.5977 | 7.4304 | 7.1651 | 6.7162 | 5.5632 | 5.0777 | 5.0279 | 4.9789 | 4.9221 | 4.8619 | 4.7932 | 4.4724 | 4.1501
|  |  |  | Base Case [MW] |  |  | 7.8285 | 7.7957 | 7.7455 | 7.6728 | 7.5674 | 7.4172 | 7.1164 | 6.583 | 5.1138 | 5.0598 | 5.0081 | 4.9531 | 4.8891 | 4.8201 | 4.7423 | 4.6513 | 4.2316 | 3.8097
|  |  |  | Aggressive [MW] |  |  | 7.8285 | 7.7694 | 7.658 | 7.4692 | 7.1209 | 6.4176 | 5.0981 | 5.0407 | 4.9826 | 4.9194 | 4.8451 | 4.7638 | 4.6701 | 4.5371 | 4.4171 | 4.2841 | 3.6538 | 3.0213
| LAWLESSTOWN | 10 | 1 | Conservative [MW] |  |  | 12.4085 | 12.4744 | 12.545 | 12.6128 | 12.6816 | 12.751 | 12.8447 | 12.9407 | 13.039 | 13.1393 | 13.2413 | 13.3406 | 13.4456 | 13.5517 | 13.6582 | 13.77 | 14.3148 | 14.8605
|  |  |  | Best View [MW] |  |  | 12.4085 | 12.4856 | 12.5592 | 12.6403 | 12.7181 | 12.7995 | 12.9284 | 13.0624 | 13.1969 | 13.3359 | 13.4783 | 13.6238 | 13.7713 | 13.9206 | 14.0947 | 14.2827 | 15.1856 | 16.0909
|  |  |  | Base Case [MW] |  |  | 12.4085 | 12.5077 | 12.6084 | 12.7143 | 12.8212 | 12.9286 | 13.0754 | 13.2206 | 13.3718 | 13.5282 | 13.6851 | 13.8496 | 14.0188 | 14.2237 | 14.4292 | 14.6438 | 15.6926 | 16.743
|  |  |  | Aggressive [MW] |  |  | 12.4085 | 12.5649 | 12.7253 | 12.8889 | 13.0626 | 13.2375 | 13.4061 | 13.58 | 13.7586 | 13.9399 | 14.1533 | 14.3867 | 14.6203 | 14.8666 | 15.1202 | 15.3795 | 16.661 | 17.9434
| LEESON STREET | 10 | 1 | Conservative [MW] |  |  | 15.4892 | 15.5784 | 15.6736 | 15.7651 | 15.8621 | 15.9592 | 16.0466 | 15.7463 | 15.8367 | 15.9284 | 16.0255 | 16.1182 | 16.2159 | 16.3135 | 16.4153 | 16.5161 | 17.0227 | 17.5291
|  |  |  | Best View [MW] |  |  | 15.4892 | 15.595 | 15.7037 | 15.8102 | 15.9236 | 16.0382 | 16.1404 | 15.8485 | 15.954 | 16.058 | 16.1652 | 16.2747 | 16.3858 | 16.4987 | 16.6126 | 16.7264 | 17.2955 | 17.8645
|  |  |  | Base Case [MW] |  |  | 15.4892 | 15.6106 | 15.7357 | 15.8636 | 15.9985 | 16.1349 | 16.2432 | 15.9658 | 16.0824 | 16.2001 | 16.3176 | 16.4396 | 16.5604 | 16.6842 | 16.8092 | 16.9353 | 17.563 | 18.1908
|  |  |  | Aggressive [MW] |  |  | 15.4892 | 15.6954 | 15.9134 | 16.14 | 16.3754 | 16.6184 | 16.7316 | 16.4605 | 16.5752 | 16.6939 | 16.8157 | 16.9355 | 17.0525 | 17.176 | 17.294 | 17.4167 | 18.0178 | 18.6196
| LEIXLIP | 10 | 1 | Conservative [MW] |  |  | 14.6538 | 14.8013 | 14.9467 | 15.0938 | 15.2409 | 15.3726 | 15.4535 | 15.5334 | 15.611 | 15.6919 | 15.7701 | 15.8449 | 15.916 | 15.9879 | 16.0543 | 16.1153 | 16.4348 | 16.7534
|  |  |  | Best View [MW] |  |  | 14.6538 | 14.8157 | 14.9794 | 15.1382 | 15.2997 | 15.4481 | 15.5365 | 15.6306 | 15.7179 | 15.803 | 15.8857 | 15.9708 | 16.0451 | 16.1203 | 16.1872 | 16.2522 | 16.5823 | 16.9121
|  |  |  | Base Case [MW] |  |  | 14.6538 | 14.8316 | 15.0092 | 15.1837 | 15.3635 | 15.5245 | 15.6233 | 15.7229 | 15.8207 | 15.9165 | 16.0032 | 16.0904 | 16.1704 | 16.2419 | 16.3031 | 16.3674 | 16.6806 | 16.9944
|  |  |  | Aggressive [MW] |  |  | 14.6538 | 14.8742 | 15.0883 | 15.3066 | 15.5182 | 15.7098 | 15.7976 | 15.8835 | 15.9596 | 16.0437 | 16.1159 | 16.1808 | 16.2439 | 16.305 | 16.3569 | 16.4033 | 16.6499 | 16.8957
| LIFFEY VALLEY | 10 | 1 | Conservative [MW] |  |  | 14.1864 | 14.2831 | 14.3836 | 14.4835 | 14.5868 | 14.6929 | 14.7549 | 14.8178 | 14.8816 | 14.9458 | 15.0105 | 15.0803 | 15.1458 | 15.2161 | 15.2816 | 15.3563 | 15.7053 | 16.0559
|  |  |  | Best View [MW] |  |  | 14.1864 | 14.2956 | 14.4023 | 14.5151 | 14.6287 | 14.7517 | 14.8235 | 14.8945 | 14.9699 | 15.044 | 15.1221 | 15.1988 | 15.2785 | 15.357 | 15.4383 | 15.5225 | 15.9359 | 16.3497
|  |  |  | Base Case [MW] |  |  | 14.1864 | 14.3025 | 14.4226 | 14.5461 | 14.6767 | 14.8093 | 14.8898 | 14.973 | 15.0584 | 15.1462 | 15.2354 | 15.3218 | 15.4142 | 15.508 | 15.6024 | 15.6975 | 16.1712 | 16.6449
|  |  |  | Aggressive [MW] |  |  | 14.1864 | 14.3299 | 14.4793 | 14.6335 | 14.7954 | 14.9628 | 15.0379 | 15.1167 | 15.1944 | 15.2704 | 15.35 | 15.4324 | 15.5129 | 15.6009 | 15.682 | 15.77 | 16.1914 | 16.6139
| LISDRUM | 20 | 1 | Conservative [MW] |  |  | 3.7904 | 3.8028 | 3.8167 | 3.8301 | 3.845 | 3.8592 | 3.8781 | 3.8979 | 3.9185 | 3.9377 | 3.9598 | 3.9804 | 4.0038 | 4.0255 | 4.0478 | 4.0705 | 4.1827 | 4.2951
|  |  |  | Best View [MW] |  |  | 3.7904 | 3.8076 | 3.8238 | 3.8412 | 3.8596 | 3.8791 | 3.9061 | 3.9327 | 3.9609 | 3.9908 | 4.0221 | 4.0525 | 4.0841 | 4.1166 | 4.15 | 4.1841 | 4.3527 | 4.5215
|  |  |  | Base Case [MW] |  |  | 3.7904 | 3.8115 | 3.8333 | 3.8556 | 3.8783 | 3.9014 | 3.9306 | 3.9634 | 3.9948 | 4.0293 | 4.0621 | 4.0976 | 4.1333 | 4.1714 | 4.2091 | 4.246 | 4.4328 | 4.6194
|  |  |  | Aggressive [MW] |  |  | 3.7904 | 3.8228 | 3.8579 | 3.8932 | 3.9284 | 3.9656 | 4.0044 | 4.0469 | 4.0881 | 4.1299 | 4.1766 | 4.2206 | 4.2687 | 4.3154 | 4.3652 | 4.4148 | 4.6634 | 4.912
| LISMORE | 10 | 1 | Conservative [MW] |  |  | 6.4973 | 6.5179 | 6.5376 | 6.5609 | 6.5789 | 6.6004 | 6.6286 | 6.6594 | 6.6888 | 6.7162 | 6.7463 | 6.779 | 6.8096 | 6.8427 | 6.8736 | 6.9114 | 7.0822 | 7.254
|  |  |  | Best View [MW] |  |  | 6.4973 | 6.5213 | 6.5442 | 6.5661 | 6.5911 | 6.615 | 6.6552 | 6.6921 | 6.7346 | 6.778 | 6.8222 | 6.8672 | 6.9125 | 6.9583 | 7.0086 | 7.0544 | 7.2953 | 7.5355
|  |  |  | Base Case [MW] |  |  | 6.4973 | 6.5284 | 6.5577 | 6.5894 | 6.6191 | 6.6553 | 6.698 | 6.7412 | 6.7892 | 6.8372 | 6.8852 | 6.933 | 6.989 | 7.04 | 7.0944 | 7.152 | 7.4316 | 7.7117
|  |  |  | Aggressive [MW] |  |  | 6.4973 | 6.5466 | 6.5915 | 6.6401 | 6.6923 | 6.7477 | 6.7966 | 6.8534 | 6.9047 | 6.9632 | 7.0245 | 7.0833 | 7.1443 | 7.2112 | 7.2794 | 7.3435 | 7.6751 | 8.0061
| LITTLE BRAY | 10 | 1 | Conservative [MW] |  |  | 13.6751 | 13.7729 | 13.8662 | 13.9649 | 14.0634 | 14.1614 | 14.2425 | 14.3169 | 14.3995 | 14.4805 | 14.5638 | 14.6451 | 14.7288 | 14.8146 | 14.9018 | 14.9855 | 15.4135 | 15.841
|  |  |  | Best View [MW] |  |  | 13.6751 | 13.7843 | 13.8955 | 14.0086 | 14.1231 | 14.2429 | 14.334 | 14.4303 | 14.5222 | 14.6193 | 14.7161 | 14.8173 | 14.917 | 15.0148 | 15.1207 | 15.2189 | 15.7303 | 16.2405
|  |  |  | Base Case [MW] |  |  | 13.6751 | 13.7988 | 13.9218 | 14.0524 | 14.1807 | 14.3153 | 14.4218 | 14.5264 | 14.6334 | 14.7423 | 14.853 | 14.9693 | 15.0804 | 15.1963 | 15.3109 | 15.4237 | 15.9923 | 16.5607
|  |  |  | Aggressive [MW] |  |  | 13.6751 | 13.8525 | 14.0353 | 14.2264 | 14.4229 | 14.6269 | 14.7292 | 14.8349 | 14.9378 | 15.0422 | 15.1533 | 15.2602 | 15.3676 | 15.4793 | 15.5849 | 15.6945 | 16.232 | 16.7701
| LITTLE MILLS | 10 | 1 | Conservative [MW] |  |  | 4.1127 | 4.1332 | 4.1547 | 4.1746 | 4.1955 | 4.2171 | 4.238 | 4.2616 | 4.2857 | 4.3101 | 4.3347 | 4.3596 | 4.3846 | 4.4095 | 4.4344 | 4.4616 | 4.5916 | 4.7219
|  |  |  | Best View [MW] |  |  | 4.1127 | 4.1367 | 4.159 | 4.1818 | 4.2051 | 4.2288 | 4.2595 | 4.2912 | 4.3262 | 4.3595 | 4.3933 | 4.4273 | 4.4639 | 4.5002 | 4.536 | 4.5737 | 4.7569 | 4.9405
|  |  |  | Base Case [MW] |  |  | 4.1127 | 4.1454 | 4.1791 | 4.2113 | 4.2462 | 4.2816 | 4.32 | 4.3581 | 4.3955 | 4.4344 | 4.4745 | 4.5155 | 4.5568 | 4.5982 | 4.642 | 4.6848 | 4.9012 | 5.1175
|  |  |  | Aggressive [MW] |  |  | 4.1127 | 4.1573 | 4.2019 | 4.2485 | 4.2964 | 4.3452 | 4.3907 | 4.4356 | 4.4846 | 4.5318 | 4.5793 | 4.629 | 4.6776 | 4.7269 | 4.7786 | 4.8266 | 5.0766 | 5.3259
| LLOYD | 10 | 1 | Conservative [MW] |  |  | 6.6214 | 6.6362 | 6.6467 | 6.6608 | 6.6745 | 6.6878 | 6.7127 | 6.7398 | 6.7692 | 6.8009 | 6.8307 | 6.8624 | 6.8963 | 6.9279 | 6.9612 | 6.9964 | 7.1673 | 7.3386
|  |  |  | Best View [MW] |  |  | 6.6214 | 6.638 | 6.6539 | 6.6733 | 6.6878 | 6.7059 | 6.7388 | 6.7695 | 6.8058 | 6.8397 | 6.875 | 6.9117 | 6.9495 | 6.9928 | 7.0326 | 7.0733 | 7.2745 | 7.4759
|  |  |  | Base Case [MW] |  |  | 6.6214 | 6.6523 | 6.6849 | 6.719 | 6.7545 | 6.7915 | 6.8246 | 6.863 | 6.8985 | 6.9393 | 6.981 | 7.0235 | 7.0667 | 7.1102 | 7.1584 | 7.2067 | 7.4477 | 7.6888
|  |  |  | Aggressive [MW] |  |  | 6.6214 | 6.6676 | 6.7091 | 6.7579 | 6.8098 | 6.8601 | 6.9061 | 6.9481 | 6.9984 | 7.0441 | 7.0978 | 7.1506 | 7.2023 | 7.2614 | 7.3185 | 7.3779 | 7.6687 | 7.9598
| LONGFORD | 20 | 1 | Conservative [MW] |  |  | 7.043 | 7.0749 | 7.1079 | 7.1408 | 7.1737 | 7.2078 | 7.2868 | 7.3678 | 7.4509 | 7.535 | 7.6224 | 7.7092 | 7.7992 | 7.8911 | 7.9835 | 8.079 | 8.5484 | 9.0183
|  |  |  | Best View [MW] |  |  | 7.043 | 7.1065 | 7.1723 | 7.2378 | 7.3057 | 7.3745 | 7.4724 | 7.5722 | 7.6751 | 7.7796 | 7.8873 | 7.9963 | 8.108 | 8.2223 | 8.339 | 8.458 | 9.0469 | 9.6361
|  |  |  | Base Case [MW] |  |  | 7.043 | 7.1176 | 7.1954 | 7.2744 | 7.3543 | 7.4375 | 7.5602 | 7.6869 | 7.8174 | 7.9516 | 8.0891 | 8.2298 | 8.3763 | 8.5236 | 8.6761 | 8.8318 | 9.6018 | 10.3723
|  |  |  | Aggressive [MW] |  |  | 7.043 | 7.164 | 7.2894 | 7.4188 | 7.5536 | 7.6921 | 7.8524 | 8.0193 | 8.1897 | 8.3675 | 8.5505 | 8.7379 | 8.9306 | 9.1275 | 9.3271 | 9.5319 | 10.5423 | 11.5535
| LOUGHANALLA | 10 | 1 | Conservative [MW] |  |  | 3.389 | 3.4043 | 3.419 | 3.4345 | 3.45 | 3.4657 | 3.4983 | 3.5311 | 3.566 | 3.6013 | 3.6377 | 3.6751 | 3.7138 | 3.7536 | 3.7943 | 3.8362 | 4.0428 | 4.2495
|  |  |  | Best View [MW] |  |  | 3.389 | 3.4087 | 3.4277 | 3.4476 | 3.4685 | 3.4887 | 3.5266 | 3.566 | 3.6066 | 3.6484 | 3.6914 | 3.7356 | 3.7809 | 3.8282 | 3.8769 | 3.9277 | 4.1759 | 4.4245
|  |  |  | Base Case [MW] |  |  | 3.389 | 3.4262 | 3.4646 | 3.5042 | 3.5462 | 3.5887 | 3.6317 | 3.675 | 3.7205 | 3.7671 | 3.8158 | 3.8647 | 3.9169 | 3.9701 | 4.0244 | 4.0806 | 4.3563 | 4.6324
|  |  |  | Aggressive [MW] |  |  | 3.389 | 3.4405 | 3.4952 | 3.5519 | 3.6121 | 3.6748 | 3.726 | 3.7794 | 3.835 | 3.8929 | 3.9529 | 4.0139 | 4.078 | 4.144 | 4.213 | 4.2825 | 4.6288 | 4.9752
| LOUGHLINSTOWN | 10 | 1 | Conservative [MW] |  |  | 13.8581 | 13.945 | 14.0333 | 14.123 | 14.2185 | 14.3103 | 14.3828 | 14.4596 | 14.5353 | 14.61 | 14.6882 | 14.7652 | 14.8449 | 14.9282 | 15.0093 | 15.0932 | 15.5051 | 15.9175
|  |  |  | Best View [MW] |  |  | 13.8581 | 13.9605 | 14.0617 | 14.1664 | 14.2742 | 14.3839 | 14.4716 | 14.5612 | 14.6522 | 14.7445 | 14.8377 | 14.9317 | 15.0261 | 15.1204 | 15.2194 | 15.3173 | 15.8097 | 16.302
|  |  |  | Base Case [MW] |  |  | 13.8581 | 13.9697 | 14.0868 | 14.2089 | 14.3307 | 14.4562 | 14.5545 | 14.6523 | 14.7589 | 14.8595 | 14.968 | 15.0744 | 15.1829 | 15.2932 | 15.4044 | 15.5214 | 16.091 | 16.6616
|  |  |  | Aggressive [MW] |  |  | 13.8581 | 14.0205 | 14.1924 | 14.3721 | 14.5567 | 14.7488 | 14.8449 | 14.9458 | 15.0456 | 15.1494 | 15.2513 | 15.3562 | 15.4636 | 15.5726 | 15.6775 | 15.788 | 16.3255 | 16.8639
| LOUGHREA | 10 | 1 | Conservative [MW] |  |  | 2.5924 | 2.6214 | 2.6517 | 2.68 | 2.7113 | 2.7411 | 2.1879 | 2.2379 | 2.2885 | 2.3394 | 2.3923 | 2.4455 | 2.4972 | 2.5506 | 2.6059 | 2.6591 | 2.9305 | 3.2015
|  |  |  | Best View [MW] |  |  | 2.5924 | 2.6369 | 2.6839 | 2.73 | 2.7784 | 2.8264 | 2.2944 | 2.3653 | 2.4385 | 2.5138 | 2.5876 | 2.6648 | 2.7396 | 2.8174 | 2.8939 | 2.9704 | 3.3529 | 3.7353
|  |  |  | Base Case [MW] |  |  | 2.5924 | 2.6563 | 2.7219 | 2.7889 | 2.8553 | 2.9253 | 2.4012 | 2.4799 | 2.5619 | 2.6416 | 2.7238 | 2.8063 | 2.8887 | 2.9723 | 3.0546 | 3.1344 | 3.5401 | 3.9454
|  |  |  | Aggressive [MW] |  |  | 2.5924 | 2.6913 | 2.7909 | 2.8959 | 3.0019 | 3.109 | 2.597 | 2.688 | 2.7785 | 2.8697 | 2.9609 | 3.0512 | 3.1395 | 3.2269 | 3.3096 | 3.3886 | 3.7935 | 4.1977
| LOUGHSHINNY | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.00045773 | 0.090829 | 0.30318 | 0.53051
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.073978 | 0.17667 | 0.28141 | 0.79966 | 1.3182
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.082272 | 0.17393 | 0.26681 | 0.36079 | 0.82777 | 1.2949
| LOUGHTAGALLA | 10 | 1 | Conservative [MW] |  |  | 6.4211 | 6.4472 | 6.4722 | 6.496 | 6.5229 | 6.5486 | 6.5869 | 6.6229 | 6.6607 | 6.6961 | 6.7377 | 6.7767 | 6.8173 | 6.855 | 6.8985 | 6.939 | 7.1496 | 7.3597
|  |  |  | Best View [MW] |  |  | 6.4211 | 6.4526 | 6.4824 | 6.5148 | 6.5454 | 6.5784 | 6.6295 | 6.6842 | 6.7381 | 6.7953 | 6.8557 | 6.9143 | 6.9754 | 7.0343 | 7.0996 | 7.1618 | 7.4811 | 7.7999
|  |  |  | Base Case [MW] |  |  | 6.4211 | 6.4598 | 6.5041 | 6.5452 | 6.5874 | 6.6349 | 6.6896 | 6.7516 | 6.8116 | 6.8739 | 6.9382 | 6.9992 | 7.0662 | 7.1338 | 7.2067 | 7.2743 | 7.6263 | 7.9774
|  |  |  | Aggressive [MW] |  |  | 6.4211 | 6.4854 | 6.5508 | 6.6212 | 6.6915 | 6.766 | 6.829 | 6.8932 | 6.9631 | 7.0333 | 7.1037 | 7.1734 | 7.2517 | 7.3233 | 7.4024 | 7.4782 | 7.8662 | 8.2535
| LUCAN EAST | 10 | 1 | Conservative [MW] |  |  | 6.4033 | 6.4601 | 6.5237 | 6.5851 | 6.6482 | 6.7131 | 6.7526 | 6.7897 | 6.8286 | 6.8646 | 6.9069 | 6.9464 | 6.9873 | 7.0251 | 7.0689 | 7.1095 | 7.3211 | 7.5321
|  |  |  | Best View [MW] |  |  | 6.4033 | 6.4668 | 6.5358 | 6.6054 | 6.6751 | 6.7492 | 6.7887 | 6.8337 | 6.8798 | 6.9265 | 6.9692 | 7.0173 | 7.0658 | 7.1097 | 7.1587 | 7.2075 | 7.4523 | 7.6969
|  |  |  | Base Case [MW] |  |  | 6.4033 | 6.4727 | 6.5503 | 6.6267 | 6.7013 | 6.7826 | 6.8352 | 6.8833 | 6.9356 | 6.9875 | 7.0388 | 7.0894 | 7.1439 | 7.1971 | 7.2536 | 7.3082 | 7.5865 | 7.8644
|  |  |  | Aggressive [MW] |  |  | 6.4033 | 6.489 | 6.5824 | 6.6784 | 6.7754 | 6.8768 | 6.9195 | 6.9677 | 7.0115 | 7.0608 | 7.1054 | 7.1553 | 7.2049 | 7.2546 | 7.2985 | 7.3522 | 7.5948 | 7.839
| LUMCLOON | 20 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| MACROOM | 20 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| MALAHIDE | 10 | 1 | Conservative [MW] |  |  | 12.0471 | 12.168 | 12.2842 | 12.4094 | 12.5338 | 12.6599 | 12.7334 | 12.8104 | 12.8823 | 12.9623 | 13.0354 | 13.1123 | 13.1922 | 13.27 | 13.3508 | 13.4288 | 13.8262 | 14.2232
|  |  |  | Best View [MW] |  |  | 12.0471 | 12.1764 | 12.3124 | 12.4446 | 12.5863 | 12.7266 | 12.8133 | 12.897 | 12.9871 | 13.0737 | 13.1616 | 13.2554 | 13.3446 | 13.4336 | 13.5279 | 13.6219 | 14.0928 | 14.5636
|  |  |  | Base Case [MW] |  |  | 12.0471 | 12.1925 | 12.3364 | 12.4869 | 12.6425 | 12.7967 | 12.8956 | 12.994 | 13.0914 | 13.1926 | 13.2921 | 13.3949 | 13.4997 | 13.6014 | 13.71 | 13.8135 | 14.3446 | 14.8749
|  |  |  | Aggressive [MW] |  |  | 12.0471 | 12.2248 | 12.4043 | 12.5879 | 12.7829 | 12.9767 | 13.0647 | 13.1538 | 13.2438 | 13.3345 | 13.4252 | 13.5212 | 13.6117 | 13.7065 | 13.7995 | 13.8916 | 14.3546 | 14.8174
| MALLOW | 10 | 1 | Conservative [MW] |  |  | 13.0067 | 13.0572 | 13.1088 | 13.1621 | 13.2167 | 13.2722 | 13.3307 | 13.3859 | 13.4465 | 13.5035 | 13.5658 | 13.6245 | 13.688 | 13.752 | 13.8206 | 13.8854 | 14.2193 | 14.5525
|  |  |  | Best View [MW] |  |  | 13.0067 | 13.0598 | 13.114 | 13.1733 | 13.2295 | 13.2907 | 13.363 | 13.4423 | 13.524 | 13.6036 | 13.6897 | 13.7774 | 13.8622 | 13.9569 | 14.048 | 14.1443 | 14.6119 | 15.0804
|  |  |  | Base Case [MW] |  |  | 13.0067 | 13.0795 | 13.1551 | 13.2331 | 13.313 | 13.3993 | 13.4786 | 13.5602 | 13.6439 | 13.7292 | 13.8158 | 13.9084 | 14.0016 | 14.0953 | 14.1936 | 14.2916 | 14.7824 | 15.2731
|  |  |  | Aggressive [MW] |  |  | 13.0067 | 13.1067 | 13.2168 | 13.3278 | 13.4431 | 13.5616 | 13.6492 | 13.7378 | 13.8277 | 13.9227 | 14.0179 | 14.1133 | 14.2126 | 14.3157 | 14.422 | 14.5311 | 15.069 | 15.6075
| MANGANS | 20 | 1 | Conservative [MW] |  |  | 1.8793 | 1.8795 | 1.8797 | 1.8799 | 1.8801 | 1.8821 | 1.8825 | 1.8826 | 1.883 | 1.8832 | 1.8836 | 1.884 | 1.8843 | 1.8847 | 1.8851 | 1.8854 | 1.8873 | 1.8892
|  |  |  | Best View [MW] |  |  | 1.8793 | 1.8795 | 1.8799 | 1.8801 | 1.8803 | 1.8825 | 1.8828 | 1.8832 | 1.8836 | 1.884 | 1.8845 | 1.8849 | 1.8854 | 1.886 | 1.8866 | 1.8871 | 1.8899 | 1.8927
|  |  |  | Base Case [MW] |  |  | 1.8793 | 1.8797 | 1.8799 | 1.8803 | 1.8806 | 1.8828 | 1.8832 | 1.8836 | 1.8841 | 1.8847 | 1.8853 | 1.8858 | 1.8864 | 1.8869 | 1.8877 | 1.8884 | 1.8921 | 1.8959
|  |  |  | Aggressive [MW] |  |  | 1.8793 | 1.8797 | 1.8803 | 1.8806 | 1.8812 | 1.8834 | 1.8841 | 1.8847 | 1.8854 | 1.8862 | 1.8871 | 1.888 | 1.889 | 1.8901 | 1.8912 | 1.8923 | 1.8979 | 1.9035
| MANOR STREET | 10 | 1 | Conservative [MW] |  |  | 14.6996 | 14.7655 | 14.8283 | 14.8914 | 14.96 | 15.0286 | 15.1103 | 15.1984 | 15.2886 | 15.3798 | 15.4721 | 15.5604 | 15.6542 | 15.7528 | 15.8465 | 15.9445 | 16.423 | 16.9023
|  |  |  | Best View [MW] |  |  | 14.6996 | 14.771 | 14.8428 | 14.9144 | 14.9852 | 15.0601 | 15.1693 | 15.2846 | 15.3966 | 15.5138 | 15.6314 | 15.7527 | 15.873 | 15.9962 | 16.1213 | 16.2525 | 16.8922 | 17.5329
|  |  |  | Base Case [MW] |  |  | 14.6996 | 14.7835 | 14.8664 | 14.9516 | 15.0386 | 15.1274 | 15.2578 | 15.3901 | 15.5229 | 15.6608 | 15.7976 | 15.9373 | 16.0837 | 16.2302 | 16.3752 | 16.5232 | 17.2553 | 17.988
|  |  |  | Aggressive [MW] |  |  | 14.6996 | 14.8303 | 14.9629 | 15.1007 | 15.2431 | 15.388 | 15.5467 | 15.7109 | 15.8801 | 16.0514 | 16.2277 | 16.4015 | 16.5811 | 16.7575 | 16.9327 | 17.1085 | 17.9861 | 18.8637
| MANORHAMILTON | 20 | 1 | Conservative [MW] |  |  | 4.4649 | 4.4792 | 4.4951 | 4.5077 | 4.522 | 4.5353 | 4.5628 | 4.592 | 4.6177 | 4.6448 | 4.6734 | 4.7004 | 4.7286 | 4.7548 | 4.7819 | 4.8096 | 4.9462 | 5.083
|  |  |  | Best View [MW] |  |  | 4.4649 | 4.4905 | 4.5136 | 4.5394 | 4.5624 | 4.5879 | 4.6226 | 4.6584 | 4.6954 | 4.7329 | 4.7678 | 4.8025 | 4.8394 | 4.872 | 4.9056 | 4.9365 | 5.0983 | 5.2596
|  |  |  | Base Case [MW] |  |  | 4.4649 | 4.4974 | 4.5282 | 4.5622 | 4.594 | 4.6259 | 4.6688 | 4.7126 | 4.7538 | 4.7973 | 4.8367 | 4.8769 | 4.9137 | 4.9523 | 4.9851 | 5.0136 | 5.1676 | 5.3209
|  |  |  | Aggressive [MW] |  |  | 4.4649 | 4.5142 | 4.5633 | 4.614 | 4.663 | 4.7119 | 4.7663 | 4.821 | 4.8714 | 4.9184 | 4.9658 | 5.0046 | 5.0333 | 5.0555 | 5.0621 | 5.0439 | 5.0192 | 4.9904
|  |  | 2 | Conservative [MW] |  |  | 1.3001 | 1.3004 | 1.3007 | 1.3009 | 1.3014 | 1.3016 | 1.3023 | 1.3029 | 1.3036 | 1.3043 | 1.3051 | 1.3058 | 1.3066 | 1.3075 | 1.3083 | 1.3093 | 1.3138 | 1.3184
|  |  |  | Best View [MW] |  |  | 1.3001 | 1.3005 | 1.3011 | 1.3016 | 1.3022 | 1.3029 | 1.3037 | 1.3047 | 1.3057 | 1.3068 | 1.3079 | 1.309 | 1.3103 | 1.3115 | 1.3129 | 1.3122 | 1.3143 | 1.3161
|  |  |  | Base Case [MW] |  |  | 1.3001 | 1.3008 | 1.3015 | 1.3022 | 1.303 | 1.3039 | 1.305 | 1.3061 | 1.3075 | 1.3087 | 1.3101 | 1.3117 | 1.3129 | 1.3118 | 1.3107 | 1.3092 | 1.3026 | 1.2959
|  |  |  | Aggressive [MW] |  |  | 1.3001 | 1.3011 | 1.3023 | 1.3035 | 1.3048 | 1.3062 | 1.3079 | 1.3096 | 1.3115 | 1.3128 | 1.3114 | 1.3099 | 1.3065 | 1.3039 | 1.3019 | 1.3 | 1.2902 | 1.2804
| MARROWBONE LANE | 10 | 1 | Conservative [MW] |  |  | 12.8201 | 12.8963 | 12.9747 | 13.0526 | 13.132 | 13.215 | 13.2874 | 13.3623 | 13.4393 | 13.516 | 13.5945 | 13.6718 | 13.7526 | 13.8315 | 13.9129 | 13.994 | 14.4002 | 14.8064
|  |  |  | Best View [MW] |  |  | 12.8201 | 12.9084 | 13.0007 | 13.0921 | 13.1866 | 13.2817 | 13.3662 | 13.4513 | 13.5363 | 13.6233 | 13.712 | 13.7994 | 13.8896 | 13.9796 | 14.072 | 14.1632 | 14.6225 | 15.0815
|  |  |  | Base Case [MW] |  |  | 12.8201 | 12.9248 | 13.0299 | 13.1374 | 13.2463 | 13.3611 | 13.4514 | 13.545 | 13.6411 | 13.7369 | 13.8338 | 13.9314 | 14.029 | 14.1281 | 14.2287 | 14.3268 | 14.8238 | 15.3204
|  |  |  | Aggressive [MW] |  |  | 12.8201 | 12.995 | 13.1775 | 13.3662 | 13.5612 | 13.765 | 13.8559 | 13.9488 | 14.0426 | 14.1377 | 14.2324 | 14.3266 | 14.4219 | 14.5147 | 14.6067 | 14.7004 | 15.1646 | 15.629
| MARSHES | 10 | 1 | Conservative [MW] |  |  | 12.0185 | 12.0763 | 12.1308 | 12.1907 | 12.2516 | 12.3133 | 12.3758 | 12.4425 | 12.5137 | 12.5848 | 12.6553 | 12.7258 | 12.7996 | 12.8772 | 12.954 | 13.0339 | 13.425 | 13.8166
|  |  |  | Best View [MW] |  |  | 12.0185 | 12.0803 | 12.1466 | 12.2087 | 12.2753 | 12.3463 | 12.4375 | 12.5335 | 12.6295 | 12.7255 | 12.8295 | 12.9324 | 13.0427 | 13.1508 | 13.2656 | 13.3766 | 13.9416 | 14.506
|  |  |  | Base Case [MW] |  |  | 12.0185 | 12.1104 | 12.2024 | 12.2986 | 12.3987 | 12.5018 | 12.6125 | 12.7206 | 12.8346 | 12.9537 | 13.073 | 13.2004 | 13.3264 | 13.4595 | 13.5889 | 13.7289 | 14.4006 | 15.074
|  |  |  | Aggressive [MW] |  |  | 12.0185 | 12.1403 | 12.2722 | 12.4048 | 12.5458 | 12.6896 | 12.8233 | 12.9581 | 13.1014 | 13.2481 | 13.3964 | 13.55 | 13.7076 | 13.8725 | 14.0376 | 14.2062 | 15.04 | 15.8744
|  | 20 | 1 | Conservative [MW] |  |  | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65
|  |  |  | Best View [MW] |  |  | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65
|  |  |  | Base Case [MW] |  |  | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65
|  |  |  | Aggressive [MW] |  |  | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65
| MAYFIELD | 10 | 1 | Conservative [MW] |  |  | 13.1592 | 13.2111 | 13.2603 | 13.3147 | 13.3663 | 13.4233 | 13.4798 | 13.5333 | 12.9995 | 13.0593 | 13.1165 | 13.1779 | 13.2403 | 13.3033 | 13.3708 | 13.4348 | 13.7641 | 14.0928
|  |  |  | Best View [MW] |  |  | 13.1592 | 13.214 | 13.2655 | 13.322 | 13.3796 | 13.4383 | 13.5133 | 13.5915 | 13.076 | 13.1592 | 13.2408 | 13.3282 | 13.4135 | 13.504 | 13.5957 | 13.692 | 14.1612 | 14.6311
|  |  |  | Base Case [MW] |  |  | 13.1592 | 13.2335 | 13.3103 | 13.3851 | 13.466 | 13.5491 | 13.6284 | 13.7057 | 13.198 | 13.2806 | 13.3684 | 13.4577 | 13.5485 | 13.6442 | 13.7404 | 13.8371 | 14.3193 | 14.8015
|  |  |  | Aggressive [MW] |  |  | 13.1592 | 13.2487 | 13.3455 | 13.4414 | 13.5444 | 13.6537 | 13.7543 | 13.862 | 13.3769 | 13.4925 | 13.6089 | 13.7298 | 13.8582 | 13.9859 | 14.1158 | 14.2552 | 14.9267 | 15.5998
| MCDONAGH | 10 | 1 | Conservative [MW] |  |  | 12.7317 | 12.769 | 12.805 | 12.8437 | 12.881 | 12.9211 | 12.9742 | 13.0327 | 13.0921 | 13.1564 | 13.2171 | 13.2782 | 13.3441 | 13.4103 | 13.4766 | 13.5473 | 13.8891 | 14.2316
|  |  |  | Best View [MW] |  |  | 12.7317 | 12.774 | 12.8225 | 12.869 | 12.9133 | 12.964 | 13.0415 | 13.1215 | 13.2039 | 13.2877 | 13.3735 | 13.4648 | 13.5571 | 13.6499 | 13.7475 | 13.8449 | 14.3323 | 14.8197
|  |  |  | Base Case [MW] |  |  | 12.7317 | 12.7827 | 12.839 | 12.8924 | 12.9512 | 13.0069 | 13.1017 | 13.196 | 13.2986 | 13.3996 | 13.5076 | 13.6178 | 13.7291 | 13.8461 | 13.9675 | 14.0929 | 14.7095 | 15.3267
|  |  |  | Aggressive [MW] |  |  | 12.7317 | 12.8178 | 12.9125 | 13.0072 | 13.1014 | 13.207 | 13.3293 | 13.4541 | 13.5849 | 13.7249 | 13.8645 | 14.011 | 14.1678 | 14.3243 | 14.4838 | 14.6539 | 15.476 | 16.2999
| MERRION SQUARE | 10 | 1 | Conservative [MW] |  |  | 15.0239 | 15.102 | 15.1784 | 15.2624 | 15.3442 | 15.4284 | 15.5031 | 15.581 | 15.6619 | 15.7412 | 15.8233 | 15.9083 | 15.9907 | 16.0799 | 16.1665 | 16.2594 | 16.7071 | 17.1559
|  |  |  | Best View [MW] |  |  | 15.0239 | 15.1171 | 15.2069 | 15.3015 | 15.3964 | 15.4953 | 15.5833 | 15.6728 | 15.7636 | 15.8558 | 15.9488 | 16.0422 | 16.1404 | 16.2434 | 16.341 | 16.4473 | 16.9556 | 17.4654
|  |  |  | Base Case [MW] |  |  | 15.0239 | 15.1284 | 15.2352 | 15.3484 | 15.4586 | 15.5786 | 15.6761 | 15.7733 | 15.875 | 15.9762 | 16.0807 | 16.1881 | 16.2984 | 16.4107 | 16.5245 | 16.6393 | 17.2106 | 17.782
|  |  |  | Aggressive [MW] |  |  | 15.0239 | 15.1999 | 15.3888 | 15.583 | 15.7891 | 16.0024 | 16.1048 | 16.2062 | 16.3109 | 16.4193 | 16.5252 | 16.6386 | 16.7479 | 16.8637 | 16.9747 | 17.0904 | 17.6561 | 18.2227
| MERVILLE | 10 | 1 | Conservative [MW] |  |  | 13.6659 | 13.7307 | 13.7986 | 13.8658 | 13.94 | 14.0124 | 14.0573 | 14.1004 | 14.1456 | 14.1931 | 14.2383 | 14.2857 | 14.3351 | 14.3821 | 14.4351 | 14.486 | 14.7461 | 15.0059
|  |  |  | Best View [MW] |  |  | 13.6659 | 13.7386 | 13.8135 | 13.8904 | 13.9691 | 14.0529 | 14.1046 | 14.1531 | 14.2079 | 14.2595 | 14.3168 | 14.3711 | 14.4308 | 14.4872 | 14.5449 | 14.6074 | 14.9071 | 15.2076
|  |  |  | Base Case [MW] |  |  | 13.6659 | 13.7418 | 13.8266 | 13.9125 | 14.0026 | 14.0962 | 14.154 | 14.2123 | 14.2712 | 14.3351 | 14.3995 | 14.4641 | 14.5288 | 14.5935 | 14.6669 | 14.7355 | 15.0913 | 15.4463
|  |  |  | Aggressive [MW] |  |  | 13.6659 | 13.7615 | 13.8626 | 13.9725 | 14.0867 | 14.204 | 14.2562 | 14.314 | 14.3686 | 14.4246 | 14.4815 | 14.5396 | 14.6029 | 14.6626 | 14.7271 | 14.7882 | 15.1026 | 15.4164
| MILFORD (MWR) | 10 | 1 | Conservative [MW] |  |  | 3.7216 | 3.7323 | 3.7426 | 3.7524 | 3.7638 | 3.7748 | 3.7859 | 3.7986 | 3.8107 | 3.8221 | 3.835 | 3.8494 | 3.8631 | 3.8761 | 3.8905 | 3.9042 | 3.9745 | 4.0447
|  |  |  | Best View [MW] |  |  | 3.7216 | 3.7336 | 3.7431 | 3.7542 | 3.7647 | 3.7769 | 3.7929 | 3.8079 | 3.8259 | 3.8428 | 3.8607 | 3.8774 | 3.8969 | 3.9152 | 3.9364 | 3.9562 | 4.0588 | 4.1612
|  |  |  | Base Case [MW] |  |  | 3.7216 | 3.7358 | 3.7493 | 3.7639 | 3.7797 | 3.7945 | 3.8133 | 3.8327 | 3.8527 | 3.8732 | 3.8943 | 3.9157 | 3.9375 | 3.9617 | 3.986 | 4.0105 | 4.1325 | 4.2546
|  |  |  | Aggressive [MW] |  |  | 3.7216 | 3.7432 | 3.7649 | 3.7887 | 3.8125 | 3.836 | 3.8587 | 3.8795 | 3.9026 | 3.928 | 3.9533 | 3.9785 | 4.0034 | 4.0323 | 4.0608 | 4.0885 | 4.2291 | 4.3696
|  | 20 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.020401 | 0.068763 | 0.11802 | 0.16811 | 0.21895 | 0.27059 | 0.32297 | 0.37622 | 0.43014 | 0.4848 | 0.54023 | 0.81532 | 1.0905
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.029607 | 0.094424 | 0.1608 | 0.22859 | 0.29772 | 0.36825 | 0.44012 | 0.51334 | 0.58777 | 0.66343 | 0.74028 | 1.1214 | 1.5027
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.04166 | 0.10433 | 0.18027 | 0.25807 | 0.33774 | 0.41906 | 0.5022 | 0.58701 | 0.67319 | 0.76109 | 0.85015 | 0.94043 | 1.3886 | 1.8369
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | 0.076393 | 0.17316 | 0.2729 | 0.35956 | 0.44832 | 0.53912 | 0.63172 | 0.72617 | 0.82215 | 0.91958 | 1.0182 | 1.1167 | 1.2157 | 1.7094 | 2.2033
| MILFORD (NR) | 10 | 1 | Conservative [MW] |  |  | 2.9706 | 2.996 | 3.0207 | 3.0484 | 3.0772 | 15.5106 | 15.5774 | 15.644 | 15.7135 | 15.7844 | 15.8581 | 15.9316 | 16.0062 | 16.0837 | 16.1669 | 16.2557 | 16.6845 | 17.1143
|  |  |  | Best View [MW] |  |  | 2.9706 | 3.0263 | 3.0902 | 3.1568 | 3.2249 | 15.6842 | 15.7829 | 15.8842 | 15.9896 | 16.0958 | 16.2155 | 16.3426 | 16.4727 | 16.6132 | 16.7607 | 16.9133 | 17.6627 | 18.4129
|  |  |  | Base Case [MW] |  |  | 2.9706 | 3.0321 | 3.1053 | 3.18 | 3.2564 | 15.7227 | 15.8382 | 15.959 | 16.0854 | 16.2239 | 16.3727 | 16.5261 | 16.6967 | 16.8744 | 17.0571 | 17.239 | 18.1505 | 19.0619
|  |  |  | Aggressive [MW] |  |  | 2.9706 | 3.0701 | 3.1832 | 3.2993 | 3.4199 | 15.9194 | 16.061 | 16.2189 | 16.3893 | 16.5705 | 16.7695 | 16.9794 | 17.1865 | 17.4039 | 17.6257 | 17.858 | 18.9914 | 20.1266
| MILLTOWN (SR) | 20 | 1 | Conservative [MW] |  |  | 3.8478 | 3.8924 | 3.9367 | 3.9823 | 4.0279 | 4.0749 | 4.1435 | 4.2139 | 4.2857 | 4.3593 | 4.4342 | 4.5102 | 4.5874 | 4.6665 | 4.7475 | 4.8295 | 5.2368 | 5.6443
|  |  |  | Best View [MW] |  |  | 3.8478 | 3.9022 | 3.9564 | 4.0124 | 4.0693 | 4.1268 | 4.2236 | 4.3234 | 4.4252 | 4.5304 | 4.638 | 4.7488 | 4.8623 | 4.9779 | 5.0972 | 5.219 | 5.8214 | 6.4242
|  |  |  | Base Case [MW] |  |  | 3.8478 | 3.9251 | 4.0037 | 4.0847 | 4.1671 | 4.2522 | 4.3524 | 4.4558 | 4.5614 | 4.6701 | 4.7819 | 4.8964 | 5.013 | 5.1332 | 5.257 | 5.3825 | 6.0053 | 6.6284
|  |  |  | Aggressive [MW] |  |  | 3.8478 | 3.9579 | 4.0721 | 4.19 | 4.3117 | 4.4382 | 4.5604 | 4.6875 | 4.8178 | 4.9527 | 5.0906 | 5.2329 | 5.3788 | 5.5286 | 5.6827 | 5.8402 | 6.6185 | 7.3974
| MILLTOWN MALBAY | 10 | 1 | Conservative [MW] |  |  | 3.8251 | 3.8392 | 3.8527 | 3.8655 | 3.8799 | 3.8935 | 3.9133 | 3.9318 | 3.9512 | 3.9714 | 3.9925 | 4.0143 | 4.0346 | 4.0556 | 4.0795 | 4.1017 | 4.2172 | 4.3325
|  |  |  | Best View [MW] |  |  | 3.8251 | 3.8407 | 3.8554 | 3.8694 | 3.8848 | 3.9015 | 3.9288 | 3.9556 | 3.9841 | 4.0143 | 4.0436 | 4.0743 | 4.1062 | 4.1391 | 4.1705 | 4.205 | 4.3694 | 4.5343
|  |  |  | Base Case [MW] |  |  | 3.8251 | 3.8476 | 3.8725 | 3.8975 | 3.9226 | 3.9476 | 3.978 | 4.0096 | 4.0421 | 4.0754 | 4.1093 | 4.1461 | 4.1806 | 4.2174 | 4.2564 | 4.2948 | 4.4884 | 4.6819
|  |  |  | Aggressive [MW] |  |  | 3.8251 | 3.8649 | 3.9075 | 3.9522 | 4.0011 | 4.0487 | 4.085 | 4.1213 | 4.1574 | 4.1978 | 4.2349 | 4.2758 | 4.3178 | 4.3602 | 4.4029 | 4.4452 | 4.6577 | 4.8701
| MOATE | 10 | 1 | Conservative [MW] |  |  | 5.7441 | 5.7601 | 5.7716 | 5.7866 | 5.8013 | 5.8155 | 5.8412 | 5.8658 | 5.8891 | 5.9153 | 5.9402 | 5.9679 | 5.9942 | 6.019 | 6.0467 | 6.0769 | 6.2212 | 6.3658
|  |  |  | Best View [MW] |  |  | 5.7441 | 5.7667 | 5.7882 | 5.8128 | 5.8321 | 5.8587 | 5.8925 | 5.9281 | 5.9652 | 5.9995 | 6.0394 | 6.0807 | 6.1188 | 6.162 | 6.2063 | 6.2513 | 6.4744 | 6.6976
|  |  |  | Base Case [MW] |  |  | 5.7441 | 5.775 | 5.8081 | 5.839 | 5.8719 | 5.9067 | 5.944 | 5.9824 | 6.026 | 6.0662 | 6.1113 | 6.157 | 6.203 | 6.2534 | 6.2995 | 6.3498 | 6.5899 | 6.8308
|  |  |  | Aggressive [MW] |  |  | 5.7441 | 5.7905 | 5.8404 | 5.8893 | 5.9454 | 5.9999 | 6.0463 | 6.0928 | 6.1434 | 6.1934 | 6.2428 | 6.3 | 6.356 | 6.4149 | 6.4718 | 6.5356 | 6.8363 | 7.1381
| MOHILL | 20 | 1 | Conservative [MW] |  |  | 6.3254 | 6.341 | 6.3561 | 6.3706 | 6.3847 | 6.4027 | 6.4321 | 6.464 | 6.4982 | 6.5305 | 6.5605 | 6.5975 | 6.6319 | 6.6687 | 6.703 | 6.7392 | 6.9152 | 7.0914
|  |  |  | Best View [MW] |  |  | 6.3254 | 6.3485 | 6.3787 | 6.4033 | 6.4307 | 6.4609 | 6.5031 | 6.5459 | 6.5895 | 6.6381 | 6.6827 | 6.7319 | 6.781 | 6.8345 | 6.883 | 6.9401 | 7.2028 | 7.4669
|  |  |  | Base Case [MW] |  |  | 6.3254 | 6.3567 | 6.3942 | 6.4293 | 6.466 | 6.5044 | 6.556 | 6.6111 | 6.6654 | 6.7227 | 6.7783 | 6.8412 | 6.9015 | 6.9639 | 7.0277 | 7.0973 | 7.4299 | 7.7634
|  |  |  | Aggressive [MW] |  |  | 6.3254 | 6.3775 | 6.4324 | 6.4898 | 6.5493 | 6.6106 | 6.6819 | 6.7527 | 6.8314 | 6.9081 | 6.9913 | 7.0756 | 7.1599 | 7.248 | 7.344 | 7.4365 | 7.9082 | 8.3793
| MONEENAGHIESHA | 10 | 1 | Conservative [MW] |  |  | 14.9127 | 14.9634 | 15.0163 | 15.0663 | 15.1226 | 15.1766 | 15.2511 | 15.3244 | 15.4017 | 15.4821 | 15.5611 | 15.6383 | 15.7235 | 15.8062 | 15.8916 | 15.974 | 16.3941 | 16.8137
|  |  |  | Best View [MW] |  |  | 14.9127 | 14.9764 | 15.041 | 15.1101 | 15.1748 | 15.2442 | 15.3521 | 15.4581 | 15.5707 | 15.6852 | 15.8004 | 15.9206 | 16.0404 | 16.1642 | 16.291 | 16.4149 | 17.0422 | 17.669
|  |  |  | Base Case [MW] |  |  | 14.9127 | 14.9928 | 15.0795 | 15.1641 | 15.2505 | 15.3388 | 15.4561 | 15.5782 | 15.704 | 15.8279 | 15.9592 | 16.0916 | 16.2292 | 16.3662 | 16.5068 | 16.6499 | 17.3587 | 18.0678
|  |  |  | Aggressive [MW] |  |  | 14.9127 | 15.0404 | 15.1743 | 15.3088 | 15.4518 | 15.5979 | 15.7389 | 15.8874 | 16.0373 | 16.1919 | 16.3495 | 16.5091 | 16.6745 | 16.8426 | 17.0073 | 17.1809 | 18.0251 | 18.8707
| MONEYCOOLEY | 10 | 1 | Conservative [MW] |  |  | 27.5811 | 27.8128 | 28.0518 | 28.2898 | 28.5387 | 28.7832 | 28.931 | 29.0744 | 29.2274 | 29.3752 | 29.5245 | 29.6756 | 29.8275 | 29.9798 | 30.1326 | 30.292 | 31.0712 | 31.8516
|  |  |  | Best View [MW] |  |  | 27.5811 | 27.8365 | 28.0998 | 28.3695 | 28.6425 | 28.9177 | 29.0859 | 29.2528 | 29.4249 | 29.5948 | 29.7691 | 29.9471 | 30.1211 | 30.3042 | 30.4804 | 30.6576 | 31.5409 | 32.4243
|  |  |  | Base Case [MW] |  |  | 27.5811 | 27.8633 | 28.153 | 28.4483 | 28.7522 | 29.0565 | 29.2429 | 29.4383 | 29.6334 | 29.8286 | 30.0218 | 30.2207 | 30.4223 | 30.6196 | 30.8259 | 31.0258 | 32.0423 | 33.0577
|  |  |  | Aggressive [MW] |  |  | 27.5811 | 27.9278 | 28.2819 | 28.6522 | 29.026 | 29.4074 | 29.5801 | 29.7568 | 29.9303 | 30.1072 | 30.2858 | 30.4657 | 30.6389 | 30.82 | 30.9918 | 31.171 | 32.0472 | 32.9247
| MONFIN | 10 | 1 | Conservative [MW] |  |  | 2.4502 | 2.4543 | 2.4626 | 2.4685 | 2.4742 | 2.4818 | 2.4962 | 2.5116 | 2.528 | 2.5431 | 2.5613 | 2.578 | 2.5956 | 2.6139 | 2.6329 | 2.6501 | 2.7408 | 2.8312
|  |  |  | Best View [MW] |  |  | 2.4502 | 2.4594 | 2.4702 | 2.4826 | 2.4943 | 2.5053 | 2.5234 | 2.5401 | 2.5596 | 2.5774 | 2.5958 | 2.6169 | 2.6361 | 2.6578 | 2.6774 | 2.6994 | 2.8029 | 2.9069
|  |  |  | Base Case [MW] |  |  | 2.4502 | 2.4627 | 2.4765 | 2.4894 | 2.5057 | 2.5187 | 2.5382 | 2.5582 | 2.5783 | 2.601 | 2.6213 | 2.6439 | 2.6663 | 2.6907 | 2.7147 | 2.7381 | 2.8567 | 2.9753
|  |  |  | Aggressive [MW] |  |  | 2.4502 | 2.4702 | 2.4923 | 2.5142 | 2.5379 | 2.5611 | 2.5907 | 2.6208 | 2.6509 | 2.6832 | 2.7149 | 2.7482 | 2.7849 | 2.8199 | 2.8575 | 2.8951 | 3.0832 | 3.2712
| MONKSTOWN | 10 | 1 | Conservative [MW] |  |  | 12.8076 | 12.886 | 12.9591 | 13.0392 | 13.1177 | 13.2032 | 13.2639 | 13.3295 | 13.3954 | 13.4619 | 13.5327 | 13.6038 | 13.67 | 13.7452 | 13.8155 | 13.8894 | 14.2494 | 14.6099
|  |  |  | Best View [MW] |  |  | 12.8076 | 12.8946 | 12.9832 | 13.0769 | 13.171 | 13.2657 | 13.3445 | 13.4224 | 13.4987 | 13.578 | 13.6601 | 13.7451 | 13.8324 | 13.9172 | 14.0035 | 14.0966 | 14.5441 | 14.9927
|  |  |  | Base Case [MW] |  |  | 12.8076 | 12.9055 | 13.0072 | 13.1118 | 13.2193 | 13.3289 | 13.4119 | 13.5007 | 13.5913 | 13.6831 | 13.7805 | 13.8734 | 13.9717 | 14.074 | 14.1758 | 14.2766 | 14.7834 | 15.2899
|  |  |  | Aggressive [MW] |  |  | 12.8076 | 12.9498 | 13.0981 | 13.2554 | 13.4152 | 13.5852 | 13.6688 | 13.759 | 13.8507 | 13.9389 | 14.0332 | 14.1274 | 14.2271 | 14.3268 | 14.4262 | 14.5244 | 15.0186 | 15.5126
| MORNINGTON ROAD | 10 | 1 | Conservative [MW] |  |  | 13.2365 | 13.2957 | 13.3522 | 13.4094 | 13.4679 | 13.5317 | 13.2133 | 13.2969 | 13.3786 | 13.4627 | 13.5488 | 13.6406 | 13.7299 | 13.8205 | 13.9163 | 14.0127 | 14.4932 | 14.9738
|  |  |  | Best View [MW] |  |  | 13.2365 | 13.304 | 13.3713 | 13.443 | 13.5145 | 13.5851 | 13.2902 | 13.3934 | 13.4997 | 13.6123 | 13.7229 | 13.8393 | 13.9564 | 14.0783 | 14.1999 | 14.329 | 14.9547 | 15.5816
|  |  |  | Base Case [MW] |  |  | 13.2365 | 13.3311 | 13.43 | 13.5287 | 13.6306 | 13.7355 | 13.4649 | 13.592 | 13.7252 | 13.8601 | 13.9996 | 14.1428 | 14.2932 | 14.4408 | 14.5978 | 14.7581 | 15.551 | 16.3444
|  |  |  | Aggressive [MW] |  |  | 13.2365 | 13.3662 | 13.4973 | 13.6327 | 13.7763 | 13.9262 | 13.696 | 13.869 | 14.0451 | 14.2309 | 14.4201 | 14.6189 | 14.8197 | 15.0236 | 15.232 | 15.4462 | 16.5016 | 17.5579
| MORRISTOWN | 10 | 1 | Conservative [MW] |  |  | 6.577 | 6.6093 | 6.6489 | 6.681 | 6.7201 | 18.3436 | 18.2717 | 18.3355 | 18.3982 | 18.4622 | 18.5304 | 18.5998 | 18.6706 | 18.7425 | 18.8155 | 18.8898 | 19.2578 | 19.6259
|  |  |  | Best View [MW] |  |  | 6.577 | 6.6204 | 6.6648 | 6.7099 | 6.7604 | 18.4262 | 18.3566 | 18.4413 | 18.5291 | 18.6173 | 18.7113 | 18.8085 | 18.9086 | 19.0112 | 19.1166 | 19.2243 | 19.7566 | 20.2892
|  |  |  | Base Case [MW] |  |  | 6.577 | 6.6292 | 6.6808 | 6.736 | 6.7948 | 18.5052 | 18.4316 | 18.5319 | 18.6374 | 18.7478 | 18.8602 | 18.9774 | 19.0994 | 19.2254 | 19.3588 | 19.4928 | 20.1613 | 20.8298
|  |  |  | Aggressive [MW] |  |  | 6.577 | 6.6422 | 6.7126 | 6.7875 | 6.8567 | 18.6486 | 18.5455 | 18.675 | 18.8112 | 18.9535 | 19.1019 | 19.259 | 19.4213 | 19.5886 | 19.7665 | 19.9549 | 20.869 | 21.7848
| MOUNT MERRION | 10 | 1 | Conservative [MW] |  |  | 12.7383 | 12.802 | 12.8698 | 12.9373 | 13.0089 | 11.8899 | 11.9466 | 12.0046 | 12.0637 | 12.1237 | 12.1819 | 12.244 | 12.3072 | 12.371 | 12.4357 | 12.5012 | 12.8263 | 13.1516
|  |  |  | Best View [MW] |  |  | 12.7383 | 12.815 | 12.8905 | 12.9681 | 13.0521 | 11.9484 | 12.0157 | 12.0834 | 12.1545 | 12.2261 | 12.2975 | 12.3721 | 12.4499 | 12.5274 | 12.6044 | 12.6875 | 13.087 | 13.4875
|  |  |  | Base Case [MW] |  |  | 12.7383 | 12.8215 | 12.9099 | 12.9993 | 13.093 | 12.0021 | 12.0784 | 12.1577 | 12.2363 | 12.3174 | 12.4009 | 12.4865 | 12.5739 | 12.6669 | 12.7577 | 12.8501 | 13.3079 | 13.766
|  |  |  | Aggressive [MW] |  |  | 12.7383 | 12.8615 | 12.9898 | 13.1267 | 13.267 | 12.2303 | 12.3056 | 12.3838 | 12.4644 | 12.548 | 12.6303 | 12.7182 | 12.805 | 12.8936 | 12.9839 | 13.0755 | 13.5299 | 13.9846
| MOUNT MISERY | 10 | 1 | Conservative [MW] |  |  | 8.4092 | 8.4593 | 8.5112 | 8.5642 | 8.6186 | 8.6726 | 8.7443 | 8.817 | 8.8908 | 8.9655 | 9.0424 | 9.1216 | 9.2016 | 9.2822 | 9.3665 | 9.4513 | 9.8739 | 10.2965
|  |  |  | Best View [MW] |  |  | 8.4092 | 8.4649 | 8.5224 | 8.581 | 8.6407 | 8.7017 | 8.7924 | 8.8868 | 8.9817 | 9.0801 | 9.1802 | 9.2836 | 9.39 | 9.4978 | 9.6086 | 9.7237 | 10.2876 | 10.8522
|  |  |  | Base Case [MW] |  |  | 8.4092 | 8.4748 | 8.5433 | 8.613 | 8.6836 | 8.7568 | 8.8636 | 8.9736 | 9.0868 | 9.2028 | 9.3231 | 9.4475 | 9.5742 | 9.7046 | 9.8367 | 9.9755 | 10.6516 | 11.3288
|  |  |  | Aggressive [MW] |  |  | 8.4092 | 8.514 | 8.6227 | 8.7361 | 8.8527 | 8.9736 | 9.1096 | 9.2506 | 9.3951 | 9.5457 | 9.7005 | 9.8607 | 10.0257 | 10.1951 | 10.3699 | 10.5472 | 11.4269 | 12.3071
| MOUNTGORRY | 10 | 1 | Conservative [MW] |  |  | 13.4297 | 13.5312 | 13.6396 | 13.7464 | 13.8599 | 13.5835 | 13.6497 | 13.7161 | 13.783 | 13.8542 | 13.9256 | 13.9966 | 14.0677 | 14.1425 | 14.2121 | 14.2902 | 14.6581 | 15.0274
|  |  |  | Best View [MW] |  |  | 13.4297 | 13.5411 | 13.6614 | 13.7823 | 13.9072 | 13.6436 | 13.7207 | 13.7967 | 13.876 | 13.9578 | 14.0427 | 14.1256 | 14.2064 | 14.2939 | 14.3787 | 14.4697 | 14.9081 | 15.3476
|  |  |  | Base Case [MW] |  |  | 13.4297 | 13.5538 | 13.6844 | 13.8172 | 13.9547 | 13.7058 | 13.793 | 13.882 | 13.9765 | 14.0677 | 14.1601 | 14.2573 | 14.3544 | 14.4517 | 14.5529 | 14.6536 | 15.1584 | 15.6632
|  |  |  | Aggressive [MW] |  |  | 13.4297 | 13.5831 | 13.7434 | 13.9107 | 14.0823 | 13.8709 | 13.9537 | 14.0349 | 14.1191 | 14.2008 | 14.2848 | 14.3707 | 14.4584 | 14.5479 | 14.6384 | 14.7299 | 15.1847 | 15.6397
|  | 20 | 1 | Conservative [MW] |  |  | 0 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683
|  |  |  | Best View [MW] |  |  | 0 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683
|  |  |  | Base Case [MW] |  |  | 0 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683
|  |  |  | Aggressive [MW] |  |  | 0 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683 | 10.683
| MOUNTMELLICK | 10 | 1 | Conservative [MW] |  |  | 6.3945 | 6.4198 | 6.4438 | 6.4706 | 6.5009 | 6.1309 | 6.1686 | 6.2079 | 6.2485 | 6.2905 | 6.3339 | 6.3746 | 6.4204 | 6.4633 | 6.507 | 6.5555 | 6.7852 | 7.0158
|  |  |  | Best View [MW] |  |  | 6.3945 | 6.4241 | 6.4563 | 6.4906 | 6.523 | 6.1637 | 6.2133 | 6.263 | 6.3163 | 6.3693 | 6.4257 | 6.4811 | 6.5397 | 6.601 | 6.6607 | 6.7227 | 7.0268 | 7.3313
|  |  |  | Base Case [MW] |  |  | 6.3945 | 6.4346 | 6.4718 | 6.51 | 6.5545 | 6.2017 | 6.2613 | 6.3232 | 6.387 | 6.4523 | 6.5189 | 6.5904 | 6.6582 | 6.7301 | 6.8056 | 6.88 | 7.2552 | 7.6301
|  |  |  | Aggressive [MW] |  |  | 6.3945 | 6.454 | 6.5197 | 6.5815 | 6.649 | 6.3244 | 6.4075 | 6.4921 | 6.581 | 6.6736 | 6.769 | 6.8617 | 6.9633 | 7.064 | 7.1666 | 7.2698 | 7.7843 | 8.2988
| MOUNTRATH | 10 | 1 | Conservative [MW] |  |  | 6.3421 | 6.3634 | 6.3836 | 6.4073 | 6.4301 | 6.4562 | 6.4902 | 6.5219 | 6.5558 | 6.5919 | 6.6301 | 6.666 | 6.7037 | 6.7433 | 6.7802 | 6.8187 | 7.0069 | 7.1953
|  |  |  | Best View [MW] |  |  | 6.3421 | 6.3693 | 6.3949 | 6.4236 | 6.4549 | 6.4849 | 6.5306 | 6.585 | 6.6346 | 6.688 | 6.7407 | 6.7966 | 6.8558 | 6.9133 | 6.9736 | 7.036 | 7.3423 | 7.649
|  |  |  | Base Case [MW] |  |  | 6.3421 | 6.3787 | 6.4168 | 6.4566 | 6.4935 | 6.5364 | 6.5912 | 6.6446 | 6.7014 | 6.761 | 6.8231 | 6.8828 | 6.9491 | 7.0122 | 7.0812 | 7.1461 | 7.4814 | 7.816
|  |  |  | Aggressive [MW] |  |  | 6.3421 | 6.4011 | 6.462 | 6.5246 | 6.5885 | 6.6576 | 6.7178 | 6.7842 | 6.8517 | 6.9198 | 6.9882 | 7.0611 | 7.1379 | 7.2132 | 7.2911 | 7.3662 | 7.7491 | 8.1316
| MOVILLE | 20 | 1 | Conservative [MW] |  |  | 2.3027 | 2.3124 | 2.3219 | 2.3318 | 2.3418 | 2.3514 | 2.3754 | 2.3993 | 2.424 | 2.4491 | 2.4749 | 2.5011 | 2.5281 | 2.5555 | 2.5837 | 2.6123 | 2.7544 | 2.8965
|  |  |  | Best View [MW] |  |  | 2.3027 | 2.3242 | 2.3455 | 2.3681 | 2.3905 | 2.4137 | 2.4486 | 2.4847 | 2.5214 | 2.5598 | 2.5995 | 2.6397 | 2.6811 | 2.7244 | 2.7682 | 2.8139 | 3.0374 | 3.2612
|  |  |  | Base Case [MW] |  |  | 2.3027 | 2.3263 | 2.3508 | 2.3756 | 2.4008 | 2.4269 | 2.4686 | 2.5111 | 2.5556 | 2.6015 | 2.6494 | 2.6988 | 2.7496 | 2.8017 | 2.8566 | 2.9121 | 3.1881 | 3.4643
|  |  |  | Aggressive [MW] |  |  | 2.3027 | 2.339 | 2.3762 | 2.4152 | 2.455 | 2.4966 | 2.5472 | 2.6 | 2.6551 | 2.7119 | 2.771 | 2.8323 | 2.8967 | 2.9626 | 3.0314 | 3.1024 | 3.4518 | 3.8016
| MOY | 20 | 1 | Conservative [MW] |  |  | 11.5434 | 11.5675 | 11.594 | 11.62 | 11.646 | 11.6715 | 11.7576 | 11.8458 | 11.9331 | 12.0249 | 12.1156 | 12.2105 | 12.3068 | 12.4011 | 12.5021 | 12.6009 | 13.1005 | 13.5999
|  |  |  | Best View [MW] |  |  | 11.5434 | 11.6008 | 11.6593 | 11.7164 | 11.7772 | 11.8366 | 11.947 | 12.0625 | 12.1773 | 12.2965 | 12.4171 | 12.5416 | 12.6663 | 12.7941 | 12.9243 | 13.0562 | 13.7112 | 14.3665
|  |  |  | Base Case [MW] |  |  | 11.5434 | 11.6202 | 11.6971 | 11.7765 | 11.8585 | 11.9403 | 12.0725 | 12.2098 | 12.3518 | 12.4948 | 12.6443 | 12.7931 | 12.9467 | 13.101 | 13.2584 | 13.4173 | 14.2077 | 14.9984
|  |  |  | Aggressive [MW] |  |  | 11.5434 | 11.6894 | 11.8416 | 11.9966 | 12.1592 | 12.3257 | 12.516 | 12.7096 | 12.9111 | 13.1152 | 13.3227 | 13.5342 | 13.7466 | 13.96 | 14.1734 | 14.3827 | 15.4402 | 16.4969
| MOYLISH | 10 | 1 | Conservative [MW] |  |  | 6.6287 | 6.649 | 6.6684 | 6.6871 | 6.7048 | 6.726 | 6.7462 | 6.7694 | 6.7957 | 6.8165 | 6.8405 | 6.8674 | 6.8929 | 6.9171 | 6.9441 | 6.9742 | 7.1166 | 7.2596
|  |  |  | Best View [MW] |  |  | 6.6287 | 6.6481 | 6.6667 | 6.6885 | 6.7095 | 6.7297 | 6.7596 | 6.7876 | 6.8217 | 6.8537 | 6.8875 | 6.9231 | 6.9605 | 6.9953 | 7.0358 | 7.0735 | 7.2697 | 7.4653
|  |  |  | Base Case [MW] |  |  | 6.6287 | 6.6558 | 6.6814 | 6.7094 | 6.7399 | 6.7686 | 6.8037 | 6.8401 | 6.8778 | 6.9208 | 6.9604 | 7.0008 | 7.0463 | 7.0922 | 7.1385 | 7.1847 | 7.416 | 7.6472
|  |  |  | Aggressive [MW] |  |  | 6.6287 | 6.6718 | 6.7147 | 6.7616 | 6.8081 | 6.858 | 6.9039 | 6.9461 | 6.9928 | 7.0394 | 7.0901 | 7.1406 | 7.1903 | 7.2478 | 7.304 | 7.3587 | 7.6362 | 7.9134
| MULGANNON | 10 | 1 | Conservative [MW] |  |  | 15.833 | 15.8819 | 15.9382 | 15.9851 | 16.0393 | 16.0902 | 16.2097 | 16.3286 | 16.4515 | 16.5666 | 16.6834 | 16.8016 | 16.9127 | 17.0219 | 17.1263 | 17.23 | 17.7502 | 18.2703
|  |  |  | Best View [MW] |  |  | 15.833 | 15.9238 | 16.0147 | 16.105 | 16.1946 | 16.2883 | 16.4166 | 16.544 | 16.6748 | 16.7959 | 16.917 | 17.0356 | 17.1492 | 17.255 | 17.3508 | 17.4387 | 17.8993 | 18.3587
|  |  |  | Base Case [MW] |  |  | 15.833 | 15.9426 | 16.0515 | 16.1644 | 16.2756 | 16.3895 | 16.532 | 16.6721 | 16.807 | 16.9407 | 17.0696 | 17.1897 | 17.3052 | 17.4045 | 17.4904 | 17.5695 | 17.983 | 18.3955
|  |  |  | Aggressive [MW] |  |  | 15.833 | 16.0026 | 16.179 | 16.3494 | 16.5252 | 16.6928 | 16.8798 | 17.0591 | 17.2273 | 17.3754 | 17.4997 | 17.5932 | 17.6525 | 17.6491 | 17.5564 | 17.3348 | 16.5707 | 15.7851
| MULLAGH | 10 | 1 | Conservative [MW] |  |  | 6.2871 | 6.2879 | 6.2923 | 6.293 | 6.2973 | 6.2979 | 6.3009 | 6.3038 | 6.3102 | 6.3129 | 6.3154 | 6.3215 | 6.3236 | 6.3294 | 6.3314 | 6.3369 | 6.3549 | 6.3735
|  |  |  | Best View [MW] |  |  | 6.2871 | 6.2907 | 6.2943 | 6.2941 | 6.2975 | 6.3008 | 6.3057 | 6.3104 | 6.3149 | 6.3227 | 6.3266 | 6.3341 | 6.3375 | 6.3442 | 6.3508 | 6.357 | 6.3888 | 6.4206
|  |  |  | Base Case [MW] |  |  | 6.2871 | 6.2898 | 6.2924 | 6.2986 | 6.3009 | 6.3067 | 6.3108 | 6.3184 | 6.3218 | 6.3287 | 6.3353 | 6.3416 | 6.3474 | 6.353 | 6.3617 | 6.3702 | 6.4132 | 6.4562
|  |  |  | Aggressive [MW] |  |  | 6.2871 | 6.2909 | 6.2982 | 6.305 | 6.3115 | 6.3175 | 6.323 | 6.3319 | 6.3403 | 6.3481 | 6.3555 | 6.3622 | 6.3721 | 6.3815 | 6.3938 | 6.4017 | 6.4532 | 6.5039
|  |  | 2 | Conservative [MW] |  |  | 3.9285 | 3.9395 | 3.9521 | 3.9641 | 3.9777 | 3.9908 | 4.0099 | 4.0277 | 4.0465 | 4.0663 | 4.0847 | 4.1063 | 4.1264 | 4.1472 | 4.1688 | 4.1887 | 4.2925 | 4.3961
|  |  |  | Best View [MW] |  |  | 3.9285 | 3.9429 | 3.9586 | 3.9756 | 3.9916 | 4.0087 | 4.0355 | 4.06 | 4.0865 | 4.1149 | 4.1427 | 4.1724 | 4.2012 | 4.2315 | 4.2631 | 4.2957 | 4.4561 | 4.6167
|  |  |  | Base Case [MW] |  |  | 3.9285 | 3.9477 | 3.9678 | 3.9885 | 4.0099 | 4.0297 | 4.0597 | 4.089 | 4.1175 | 4.1495 | 4.1824 | 4.214 | 4.2486 | 4.2837 | 4.3191 | 4.3546 | 4.5318 | 4.7091
|  |  |  | Aggressive [MW] |  |  | 3.9285 | 3.9572 | 3.9891 | 4.0217 | 4.0568 | 4.0922 | 4.1277 | 4.165 | 4.204 | 4.2467 | 4.2879 | 4.33 | 4.3746 | 4.4215 | 4.4675 | 4.5173 | 4.7563 | 4.9959
| NAAS | 10 | 1 | Conservative [MW] |  |  | 13.4889 | 13.5908 | 13.6961 | 13.8041 | 13.9101 | 13.7281 | 13.8105 | 13.8962 | 13.984 | 14.0681 | 14.1582 | 14.2445 | 14.3363 | 14.4231 | 14.5149 | 14.601 | 15.0468 | 15.4917
|  |  |  | Best View [MW] |  |  | 13.4889 | 13.6087 | 13.7282 | 13.8512 | 13.9775 | 13.8166 | 13.914 | 14.0164 | 14.1176 | 14.221 | 14.322 | 14.4245 | 14.5336 | 14.6376 | 14.7418 | 14.8451 | 15.364 | 15.8828
|  |  |  | Base Case [MW] |  |  | 13.4889 | 13.6259 | 13.7586 | 13.9004 | 14.0403 | 13.8939 | 14.0079 | 14.1194 | 14.2352 | 14.3501 | 14.4682 | 14.5836 | 14.7004 | 14.8177 | 14.9354 | 15.0515 | 15.6363 | 16.2208
|  |  |  | Aggressive [MW] |  |  | 13.4889 | 13.6837 | 13.8861 | 14.0886 | 14.3017 | 14.2254 | 14.3329 | 14.4407 | 14.5535 | 14.6646 | 14.7736 | 14.8853 | 14.9933 | 15.1021 | 15.2054 | 15.3127 | 15.8387 | 16.3653
| NENAGH | 10 | 1 | Conservative [MW] |  |  | 10.2377 | 10.279 | 10.32 | 10.3608 | 10.403 | 10.4467 | 10.5064 | 10.5691 | 10.6329 | 10.6976 | 10.7632 | 10.8318 | 10.8991 | 10.9692 | 11.0422 | 11.1137 | 11.475 | 11.8361
|  |  |  | Best View [MW] |  |  | 10.2377 | 10.289 | 10.3399 | 10.3904 | 10.4438 | 10.4968 | 10.5874 | 10.6781 | 10.7745 | 10.8706 | 10.9724 | 11.0754 | 11.1816 | 11.2909 | 11.403 | 11.5177 | 12.084 | 12.6509
|  |  |  | Base Case [MW] |  |  | 10.2377 | 10.3059 | 10.3749 | 10.445 | 10.5176 | 10.5928 | 10.6904 | 10.7935 | 10.8979 | 11.0076 | 11.118 | 11.2332 | 11.3509 | 11.4705 | 11.5966 | 11.724 | 12.3575 | 12.9912
|  |  |  | Aggressive [MW] |  |  | 10.2377 | 10.3455 | 10.4548 | 10.5706 | 10.6891 | 10.8139 | 10.9291 | 11.0488 | 11.1706 | 11.2986 | 11.4302 | 11.5651 | 11.7025 | 11.8447 | 11.991 | 12.141 | 12.8811 | 13.6219
|  | 20 | 1 | Conservative [MW] |  |  | 0.16239 | 0.16421 | 0.16613 | 0.16795 | 0.16987 | 0.17179 | 0.17457 | 0.17745 | 0.18042 | 0.18339 | 0.18646 | 0.18963 | 0.1929 | 0.19616 | 0.19961 | 0.20306 | 0.22032 | 0.23758
|  |  |  | Best View [MW] |  |  | 0.16239 | 0.16469 | 0.167 | 0.1693 | 0.1717 | 0.17419 | 0.17831 | 0.18253 | 0.18695 | 0.19155 | 0.19626 | 0.20124 | 0.20634 | 0.21161 | 0.21708 | 0.22284 | 0.25088 | 0.27896
|  |  |  | Base Case [MW] |  |  | 0.16239 | 0.16546 | 0.16863 | 0.17179 | 0.17515 | 0.1785 | 0.18311 | 0.1879 | 0.1928 | 0.19789 | 0.20326 | 0.20883 | 0.21459 | 0.22054 | 0.22651 | 0.23294 | 0.26387 | 0.29488
|  |  |  | Aggressive [MW] |  |  | 0.16239 | 0.16719 | 0.17227 | 0.17754 | 0.18301 | 0.18886 | 0.19424 | 0.1999 | 0.20585 | 0.212 | 0.21843 | 0.22505 | 0.23188 | 0.23955 | 0.24771 | 0.25623 | 0.29786 | 0.33955
| NEW CASTLEBAR | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979 | 20.1979
| NEW GURRANEBANE | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694 | 12.6694
| NEW KILMONEY-CARRIGALINE STATION | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 18.525 | 19.0041 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 18.525 | 19.0041 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 18.525 | 19.0041 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 18.525 | 19.0041 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756 | 19.4756
| NEW TINAHASK | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041 | 19.0041
| NEWBROOK | 10 | 1 | Conservative [MW] |  |  | 4.4076 | 4.4244 | 4.4425 | 4.4594 | 4.4774 | 4.4944 | 4.5273 | 4.5652 | 4.5993 | 4.6351 | 4.6695 | 4.7048 | 4.7407 | 4.7766 | 4.8123 | 4.844 | 5.0129 | 5.1812
|  |  |  | Best View [MW] |  |  | 4.4076 | 4.4315 | 4.4532 | 4.4754 | 4.4953 | 4.5183 | 4.5577 | 4.5999 | 4.6391 | 4.6803 | 4.7201 | 4.7607 | 4.8015 | 4.8388 | 4.8745 | 4.9106 | 5.09 | 5.2695
|  |  |  | Base Case [MW] |  |  | 4.4076 | 4.45 | 4.4922 | 4.5367 | 4.5776 | 4.6223 | 4.6638 | 4.7065 | 4.7467 | 4.7896 | 4.8284 | 4.868 | 4.9016 | 4.9364 | 4.9654 | 4.9938 | 5.1373 | 5.2807
|  |  |  | Aggressive [MW] |  |  | 4.4076 | 4.4677 | 4.5255 | 4.5852 | 4.6456 | 4.7048 | 4.7509 | 4.799 | 4.8446 | 4.8864 | 4.9254 | 4.9631 | 4.9909 | 5.0127 | 5.0306 | 5.0338 | 5.0889 | 5.1416
| NEWCASTLEWEST | 10 | 1 | Conservative [MW] |  |  | 6.3556 | 6.3911 | 6.4247 | 6.4562 | 6.4944 | 6.5259 | 6.5667 | 6.6049 | 6.6447 | 6.6862 | 6.7246 | 6.7692 | 6.8103 | 6.8528 | 6.8963 | 6.941 | 7.1612 | 7.3816
|  |  |  | Best View [MW] |  |  | 6.3556 | 6.3923 | 6.4268 | 6.4634 | 6.4977 | 6.5342 | 6.586 | 6.6374 | 6.6928 | 6.7472 | 6.8052 | 6.862 | 6.9169 | 6.9795 | 7.0399 | 7.0977 | 7.3937 | 7.6892
|  |  |  | Base Case [MW] |  |  | 6.3556 | 6.4012 | 6.4475 | 6.4941 | 6.5456 | 6.5927 | 6.6551 | 6.7154 | 6.7821 | 6.846 | 6.9111 | 6.9769 | 7.0483 | 7.1145 | 7.185 | 7.2594 | 7.6211 | 7.9834
|  |  |  | Aggressive [MW] |  |  | 6.3556 | 6.4271 | 6.4985 | 6.5737 | 6.6476 | 6.7286 | 6.7972 | 6.866 | 6.9391 | 7.0115 | 7.0872 | 7.1657 | 7.2414 | 7.3182 | 7.401 | 7.4783 | 7.8794 | 8.2796
| NEWMARKET (DR) | 10 | 1 | Conservative [MW] |  |  | 8.6303 | 8.684 | 8.7372 | 8.792 | 8.8481 | 8.9056 | 8.956 | 9.0087 | 9.0606 | 9.1143 | 9.1669 | 9.221 | 9.2759 | 9.3316 | 9.3853 | 9.4417 | 9.7166 | 9.9919
|  |  |  | Best View [MW] |  |  | 8.6303 | 8.6919 | 8.7556 | 8.8189 | 8.8838 | 8.9525 | 9.01 | 9.0683 | 9.1268 | 9.1876 | 9.2482 | 9.3079 | 9.3691 | 9.4316 | 9.4947 | 9.5579 | 9.8738 | 10.1896
|  |  |  | Base Case [MW] |  |  | 8.6303 | 8.7032 | 8.7757 | 8.8498 | 8.9271 | 9.005 | 9.0705 | 9.1349 | 9.198 | 9.2642 | 9.3305 | 9.3991 | 9.4669 | 9.5332 | 9.6032 | 9.6703 | 10.0134 | 10.3561
|  |  |  | Aggressive [MW] |  |  | 8.6303 | 8.751 | 8.8785 | 9.01 | 9.1447 | 9.2828 | 9.3466 | 9.4111 | 9.4758 | 9.5402 | 9.6037 | 9.6686 | 9.7313 | 9.7961 | 9.8571 | 9.9166 | 10.2183 | 10.5196
| NEWMARKET (SR) | 10 | 1 | Conservative [MW] |  |  | 6.9546 | 6.9776 | 6.9999 | 7.021 | 7.0456 | 7.0691 | 7.1051 | 7.1432 | 7.1789 | 7.2164 | 7.256 | 7.2928 | 7.3312 | 7.3714 | 7.4132 | 7.4564 | 7.6689 | 7.8816
|  |  |  | Best View [MW] |  |  | 6.9546 | 6.9837 | 7.0116 | 7.0379 | 7.067 | 7.0991 | 7.1492 | 7.1993 | 7.2489 | 7.3025 | 7.36 | 7.4163 | 7.4711 | 7.529 | 7.5897 | 7.6482 | 7.9465 | 8.2444
|  |  |  | Base Case [MW] |  |  | 6.9546 | 6.9918 | 7.0351 | 7.0752 | 7.1163 | 7.1633 | 7.2116 | 7.2642 | 7.3207 | 7.3763 | 7.4304 | 7.488 | 7.5485 | 7.6069 | 7.6676 | 7.7304 | 8.0387 | 8.3473
|  |  |  | Aggressive [MW] |  |  | 6.9546 | 7.01 | 7.0682 | 7.1287 | 7.1912 | 7.2552 | 7.3168 | 7.3847 | 7.4494 | 7.5149 | 7.5856 | 7.6561 | 7.7311 | 7.805 | 7.8769 | 7.9565 | 8.334 | 8.7127
| NEWPORT | 20 | 1 | Conservative [MW] |  |  | 3.4634 | 3.4679 | 3.4712 | 3.4757 | 3.4802 | 3.4834 | 3.5001 | 3.5164 | 3.5322 | 3.5502 | 3.5677 | 3.5845 | 3.6036 | 3.622 | 3.6413 | 3.6612 | 3.7589 | 3.8568
|  |  |  | Best View [MW] |  |  | 3.4634 | 3.4727 | 3.4819 | 3.4924 | 3.5013 | 3.5113 | 3.532 | 3.5519 | 3.5736 | 3.596 | 3.6187 | 3.642 | 3.6655 | 3.6909 | 3.7166 | 3.7424 | 3.8712 | 4
|  |  |  | Base Case [MW] |  |  | 3.4634 | 3.4772 | 3.4908 | 3.504 | 3.5183 | 3.5321 | 3.5587 | 3.5841 | 3.611 | 3.6394 | 3.6676 | 3.6987 | 3.7294 | 3.7611 | 3.7938 | 3.8274 | 3.993 | 4.1587
|  |  |  | Aggressive [MW] |  |  | 3.4634 | 3.4908 | 3.5181 | 3.5481 | 3.5778 | 3.61 | 3.647 | 3.6857 | 3.7257 | 3.7685 | 3.812 | 3.8578 | 3.9055 | 3.9546 | 4.0047 | 4.057 | 4.3126 | 4.5686
| NEWTOWNCUNNINGHAM | 10 | 1 | Conservative [MW] |  |  | 6.8583 | 6.8713 | 6.8841 | 6.9008 | 6.9128 | 6.9288 | 6.9615 | 6.9965 | 7.0293 | 7.0643 | 7.1014 | 7.1362 | 7.1729 | 7.2115 | 7.2521 | 7.2899 | 7.4863 | 7.6823
|  |  |  | Best View [MW] |  |  | 6.8583 | 6.8862 | 6.9168 | 6.9501 | 6.9817 | 7.0156 | 7.0622 | 7.1132 | 7.1638 | 7.2187 | 7.2728 | 7.3259 | 7.3824 | 7.4422 | 7.5001 | 7.5607 | 7.8564 | 8.1525
|  |  |  | Base Case [MW] |  |  | 6.8583 | 6.8915 | 6.927 | 6.9603 | 6.9956 | 7.033 | 7.0928 | 7.1506 | 7.2107 | 7.2774 | 7.3411 | 7.4058 | 7.476 | 7.5467 | 7.617 | 7.6868 | 8.0372 | 8.3874
|  |  |  | Aggressive [MW] |  |  | 6.8583 | 6.9081 | 6.9618 | 7.0191 | 7.0751 | 7.1294 | 7.1995 | 7.274 | 7.3474 | 7.4242 | 7.5033 | 7.5841 | 7.6664 | 7.7536 | 7.8402 | 7.9302 | 8.3712 | 8.8128
| OAKFIELD | 10 | 1 | Conservative [MW] |  |  | 11.8678 | 11.889 | 11.9096 | 11.9336 | 11.957 | 11.9799 | 12.0242 | 12.07 | 12.1177 | 12.1672 | 12.2184 | 12.2666 | 12.3206 | 12.3718 | 12.4242 | 12.4819 | 12.7562 | 13.0313
|  |  |  | Best View [MW] |  |  | 11.8678 | 11.9054 | 11.9453 | 11.9833 | 12.0236 | 12.0661 | 12.1268 | 12.1911 | 12.2594 | 12.3272 | 12.3983 | 12.4683 | 12.5456 | 12.6217 | 12.7001 | 12.781 | 13.179 | 13.5773
|  |  |  | Base Case [MW] |  |  | 11.8678 | 11.9158 | 11.9691 | 12.0233 | 12.0784 | 12.1342 | 12.2096 | 12.2871 | 12.3703 | 12.4508 | 12.5409 | 12.6315 | 12.7224 | 12.8173 | 12.9161 | 13.0224 | 13.5338 | 14.0465
|  |  |  | Aggressive [MW] |  |  | 11.8678 | 11.9436 | 12.0244 | 12.11 | 12.1996 | 12.289 | 12.3944 | 12.5051 | 12.6162 | 12.7352 | 12.8572 | 12.9855 | 13.1192 | 13.2571 | 13.403 | 13.5507 | 14.2845 | 15.0186
| OLDBAWN | 10 | 1 | Conservative [MW] |  |  | 11.9488 | 12.0179 | 12.0874 | 12.1567 | 12.2324 | 12.3077 | 12.3665 | 12.4261 | 12.4868 | 12.5484 | 12.611 | 12.6741 | 12.738 | 12.806 | 12.8745 | 12.9398 | 13.2749 | 13.6095
|  |  |  | Best View [MW] |  |  | 11.9488 | 12.0266 | 12.1097 | 12.1918 | 12.2792 | 12.365 | 12.4363 | 12.5081 | 12.5796 | 12.6545 | 12.7291 | 12.8068 | 12.8873 | 12.9672 | 13.0498 | 13.1311 | 13.5411 | 13.9509
|  |  |  | Base Case [MW] |  |  | 11.9488 | 12.0363 | 12.128 | 12.2239 | 12.3203 | 12.4207 | 12.5003 | 12.5825 | 12.6672 | 12.7506 | 12.8396 | 12.9267 | 13.0189 | 13.1091 | 13.2039 | 13.3033 | 13.7882 | 14.2738
|  |  |  | Aggressive [MW] |  |  | 11.9488 | 12.0764 | 12.2118 | 12.3546 | 12.5039 | 12.6586 | 12.7366 | 12.8206 | 12.9036 | 12.989 | 13.0762 | 13.1617 | 13.2526 | 13.3452 | 13.4386 | 13.5335 | 14.0039 | 14.4746
| OLDCASTLE | 10 | 1 | Conservative [MW] |  |  | 3.4363 | 3.4427 | 3.4507 | 3.4567 | 3.4645 | 3.472 | 3.4861 | 3.5013 | 3.5174 | 3.5345 | 3.5507 | 3.5678 | 3.5857 | 3.6045 | 3.622 | 3.6423 | 3.7364 | 3.831
|  |  |  | Best View [MW] |  |  | 3.4363 | 3.4452 | 3.4538 | 3.4639 | 3.4737 | 3.4832 | 3.4991 | 3.5175 | 3.5366 | 3.5545 | 3.5749 | 3.5958 | 3.6172 | 3.639 | 3.6611 | 3.6834 | 3.7944 | 3.9055
|  |  |  | Base Case [MW] |  |  | 3.4363 | 3.4531 | 3.4706 | 3.4907 | 3.5094 | 3.5288 | 3.5482 | 3.5681 | 3.5884 | 3.6111 | 3.6322 | 3.6554 | 3.6789 | 3.7044 | 3.7298 | 3.7551 | 3.882 | 4.0089
|  |  |  | Aggressive [MW] |  |  | 3.4363 | 3.4597 | 3.4846 | 3.5108 | 3.5383 | 3.5668 | 3.5917 | 3.6166 | 3.6413 | 3.6676 | 3.6955 | 3.7248 | 3.7533 | 3.785 | 3.8155 | 3.8488 | 4.0079 | 4.1675
|  | 20 | 1 | Conservative [MW] |  |  | 2.0102 | 2.0179 | 2.0259 | 2.0336 | 2.0416 | 2.0498 | 2.0666 | 2.0841 | 2.1027 | 2.1219 | 2.1418 | 2.1619 | 2.1827 | 2.2039 | 2.2256 | 2.2482 | 2.3585 | 2.4691
|  |  |  | Best View [MW] |  |  | 2.0102 | 2.0203 | 2.0304 | 2.0405 | 2.051 | 2.062 | 2.0817 | 2.1027 | 2.1246 | 2.1471 | 2.1703 | 2.1942 | 2.2185 | 2.2439 | 2.2709 | 2.2985 | 2.4351 | 2.5718
|  |  |  | Base Case [MW] |  |  | 2.0102 | 2.0297 | 2.0494 | 2.0701 | 2.092 | 2.115 | 2.138 | 2.1617 | 2.186 | 2.211 | 2.2368 | 2.2641 | 2.2925 | 2.3218 | 2.3521 | 2.383 | 2.536 | 2.689
|  |  |  | Aggressive [MW] |  |  | 2.0102 | 2.0369 | 2.065 | 2.0952 | 2.1275 | 2.1613 | 2.189 | 2.2177 | 2.2475 | 2.2793 | 2.3123 | 2.3465 | 2.3819 | 2.419 | 2.4576 | 2.4978 | 2.6944 | 2.8913
| ORANMORE | 10 | 1 | Conservative [MW] |  |  | 13.8428 | 13.9064 | 13.9705 | 14.0401 | 14.1044 | 14.1742 | 14.2642 | 14.3541 | 14.4495 | 14.5444 | 14.6386 | 14.7319 | 14.8286 | 14.9238 | 15.0214 | 15.1215 | 15.6153 | 16.1095
|  |  |  | Best View [MW] |  |  | 13.8428 | 13.9213 | 14.0069 | 14.0903 | 14.1756 | 14.2588 | 14.3875 | 14.5215 | 14.65 | 14.7863 | 14.9202 | 15.0547 | 15.1936 | 15.3252 | 15.4637 | 15.5969 | 16.277 | 16.9563
|  |  |  | Base Case [MW] |  |  | 13.8428 | 13.9477 | 14.0505 | 14.1557 | 14.2631 | 14.3726 | 14.5135 | 14.6603 | 14.8058 | 14.9539 | 15.103 | 15.2509 | 15.3958 | 15.5404 | 15.683 | 15.8257 | 16.5387 | 17.2517
|  |  |  | Aggressive [MW] |  |  | 13.8428 | 14.0041 | 14.1708 | 14.3358 | 14.5081 | 14.6838 | 14.8529 | 15.0205 | 15.1885 | 15.3599 | 15.5259 | 15.6883 | 15.8471 | 15.9912 | 16.1273 | 16.2501 | 16.8997 | 17.547
| OUGHTERARD | 10 | 1 | Conservative [MW] |  |  | 5.5305 | 5.5421 | 5.5495 | 5.5606 | 5.5712 | 5.5815 | 5.5973 | 5.6123 | 5.6267 | 5.6444 | 5.6615 | 5.6778 | 5.6933 | 5.7121 | 5.7302 | 5.7474 | 5.8357 | 5.9239
|  |  |  | Best View [MW] |  |  | 5.5305 | 5.542 | 5.5569 | 5.5714 | 5.5813 | 5.5986 | 5.6196 | 5.6393 | 5.6614 | 5.6864 | 5.7097 | 5.7355 | 5.7598 | 5.7864 | 5.8153 | 5.8423 | 5.9824 | 6.1222
|  |  |  | Base Case [MW] |  |  | 5.5305 | 5.5484 | 5.5616 | 5.5818 | 5.5973 | 5.6158 | 5.6401 | 5.663 | 5.6881 | 5.7155 | 5.745 | 5.7725 | 5.8022 | 5.8338 | 5.8631 | 5.8982 | 6.0582 | 6.2192
|  |  |  | Aggressive [MW] |  |  | 5.5305 | 5.5575 | 5.5824 | 5.6093 | 5.6379 | 5.6682 | 5.6987 | 5.7268 | 5.7606 | 5.7957 | 5.8281 | 5.8657 | 5.9002 | 5.9397 | 5.9799 | 6.0248 | 6.2365 | 6.4491
| PALLAS | 10 | 1 | Conservative [MW] |  |  | 6.8166 | 6.848 | 6.8821 | 6.914 | 6.9487 | 6.981 | 7.0281 | 7.0801 | 7.1272 | 7.1791 | 7.2257 | 7.2766 | 7.3323 | 7.3816 | 7.435 | 7.4868 | 7.75 | 8.013
|  |  |  | Best View [MW] |  |  | 6.8166 | 6.8556 | 6.8963 | 6.9385 | 6.9773 | 7.0176 | 7.0826 | 7.1444 | 7.2079 | 7.2726 | 7.3381 | 7.404 | 7.4751 | 7.5403 | 7.6097 | 7.6771 | 8.0193 | 8.3612
|  |  |  | Base Case [MW] |  |  | 6.8166 | 6.8635 | 6.9154 | 6.9624 | 7.0138 | 7.0648 | 7.142 | 7.2172 | 7.2904 | 7.3709 | 7.4476 | 7.5303 | 7.6073 | 7.6887 | 7.7731 | 7.854 | 8.2678 | 8.681
|  |  |  | Aggressive [MW] |  |  | 6.8166 | 6.8921 | 6.9704 | 7.0505 | 7.1367 | 7.2182 | 7.3175 | 7.4201 | 7.519 | 7.6234 | 7.731 | 7.8341 | 7.9355 | 8.0378 | 8.1378 | 8.2311 | 8.7154 | 9.1985
| PALMERSTOWN | 10 | 1 | Conservative [MW] |  |  | 13.4742 | 13.5666 | 13.6592 | 13.7567 | 13.8578 | 13.9582 | 14.0166 | 14.0802 | 14.1411 | 14.2026 | 14.2649 | 14.3278 | 14.3957 | 14.4599 | 14.5286 | 14.5934 | 14.9277 | 15.2613
|  |  |  | Best View [MW] |  |  | 13.4742 | 13.5762 | 13.6809 | 13.7882 | 13.8976 | 14.0123 | 14.0821 | 14.1516 | 14.2257 | 14.2948 | 14.372 | 14.4445 | 14.5202 | 14.5997 | 14.6777 | 14.7589 | 15.1562 | 15.5541
|  |  |  | Base Case [MW] |  |  | 13.4742 | 13.5849 | 13.7 | 13.8202 | 13.9437 | 14.0704 | 14.1506 | 14.2299 | 14.3118 | 14.396 | 14.4785 | 14.5673 | 14.6535 | 14.746 | 14.8354 | 14.9259 | 15.3755 | 15.8252
|  |  |  | Aggressive [MW] |  |  | 13.4742 | 13.6115 | 13.7519 | 13.9029 | 14.0585 | 14.2177 | 14.2917 | 14.3656 | 14.4387 | 14.5156 | 14.5914 | 14.6703 | 14.7524 | 14.8332 | 14.9168 | 14.9982 | 15.4109 | 15.8233
| PARKMORE | 10 | 1 | Conservative [MW] |  |  | 9.0779 | 9.1056 | 9.1387 | 9.1643 | 9.1951 | 9.2247 | 9.2546 | 9.2883 | 9.3109 | 9.3353 | 9.3532 | 9.3551 | 9.3558 | 9.3527 | 9.3275 | 9.2928 | 9.1446 | 8.9947
|  |  |  | Best View [MW] |  |  | 9.0779 | 9.1121 | 9.1537 | 9.1901 | 9.2204 | 9.257 | 9.2957 | 9.3259 | 9.3515 | 9.362 | 9.3526 | 9.3241 | 9.2591 | 9.1535 | 8.9971 | 8.7358 | 7.7091 | 6.665
|  |  |  | Base Case [MW] |  |  | 9.0779 | 9.1256 | 9.1733 | 9.2148 | 9.2543 | 9.2907 | 9.3313 | 9.3527 | 9.3572 | 9.346 | 9.3028 | 9.2221 | 9.0856 | 8.8562 | 8.4311 | 6.9315 | 2.2991 | -0.0001
|  |  |  | Aggressive [MW] |  |  | 9.0779 | 9.1509 | 9.2226 | 9.2809 | 9.3283 | 9.3542 | 9.3565 | 9.3285 | 9.263 | 9.128 | 8.8881 | 8.4108 | 6.936 | 6.9403 | 6.9435 | 6.9438 | 6.9529 | 6.9615
| PATRICKSWELL | 20 | 1 | Conservative [MW] |  |  | 2.4889 | 2.5312 | 2.5728 | 2.6154 | 2.6588 | 2.7031 | 2.7502 | 2.798 | 2.8463 | 2.897 | 2.9463 | 2.996 | 3.0479 | 3.098 | 3.1502 | 3.2025 | 3.4636 | 3.7248
|  |  |  | Best View [MW] |  |  | 2.4889 | 2.5323 | 2.5766 | 2.62 | 2.666 | 2.7111 | 2.7763 | 2.8395 | 2.9059 | 2.9716 | 3.0403 | 3.1078 | 3.1779 | 3.2462 | 3.3167 | 3.3869 | 3.7386 | 4.0903
|  |  |  | Base Case [MW] |  |  | 2.4889 | 2.5458 | 2.6046 | 2.6637 | 2.7247 | 2.7857 | 2.8594 | 2.9338 | 3.0105 | 3.0891 | 3.1675 | 3.2471 | 3.3255 | 3.4065 | 3.4874 | 3.5676 | 3.9705 | 4.3734
|  |  |  | Aggressive [MW] |  |  | 2.4889 | 2.5766 | 2.6662 | 2.7572 | 2.8528 | 2.949 | 3.0311 | 3.117 | 3.2015 | 3.2884 | 3.3749 | 3.4626 | 3.5485 | 3.6366 | 3.7208 | 3.8024 | 4.2173 | 4.6317
| PEMBROKE | 10 | 1 | Conservative [MW] |  |  | 30.4954 | 30.6667 | 30.8366 | 31.018 | 31.1982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Best View [MW] |  |  | 30.4954 | 30.6895 | 30.8969 | 31.104 | 31.3178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Base Case [MW] |  |  | 30.4954 | 30.7226 | 30.9628 | 31.2087 | 31.4594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Aggressive [MW] |  |  | 30.4954 | 30.8836 | 31.2933 | 31.7247 | 32.1763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | Conservative [MW] |  |  | 8.157 | 8.1986 | 8.2432 | 8.2867 | 8.3332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Best View [MW] |  |  | 8.157 | 8.2065 | 8.2558 | 8.3092 | 8.3622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Base Case [MW] |  |  | 8.157 | 8.2145 | 8.2722 | 8.3347 | 8.3972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Aggressive [MW] |  |  | 8.157 | 8.2553 | 8.3577 | 8.465 | 8.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PHIBSBORO | 10 | 1 | Conservative [MW] |  |  | 14.9976 | 15.1079 | 15.2197 | 15.3368 | 15.4518 | 15.5695 | 15.2863 | 15.0017 | 15.1107 | 15.2173 | 15.3278 | 15.4349 | 15.5455 | 15.6549 | 15.7631 | 15.8685 | 16.4031 | 16.9372
|  |  |  | Best View [MW] |  |  | 14.9976 | 15.1261 | 15.2566 | 15.3926 | 15.5299 | 15.6652 | 15.3949 | 15.1281 | 15.2475 | 15.3684 | 15.4902 | 15.6125 | 15.7302 | 15.8503 | 15.9725 | 16.0867 | 16.6789 | 17.2697
|  |  |  | Base Case [MW] |  |  | 14.9976 | 15.146 | 15.2992 | 15.4567 | 15.614 | 15.7744 | 15.5182 | 15.2619 | 15.3919 | 15.5236 | 15.6568 | 15.786 | 15.9179 | 16.0434 | 16.169 | 16.2938 | 16.9199 | 17.5459
|  |  |  | Aggressive [MW] |  |  | 14.9976 | 15.2497 | 15.5145 | 15.7818 | 16.0575 | 16.3308 | 16.069 | 15.8103 | 15.9348 | 16.0543 | 16.1767 | 16.2915 | 16.4032 | 16.5092 | 16.6117 | 16.7091 | 17.2098 | 17.7097
| POLLERTON | 10 | 1 | Conservative [MW] |  |  | 13.5309 | 13.5903 | 13.6508 | 13.7126 | 13.7751 | 11.9993 | 11.3054 | 11.4027 | 11.4978 | 11.5967 | 11.696 | 11.7953 | 11.898 | 12.0004 | 12.1018 | 12.2057 | 12.7186 | 13.2319
|  |  |  | Best View [MW] |  |  | 13.5309 | 13.6027 | 13.6788 | 13.7537 | 13.8329 | 12.0723 | 11.4112 | 11.5423 | 11.6727 | 11.8083 | 11.9447 | 12.0817 | 12.2217 | 12.3605 | 12.5005 | 12.6446 | 13.3539 | 14.0639
|  |  |  | Base Case [MW] |  |  | 13.5309 | 13.6189 | 13.7086 | 13.7951 | 13.8879 | 12.1453 | 11.5109 | 11.6668 | 11.8232 | 11.9858 | 12.1501 | 12.3149 | 12.4819 | 12.6462 | 12.8169 | 12.9791 | 13.8129 | 14.6452
|  |  |  | Aggressive [MW] |  |  | 13.5309 | 13.6784 | 13.8234 | 13.9743 | 14.1295 | 12.4602 | 11.8724 | 12.0676 | 12.2682 | 12.4716 | 12.6714 | 12.8749 | 13.0736 | 13.2678 | 13.4561 | 13.6325 | 14.5461 | 15.4578
| PORTARLINGTON | 10 | 1 | Conservative [MW] |  |  | 7.5783 | 7.6016 | 7.6289 | 7.953 | 7.196 | 7.2886 | 7.5001 | 7.5584 | 7.6094 | 7.6621 | 7.7175 | 7.773 | 7.8213 | 7.8796 | 7.9309 | 7.9849 | 8.2476 | 8.5107
|  |  |  | Best View [MW] |  |  | 7.5783 | 7.6046 | 7.6464 | 7.9727 | 7.2269 | 7.3316 | 7.5516 | 7.6342 | 7.703 | 7.7701 | 7.8416 | 7.9101 | 7.9735 | 8.0407 | 8.1192 | 8.1914 | 8.5692 | 8.946
|  |  |  | Base Case [MW] |  |  | 7.5783 | 7.615 | 7.6651 | 7.997 | 7.2593 | 7.3733 | 7.6134 | 7.7087 | 7.7902 | 7.8728 | 7.9491 | 8.026 | 8.1131 | 8.2047 | 8.2921 | 8.3824 | 8.8264 | 9.2708
|  |  |  | Aggressive [MW] |  |  | 7.5783 | 7.6319 | 7.7043 | 8.0588 | 7.3492 | 7.4879 | 7.7748 | 7.8854 | 7.9835 | 8.0857 | 8.1899 | 8.3012 | 8.4173 | 8.536 | 8.6528 | 8.7824 | 9.3962 | 10.0121
|  |  | 2 | Conservative [MW] |  |  | 3.024 | 3.0384 | 3.0506 | 2.7703 | 2.3782 | 2.3231 | 2.1742 | 2.175 | 2.1863 | 2.1972 | 2.2105 | 2.2239 | 2.2368 | 2.2516 | 2.2696 | 2.2907 | 2.3878 | 2.4854
|  |  |  | Best View [MW] |  |  | 3.024 | 3.0416 | 3.0548 | 2.7762 | 2.3857 | 2.3333 | 2.1821 | 2.1851 | 2.1998 | 2.2166 | 2.2328 | 2.252 | 2.2787 | 2.3007 | 2.3212 | 2.342 | 2.4451 | 2.5483
|  |  |  | Base Case [MW] |  |  | 3.024 | 3.0447 | 3.0617 | 2.7855 | 2.3996 | 2.3509 | 2.1958 | 2.2031 | 2.2227 | 2.2433 | 2.271 | 2.3011 | 2.3255 | 2.3513 | 2.3762 | 2.4015 | 2.527 | 2.6525
|  |  |  | Aggressive [MW] |  |  | 3.024 | 3.0598 | 3.0924 | 2.829 | 2.4645 | 2.4332 | 2.2725 | 2.2943 | 2.3336 | 2.3777 | 2.416 | 2.4553 | 2.4952 | 2.536 | 2.5741 | 2.6078 | 2.7878 | 2.9672
| PORTLAOISE | 10 | 1 | Conservative [MW] |  |  | 16.0437 | 16.1143 | 16.1888 | 16.2623 | 16.3346 | 16.4058 | 16.5131 | 16.6173 | 16.7177 | 16.8244 | 16.9314 | 17.0382 | 17.1383 | 17.2478 | 17.349 | 17.4525 | 17.9638 | 18.4755
|  |  |  | Best View [MW] |  |  | 16.0437 | 16.1312 | 16.22 | 16.3096 | 16.3999 | 16.4904 | 16.6246 | 16.7573 | 16.8921 | 17.0223 | 17.1574 | 17.2901 | 17.4189 | 17.5476 | 17.6747 | 17.7969 | 18.4209 | 19.0441
|  |  |  | Base Case [MW] |  |  | 16.0437 | 16.1515 | 16.2606 | 16.3713 | 16.4825 | 16.5937 | 16.7502 | 16.905 | 17.0617 | 17.2166 | 17.3741 | 17.5252 | 17.672 | 17.8116 | 17.9499 | 18.0707 | 18.7213 | 19.3689
|  |  |  | Aggressive [MW] |  |  | 16.0437 | 16.2135 | 16.3843 | 16.56 | 16.7382 | 16.9157 | 17.1179 | 17.3154 | 17.5122 | 17.7015 | 17.8813 | 18.0405 | 18.1811 | 18.2895 | 18.3479 | 18.3539 | 18.5236 | 18.6846
|  | 20 | 1 | Conservative [MW] |  |  | 12.7058 | 12.7319 | 12.7571 | 12.7815 | 12.8092 | 12.8356 | 12.8752 | 12.9129 | 12.9525 | 12.9944 | 13.0381 | 13.0797 | 13.1233 | 13.1684 | 13.2154 | 13.264 | 13.5027 | 13.7418
|  |  |  | Best View [MW] |  |  | 12.7058 | 12.7385 | 12.7697 | 12.7999 | 12.8324 | 12.8676 | 12.9156 | 12.9684 | 13.022 | 13.0763 | 13.1313 | 13.1865 | 13.2459 | 13.3095 | 13.373 | 13.4363 | 13.7534 | 14.0704
|  |  |  | Base Case [MW] |  |  | 12.7058 | 12.7429 | 12.7822 | 12.8233 | 12.8625 | 12.9036 | 12.9657 | 13.0275 | 13.0926 | 13.1568 | 13.228 | 13.2978 | 13.3702 | 13.4488 | 13.5291 | 13.6112 | 14.0171 | 14.4233
|  |  |  | Aggressive [MW] |  |  | 12.7058 | 12.7664 | 12.8261 | 12.8928 | 12.958 | 13.0298 | 13.114 | 13.1981 | 13.2895 | 13.3882 | 13.4848 | 13.5913 | 13.6989 | 13.8106 | 13.9305 | 14.0529 | 14.6584 | 15.2642
| PORTLAW | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| PURCELLS INCH | 10 | 1 | Conservative [MW] |  |  | 5.8063 | 5.8229 | 5.839 | 5.8564 | 5.8733 | 5.8916 | 5.9166 | 5.9424 | 5.9687 | 5.9957 | 6.0251 | 6.0531 | 6.0815 | 6.1104 | 6.1415 | 6.173 | 6.3295 | 6.486
|  |  |  | Best View [MW] |  |  | 5.8063 | 5.8264 | 5.8475 | 5.8679 | 5.8893 | 5.9099 | 5.9453 | 5.9804 | 6.0189 | 6.0567 | 6.0957 | 6.1358 | 6.1769 | 6.2188 | 6.2614 | 6.3066 | 6.5255 | 6.7449
|  |  |  | Base Case [MW] |  |  | 5.8063 | 5.8315 | 5.8556 | 5.8805 | 5.9042 | 5.9304 | 5.9723 | 6.0166 | 6.0613 | 6.108 | 6.1547 | 6.205 | 6.2547 | 6.3077 | 6.3615 | 6.4181 | 6.6936 | 6.9696
|  |  |  | Aggressive [MW] |  |  | 5.8063 | 5.847 | 5.8865 | 5.9303 | 5.9744 | 6.0187 | 6.0741 | 6.1316 | 6.1909 | 6.2515 | 6.3151 | 6.3831 | 6.451 | 6.5225 | 6.5946 | 6.6712 | 7.0424 | 7.4143
| RAHANS | 10 | 1 | Conservative [MW] |  |  | 4.4721 | 4.4805 | 4.4886 | 4.4965 | 4.5066 | 4.5139 | 4.5433 | 4.5695 | 4.5973 | 4.6268 | 4.6549 | 4.6843 | 4.7123 | 4.741 | 4.7706 | 4.8008 | 4.9502 | 5.0997
|  |  |  | Best View [MW] |  |  | 4.4721 | 4.4915 | 4.5096 | 4.5287 | 4.5489 | 4.5673 | 4.6033 | 4.6387 | 4.6732 | 4.7091 | 4.7463 | 4.7814 | 4.817 | 4.8527 | 4.8881 | 4.9224 | 5.0969 | 5.2713
|  |  |  | Base Case [MW] |  |  | 4.4721 | 4.4967 | 4.5237 | 4.548 | 4.5746 | 4.6008 | 4.6412 | 4.6837 | 4.7277 | 4.7699 | 4.8125 | 4.8518 | 4.8933 | 4.9357 | 4.9721 | 5.0107 | 5.1978 | 5.3853
|  |  |  | Aggressive [MW] |  |  | 4.4721 | 4.5202 | 4.5688 | 4.6196 | 4.6692 | 4.7197 | 4.7739 | 4.8313 | 4.8853 | 4.9393 | 4.988 | 5.0353 | 5.0745 | 5.1051 | 5.1255 | 5.1292 | 5.1922 | 5.2525
| RAHEEN | 10 | 1 | Conservative [MW] |  |  | 14.3032 | 14.3834 | 14.4621 | 14.5389 | 14.6182 | 14.7005 | 14.793 | 14.8789 | 14.97 | 15.066 | 15.1554 | 15.2491 | 15.3411 | 15.4363 | 15.5231 | 15.6182 | 16.0715 | 16.5262
|  |  |  | Best View [MW] |  |  | 14.3032 | 14.382 | 14.4638 | 14.5429 | 14.6248 | 14.709 | 14.8308 | 14.9533 | 15.0769 | 15.2058 | 15.3286 | 15.4547 | 15.5779 | 15.7026 | 15.8213 | 15.9446 | 16.549 | 17.1541
|  |  |  | Base Case [MW] |  |  | 14.3032 | 14.4142 | 14.5218 | 14.6357 | 14.7492 | 14.863 | 15.0052 | 15.1515 | 15.2902 | 15.4363 | 15.577 | 15.7166 | 15.858 | 15.9998 | 16.1334 | 16.2605 | 16.9132 | 17.5649
|  |  |  | Aggressive [MW] |  |  | 14.3032 | 14.4802 | 14.6619 | 14.8448 | 15.0324 | 15.2208 | 15.3749 | 15.5297 | 15.6835 | 15.8382 | 15.9867 | 16.1359 | 16.2764 | 16.4104 | 16.526 | 16.6372 | 17.2049 | 17.7719
| RAMPARTS | 10 | 1 | Conservative [MW] |  |  | 13.6669 | 13.711 | 13.761 | 13.8088 | 13.8583 | 13.9092 | 13.9636 | 14.019 | 14.0798 | 14.1372 | 14.1953 | 14.2584 | 14.322 | 14.3864 | 14.4508 | 14.5153 | 14.8376 | 15.1599
|  |  |  | Best View [MW] |  |  | 13.6669 | 13.7176 | 13.7698 | 13.827 | 13.8814 | 13.9364 | 14.0146 | 14.0908 | 14.1737 | 14.2582 | 14.3444 | 14.432 | 14.5245 | 14.6179 | 14.7111 | 14.8135 | 15.3007 | 15.7895
|  |  |  | Base Case [MW] |  |  | 13.6669 | 13.7391 | 13.8175 | 13.8982 | 13.9842 | 14.0673 | 14.1612 | 14.2552 | 14.3488 | 14.4505 | 14.5511 | 14.6589 | 14.7687 | 14.8803 | 14.997 | 15.1146 | 15.7004 | 16.2862
|  |  |  | Aggressive [MW] |  |  | 13.6669 | 13.7663 | 13.8751 | 13.9886 | 14.1057 | 14.2256 | 14.3393 | 14.4534 | 14.5759 | 14.6974 | 14.8255 | 14.9598 | 15.0994 | 15.2428 | 15.3892 | 15.5367 | 16.2713 | 17.0061
| RANDALSTOWN | 10 | 1 | Conservative [MW] |  |  | 3.6798 | 3.6885 | 3.6989 | 3.7089 | 3.7164 | 3.7276 | 3.7394 | 3.7525 | 3.7669 | 3.7805 | 3.7953 | 3.8093 | 3.8245 | 3.8409 | 3.8563 | 3.8728 | 3.9524 | 4.0322
|  |  |  | Best View [MW] |  |  | 3.6798 | 3.6918 | 3.7012 | 3.7121 | 3.7245 | 3.7363 | 3.7519 | 3.7703 | 3.7876 | 3.8056 | 3.8243 | 3.8438 | 3.8637 | 3.8843 | 3.9052 | 3.9266 | 4.0325 | 4.1384
|  |  |  | Base Case [MW] |  |  | 3.6798 | 3.6943 | 3.7099 | 3.7263 | 3.7436 | 3.7598 | 3.7802 | 3.801 | 3.8241 | 3.8473 | 3.8704 | 3.8957 | 3.9206 | 3.9474 | 3.9736 | 4.0014 | 4.1361 | 4.2711
|  |  |  | Aggressive [MW] |  |  | 3.6798 | 3.7013 | 3.7229 | 3.7443 | 3.7677 | 3.7929 | 3.8202 | 3.8487 | 3.8779 | 3.9099 | 3.9421 | 3.9767 | 4.0132 | 4.0514 | 4.0909 | 4.1314 | 4.3312 | 4.5311
|  | 20 | 1 | Conservative [MW] |  |  | 3.7149 | 3.7251 | 3.737 | 3.7463 | 3.7572 | 3.7696 | 3.7838 | 3.7991 | 3.8135 | 3.8291 | 3.8457 | 3.8635 | 3.8802 | 3.8979 | 3.9144 | 3.9341 | 4.0239 | 4.1143
|  |  |  | Best View [MW] |  |  | 3.7149 | 3.7279 | 3.7404 | 3.7521 | 3.7653 | 3.7797 | 3.7987 | 3.8161 | 3.8363 | 3.857 | 3.8782 | 3.8998 | 3.9217 | 3.946 | 3.9704 | 3.995 | 4.1175 | 4.24
|  |  |  | Base Case [MW] |  |  | 3.7149 | 3.7334 | 3.7506 | 3.7685 | 3.787 | 3.8063 | 3.8309 | 3.8534 | 3.878 | 3.9043 | 3.9303 | 3.9579 | 3.9869 | 4.0173 | 4.0467 | 4.0792 | 4.2336 | 4.3884
|  |  |  | Aggressive [MW] |  |  | 3.7149 | 3.7387 | 3.7623 | 3.7875 | 3.8141 | 3.8421 | 3.8735 | 3.9052 | 3.9393 | 3.9754 | 4.0134 | 4.0506 | 4.0911 | 4.1346 | 4.1784 | 4.2243 | 4.4482 | 4.6724
| RATHDOWNEY | 10 | 1 | Conservative [MW] |  |  | 4.2408 | 4.2548 | 4.2702 | 4.2849 | 4.3011 | 4.3155 | 4.3377 | 4.3604 | 4.3836 | 4.4073 | 4.429 | 4.4534 | 4.4781 | 4.5028 | 4.5278 | 4.5527 | 4.6774 | 4.8021
|  |  |  | Best View [MW] |  |  | 4.2408 | 4.2593 | 4.2766 | 4.2972 | 4.3166 | 4.3336 | 4.3657 | 4.3987 | 4.4347 | 4.4688 | 4.5031 | 4.5399 | 4.5765 | 4.6126 | 4.6504 | 4.687 | 4.8733 | 5.0593
|  |  |  | Base Case [MW] |  |  | 4.2408 | 4.2653 | 4.2898 | 4.3167 | 4.3435 | 4.369 | 4.4044 | 4.4398 | 4.4775 | 4.5147 | 4.5535 | 4.5939 | 4.6327 | 4.6722 | 4.7147 | 4.7543 | 4.9599 | 5.1651
|  |  |  | Aggressive [MW] |  |  | 4.2408 | 4.2802 | 4.3209 | 4.3625 | 4.4048 | 4.4485 | 4.4886 | 4.5295 | 4.5735 | 4.615 | 4.6586 | 4.7038 | 4.7475 | 4.7916 | 4.8385 | 4.8817 | 5.1074 | 5.3325
| RATHDRUM | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.031071 | 0.072161 | 0.11369 | 0.32016 | 0.5267
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.017604 | 0.062978 | 0.109 | 0.15566 | 0.20264 | 0.43671 | 0.67084
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | 0.054748 | 0.11574 | 0.17769 | 0.24045 | 0.3038 | 0.36708 | 0.42952 | 0.74398 | 1.0583
| RATHKEALE | 20 | 1 | Conservative [MW] |  |  | 13.4566 | 13.5169 | 13.5738 | 13.632 | 13.6912 | 13.7557 | 13.8194 | 13.8882 | 13.9566 | 14.0297 | 14.0981 | 14.1703 | 14.2468 | 14.3224 | 14.3974 | 14.4757 | 14.8582 | 15.2414
|  |  |  | Best View [MW] |  |  | 13.4566 | 13.5162 | 13.5805 | 13.6418 | 13.7033 | 13.7658 | 13.8551 | 13.9455 | 14.0416 | 14.138 | 14.2345 | 14.3357 | 14.436 | 14.54 | 14.6473 | 14.7569 | 15.2988 | 15.8412
|  |  |  | Base Case [MW] |  |  | 13.4566 | 13.5348 | 13.6155 | 13.6985 | 13.784 | 13.8713 | 13.9736 | 14.0831 | 14.1902 | 14.304 | 14.4234 | 14.5389 | 14.6587 | 14.7827 | 14.9097 | 15.0394 | 15.6806 | 16.3223
|  |  |  | Aggressive [MW] |  |  | 13.4566 | 13.5767 | 13.7045 | 13.8303 | 13.9665 | 14.1032 | 14.2203 | 14.3464 | 14.4708 | 14.6026 | 14.7364 | 14.8705 | 15.0096 | 15.1523 | 15.2972 | 15.4435 | 16.1713 | 16.8993
| RATHMORE | 10 | 1 | Conservative [MW] |  |  | 3.9901 | 3.9997 | 4.0111 | 4.0219 | 4.0346 | 4.0446 | 4.0621 | 4.0786 | 4.0961 | 4.1149 | 4.1325 | 4.1511 | 4.1685 | 4.1892 | 4.2086 | 4.2288 | 4.3276 | 4.4265
|  |  |  | Best View [MW] |  |  | 3.9901 | 4.0033 | 4.0158 | 4.0298 | 4.0432 | 4.058 | 4.0821 | 4.1064 | 4.1308 | 4.1551 | 4.1816 | 4.2078 | 4.2361 | 4.2639 | 4.2934 | 4.3223 | 4.4685 | 4.6146
|  |  |  | Base Case [MW] |  |  | 3.9901 | 4.0086 | 4.028 | 4.0481 | 4.0669 | 4.0886 | 4.1121 | 4.138 | 4.1638 | 4.1895 | 4.2172 | 4.2446 | 4.2738 | 4.3024 | 4.3324 | 4.3617 | 4.5103 | 4.6587
|  |  |  | Aggressive [MW] |  |  | 3.9901 | 4.0173 | 4.044 | 4.0722 | 4.1017 | 4.1325 | 4.1642 | 4.1949 | 4.2245 | 4.2573 | 4.2908 | 4.3273 | 4.3618 | 4.3988 | 4.4355 | 4.4718 | 4.6545 | 4.8372
|  | 20 | 1 | Conservative [MW] |  |  | 4.0073 | 4.0201 | 4.0323 | 4.0441 | 4.0553 | 4.0682 | 4.0868 | 4.1064 | 4.1247 | 4.144 | 4.1642 | 4.1852 | 4.2047 | 4.2274 | 4.2485 | 4.2703 | 4.3773 | 4.4844
|  |  |  | Best View [MW] |  |  | 4.0073 | 4.0229 | 4.0377 | 4.0518 | 4.0672 | 4.0819 | 4.1092 | 4.134 | 4.1632 | 4.1896 | 4.2201 | 4.2476 | 4.2791 | 4.3096 | 4.3414 | 4.3719 | 4.5279 | 4.6837
|  |  |  | Base Case [MW] |  |  | 4.0073 | 4.0287 | 4.0484 | 4.071 | 4.0941 | 4.1155 | 4.1418 | 4.17 | 4.1978 | 4.2274 | 4.2562 | 4.2866 | 4.3183 | 4.3489 | 4.383 | 4.4155 | 4.5822 | 4.7486
|  |  |  | Aggressive [MW] |  |  | 4.0073 | 4.0369 | 4.0678 | 4.0997 | 4.1326 | 4.166 | 4.1983 | 4.2312 | 4.267 | 4.3032 | 4.3395 | 4.3755 | 4.4136 | 4.4532 | 4.4917 | 4.5337 | 4.7343 | 4.9356
| RATHMULLAN | 10 | 1 | Conservative [MW] |  |  | 13.8803 | 13.9486 | 14.0125 | 14.0812 | 14.1501 | 14.2188 | 14.3084 | 14.0113 | 14.1093 | 14.2039 | 14.3025 | 14.4056 | 14.5077 | 14.6133 | 14.7175 | 14.8242 | 15.351 | 15.8782
|  |  |  | Best View [MW] |  |  | 13.8803 | 13.9596 | 14.0379 | 14.1188 | 14.2028 | 14.2849 | 14.3972 | 14.1279 | 14.2485 | 14.3728 | 14.5002 | 14.6301 | 14.7657 | 14.8974 | 15.038 | 15.1772 | 15.877 | 16.5766
|  |  |  | Base Case [MW] |  |  | 13.8803 | 13.9892 | 14.1004 | 14.217 | 14.3347 | 14.4572 | 14.5948 | 14.3508 | 14.5022 | 14.6543 | 14.8104 | 14.9736 | 15.1331 | 15.3013 | 15.4667 | 15.6369 | 16.4753 | 17.3145
|  |  |  | Aggressive [MW] |  |  | 13.8803 | 14.028 | 14.1812 | 14.3433 | 14.5077 | 14.6775 | 14.86 | 14.6664 | 14.8636 | 15.0703 | 15.2785 | 15.4895 | 15.7036 | 15.9211 | 16.131 | 16.343 | 17.3974 | 18.4521
| RECESS | 10 | 1 | Conservative [MW] |  |  | 3.5339 | 3.5404 | 3.5485 | 3.5545 | 3.5622 | 3.5697 | 3.5805 | 3.5908 | 3.6006 | 3.6119 | 3.6227 | 3.6351 | 3.6449 | 3.6581 | 3.6688 | 3.6829 | 3.7444 | 3.8064
|  |  |  | Best View [MW] |  |  | 3.5339 | 3.5434 | 3.5525 | 3.5612 | 3.5696 | 3.5795 | 3.5946 | 3.6087 | 3.6239 | 3.6401 | 3.6573 | 3.6732 | 3.6921 | 3.7097 | 3.7281 | 3.7472 | 3.8409 | 3.9346
|  |  |  | Base Case [MW] |  |  | 3.5339 | 3.5455 | 3.5564 | 3.5687 | 3.5804 | 3.5915 | 3.6094 | 3.6261 | 3.6437 | 3.6619 | 3.6809 | 3.6983 | 3.7184 | 3.739 | 3.7621 | 3.7834 | 3.8945 | 4.0054
|  |  |  | Aggressive [MW] |  |  | 3.5339 | 3.5508 | 3.5704 | 3.5883 | 3.6087 | 3.6274 | 3.6481 | 3.6693 | 3.6906 | 3.7141 | 3.7376 | 3.761 | 3.7863 | 3.8134 | 3.8399 | 3.8679 | 4.004 | 4.1403
| RINAWADE | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
| RINEANNA | 10 | 1 | Conservative [MW] |  |  | 14.7381 | 14.8036 | 14.8693 | 14.9312 | 14.9979 | 15.0693 | 15.143 | 15.2203 | 15.3009 | 15.3797 | 15.4617 | 15.5417 | 15.6289 | 15.7088 | 15.7955 | 15.8845 | 16.3234 | 16.7626
|  |  |  | Best View [MW] |  |  | 14.7381 | 14.8041 | 14.8701 | 14.9365 | 15.0077 | 15.0743 | 15.1795 | 15.2831 | 15.3942 | 15.503 | 15.6133 | 15.7299 | 15.8418 | 15.9639 | 16.0801 | 16.1996 | 16.7883 | 17.3775
|  |  |  | Base Case [MW] |  |  | 14.7381 | 14.8275 | 14.9226 | 15.014 | 15.1105 | 15.2069 | 15.328 | 15.4531 | 15.5808 | 15.7106 | 15.8464 | 15.9774 | 16.1174 | 16.2561 | 16.397 | 16.5381 | 17.2431 | 17.9482
|  |  |  | Aggressive [MW] |  |  | 14.7381 | 14.8846 | 15.0371 | 15.1901 | 15.3507 | 15.5181 | 15.6588 | 15.798 | 15.9439 | 16.0953 | 16.2463 | 16.4003 | 16.5556 | 16.71 | 16.8671 | 17.0247 | 17.8114 | 18.5982
| RINGASKIDDY 110KV | 10 | 1 | Conservative [MW] |  |  | 7.3536 | 7.3726 | 7.3905 | 7.4097 | 7.43 | 7.4514 | 7.4705 | 7.4908 | 7.5121 | 7.5345 | 7.5559 | 7.5781 | 7.6014 | 7.6257 | 7.6508 | 7.6746 | 7.7972 | 7.9196
|  |  |  | Best View [MW] |  |  | 7.3536 | 7.3728 | 7.3929 | 7.4141 | 7.4344 | 7.4556 | 7.4843 | 7.5113 | 7.5406 | 7.57 | 7.6017 | 7.6333 | 7.6669 | 7.7004 | 7.7357 | 7.7707 | 7.9465 | 8.1222
|  |  |  | Base Case [MW] |  |  | 7.3536 | 7.3804 | 7.4075 | 7.4367 | 7.466 | 7.4974 | 7.5255 | 7.5558 | 7.5862 | 7.6167 | 7.6492 | 7.6837 | 7.7179 | 7.7519 | 7.7875 | 7.8248 | 8.007 | 8.1895
|  |  |  | Aggressive [MW] |  |  | 7.3536 | 7.3874 | 7.4226 | 7.4587 | 7.4959 | 7.5339 | 7.5733 | 7.6115 | 7.6527 | 7.6965 | 7.7387 | 7.7853 | 7.8319 | 7.8826 | 7.9329 | 7.9845 | 8.2391 | 8.4939
| RIVERSTOWN | 10 | 1 | Conservative [MW] |  |  | 6.2351 | 6.2715 | 6.3138 | 6.3576 | 6.3979 | 6.4396 | 5.8937 | 5.9365 | 5.9801 | 6.0247 | 6.0701 | 6.1162 | 6.1629 | 6.2099 | 6.2614 | 6.3089 | 6.5571 | 6.8046
|  |  |  | Best View [MW] |  |  | 6.2351 | 6.2747 | 6.3199 | 6.3613 | 6.4086 | 6.4518 | 5.9225 | 5.9795 | 6.0388 | 6.1002 | 6.1634 | 6.2284 | 6.2905 | 6.3577 | 6.4255 | 6.489 | 6.8181 | 7.1465
|  |  |  | Base Case [MW] |  |  | 6.2351 | 6.2925 | 6.3524 | 6.4099 | 6.4743 | 6.5356 | 6.0075 | 6.0677 | 6.1297 | 6.1936 | 6.2589 | 6.3253 | 6.3881 | 6.4556 | 6.523 | 6.5898 | 6.9252 | 7.2606
|  |  |  | Aggressive [MW] |  |  | 6.2351 | 6.3053 | 6.3788 | 6.4556 | 6.535 | 6.6162 | 6.1037 | 6.1833 | 6.2681 | 6.3495 | 6.431 | 6.5158 | 6.6032 | 6.6878 | 6.7728 | 6.8623 | 7.2978 | 7.7342
| ROCHES STREET | 10 | 1 | Conservative [MW] |  |  | 14.8567 | 14.9125 | 14.9696 | 15.0283 | 15.0836 | 15.1443 | 15.2084 | 15.2769 | 15.3454 | 15.4179 | 15.4904 | 15.5623 | 15.6337 | 15.709 | 15.7877 | 15.8658 | 16.2578 | 16.6497
|  |  |  | Best View [MW] |  |  | 14.8567 | 14.9137 | 14.9721 | 15.0317 | 15.0921 | 15.1492 | 15.2407 | 15.3331 | 15.4302 | 15.5233 | 15.625 | 15.7265 | 15.8271 | 15.9353 | 16.0417 | 16.1501 | 16.6868 | 17.2239
|  |  |  | Base Case [MW] |  |  | 14.8567 | 14.9359 | 15.0179 | 15.0982 | 15.1805 | 15.2652 | 15.375 | 15.4826 | 15.5963 | 15.7111 | 15.8311 | 15.9512 | 16.0748 | 16.2019 | 16.3308 | 16.4611 | 17.1089 | 17.757
|  |  |  | Aggressive [MW] |  |  | 14.8567 | 14.9844 | 15.1136 | 15.2525 | 15.3911 | 15.5369 | 15.6632 | 15.7878 | 15.9196 | 16.0569 | 16.1946 | 16.3315 | 16.4765 | 16.6226 | 16.7747 | 16.9261 | 17.685 | 18.4437
| ROOSKY | 10 | 1 | Conservative [MW] |  |  | 3.9604 | 3.9666 | 3.9747 | 3.9804 | 3.9882 | 3.9957 | 4.0155 | 4.032 | 4.0516 | 4.0699 | 4.0891 | 4.1092 | 4.1301 | 4.1518 | 4.172 | 4.1927 | 4.2949 | 4.3973
|  |  |  | Best View [MW] |  |  | 3.9604 | 3.9731 | 3.9893 | 4.0025 | 4.0193 | 4.0352 | 4.056 | 4.0794 | 4.101 | 4.1251 | 4.1494 | 4.1738 | 4.2006 | 4.2273 | 4.2539 | 4.2803 | 4.4127 | 4.5451
|  |  |  | Base Case [MW] |  |  | 3.9604 | 3.9763 | 3.9931 | 4.0111 | 4.03 | 4.0478 | 4.0749 | 4.1037 | 4.1339 | 4.1655 | 4.1959 | 4.2274 | 4.2621 | 4.2951 | 4.3308 | 4.3668 | 4.5462 | 4.7256
|  |  |  | Aggressive [MW] |  |  | 3.9604 | 3.9867 | 4.0144 | 4.0435 | 4.0738 | 4.1052 | 4.1413 | 4.1793 | 4.219 | 4.26 | 4.302 | 4.3446 | 4.3898 | 4.4347 | 4.4811 | 4.5311 | 4.7715 | 5.0124
| ROSBERCON | 10 | 1 | Conservative [MW] |  |  | 1.7853 | 1.797 | 1.8098 | 1.8232 | 1.8362 | 1.8495 | 1.8667 | 1.8843 | 1.9024 | 1.9212 | 1.94 | 1.9594 | 1.9792 | 1.9995 | 2.0199 | 2.0413 | 2.1454 | 2.2498
|  |  |  | Best View [MW] |  |  | 1.7853 | 1.7984 | 1.8126 | 1.8273 | 1.8415 | 1.8566 | 1.8788 | 1.9016 | 1.9251 | 1.9491 | 1.9741 | 1.9996 | 2.0261 | 2.0526 | 2.0805 | 2.1083 | 2.2476 | 2.3868
|  |  |  | Base Case [MW] |  |  | 1.7853 | 1.801 | 1.8178 | 1.8352 | 1.852 | 1.8697 | 1.8958 | 1.9231 | 1.9509 | 1.9798 | 2.0091 | 2.04 | 2.0712 | 2.1039 | 2.1369 | 2.1704 | 2.3365 | 2.5027
|  |  |  | Aggressive [MW] |  |  | 1.7853 | 1.8105 | 1.8374 | 1.8654 | 1.8932 | 1.9231 | 1.9567 | 1.9913 | 2.0275 | 2.0645 | 2.1029 | 2.1429 | 2.1834 | 2.225 | 2.2679 | 2.3028 | 2.4987 | 2.6933
|  | 20 | 1 | Conservative [MW] |  |  | 0.87157 | 0.86522 | 0.86548 | 0.86577 | 0.8698 | 0.86854 | 0.86605 | 0.86436 | 0.86494 | 0.86548 | 0.86605 | 0.86674 | 0.86728 | 0.86797 | 0.86868 | 0.86937 | 0.87288 | 0.87638
|  |  |  | Best View [MW] |  |  | 0.87157 | 0.86534 | 0.86577 | 0.86631 | 0.86688 | 0.86494 | 0.86465 | 0.86534 | 0.86591 | 0.8666 | 0.86728 | 0.86811 | 0.86883 | 0.86966 | 0.87049 | 0.87132 | 0.87546 | 0.87961
|  |  |  | Base Case [MW] |  |  | 0.87157 | 0.86548 | 0.86605 | 0.8666 | 0.86522 | 0.86451 | 0.86522 | 0.86591 | 0.86674 | 0.86743 | 0.86826 | 0.86909 | 0.87006 | 0.87103 | 0.872 | 0.86717 | 0.85847 | 0.84881
|  |  |  | Aggressive [MW] |  |  | 0.87157 | 0.86577 | 0.86674 | 0.86771 | 0.86522 | 0.86605 | 0.86702 | 0.86811 | 0.86937 | 0.87063 | 0.87186 | 0.86591 | 0.86508 | 0.86605 | 0.86728 | 0.65111 | 0.14999 | -0.0001
| ROSCOMMON | 10 | 1 | Conservative [MW] |  |  | 5.0542 | 5.0836 | 5.1131 | 5.1484 | 5.1786 | 5.2088 | 5.2801 | 5.3531 | 5.428 | 5.5037 | 5.581 | 5.6601 | 5.7409 | 5.8221 | 5.906 | 5.9901 | 6.41 | 6.83
|  |  |  | Best View [MW] |  |  | 5.0542 | 5.112 | 5.1716 | 5.2364 | 5.2974 | 5.3593 | 5.4476 | 5.5375 | 5.6291 | 5.7231 | 5.8187 | 5.9164 | 6.0165 | 6.1186 | 6.2215 | 6.3274 | 6.8491 | 7.3712
|  |  |  | Base Case [MW] |  |  | 5.0542 | 5.1231 | 5.1931 | 5.2687 | 5.3409 | 5.4157 | 5.5256 | 5.6399 | 5.7563 | 5.8769 | 5.9993 | 6.1254 | 6.2538 | 6.385 | 6.5178 | 6.6542 | 7.3264 | 7.9992
|  |  |  | Aggressive [MW] |  |  | 5.0542 | 5.1641 | 5.2778 | 5.3997 | 5.5206 | 5.6446 | 5.7882 | 5.9372 | 6.0892 | 6.2458 | 6.4078 | 6.5718 | 6.7408 | 6.9122 | 7.0858 | 7.263 | 8.1395 | 9.0166
|  | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0.15545 | 0.15545 | 0.1554 | 0.15536 | 0.15531 | 0.15521 | 0.15517 | 0.15512 | 0.15502 | 0.15498 | 0.15488 | 0.15483 | 0.15474 | 0.15439 | 0.15404
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0.1554 | 0.15536 | 0.15531 | 0.15521 | 0.15512 | 0.15507 | 0.15498 | 0.15488 | 0.15479 | 0.15474 | 0.15465 | 0.15455 | 0.15441 | 0.15382 | 0.15323
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0.15536 | 0.15531 | 0.15526 | 0.15517 | 0.15507 | 0.15493 | 0.15483 | 0.15474 | 0.1546 | 0.1545 | 0.15436 | 0.15422 | 0.15413 | 0.15354 | 0.15297
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0.15526 | 0.15517 | 0.15507 | 0.15493 | 0.15479 | 0.15465 | 0.1545 | 0.15436 | 0.15417 | 0.15404 | 0.15385 | 0.15361 | 0.15323 | 0.15172 | 0.15018
| ROSCREA | 10 | 1 | Conservative [MW] |  |  | 14.0938 | 14.1488 | 14.2059 | 14.2597 | 14.3198 | 14.3734 | 14.4549 | 14.5347 | 14.617 | 14.7016 | 14.7884 | 14.8771 | 14.963 | 15.0548 | 15.1432 | 15.2371 | 15.6921 | 16.1479
|  |  |  | Best View [MW] |  |  | 14.0938 | 14.1611 | 14.2327 | 14.3003 | 14.3721 | 14.4403 | 14.5575 | 14.6794 | 14.8006 | 14.9298 | 15.0566 | 15.1853 | 15.3194 | 15.4535 | 15.5915 | 15.7273 | 16.4124 | 17.097
|  |  |  | Base Case [MW] |  |  | 14.0938 | 14.186 | 14.2795 | 14.3735 | 14.4726 | 14.5679 | 14.6973 | 14.8283 | 14.9602 | 15.1016 | 15.2419 | 15.3849 | 15.5292 | 15.6738 | 15.8217 | 15.9714 | 16.7154 | 17.4596
|  |  |  | Aggressive [MW] |  |  | 14.0938 | 14.2397 | 14.3885 | 14.5387 | 14.6981 | 14.8557 | 15.0018 | 15.1529 | 15.3084 | 15.4616 | 15.621 | 15.7843 | 15.9446 | 16.1047 | 16.268 | 16.4257 | 17.2292 | 18.0318
| ROSEHILL | 10 | 1 | Conservative [MW] |  |  | 13.905 | 13.9591 | 14.0154 | 14.0682 | 14.1232 | 13.7895 | 13.8705 | 13.9542 | 14.0404 | 14.1243 | 14.2146 | 14.3019 | 14.3904 | 14.4846 | 14.5754 | 14.6711 | 15.1365 | 15.6027
|  |  |  | Best View [MW] |  |  | 13.905 | 13.9697 | 14.0391 | 14.1043 | 14.1747 | 13.8501 | 13.9627 | 14.0769 | 14.1923 | 14.3126 | 14.4324 | 14.5563 | 14.6828 | 14.8116 | 14.9374 | 15.0683 | 15.7092 | 16.351
|  |  |  | Base Case [MW] |  |  | 13.905 | 13.9836 | 14.0609 | 14.1412 | 14.2244 | 13.9163 | 14.0514 | 14.1873 | 14.3273 | 14.4711 | 14.6166 | 14.7678 | 14.9189 | 15.0729 | 15.2283 | 15.3881 | 16.1754 | 16.9634
|  |  |  | Aggressive [MW] |  |  | 13.905 | 14.0371 | 14.1664 | 14.306 | 14.4456 | 14.1959 | 14.368 | 14.5474 | 14.7274 | 14.9104 | 15.0985 | 15.284 | 15.4784 | 15.6685 | 15.8611 | 16.0526 | 17.0129 | 17.9731
| ROSS CARBERY | 10 | 1 | Conservative [MW] |  |  | 1.5321 | 1.5545 | 1.5768 | 1.6003 | 1.6237 | 1.6479 | 1.6721 | 1.6972 | 1.7225 | 1.7482 | 1.7747 | 1.8015 | 1.8292 | 1.8572 | 1.886 | 1.9158 | 2.0621 | 2.2085
|  |  |  | Best View [MW] |  |  | 1.5321 | 1.5554 | 1.5795 | 1.604 | 1.6292 | 1.6549 | 1.6877 | 1.7215 | 1.7565 | 1.7925 | 1.8292 | 1.8669 | 1.9063 | 1.9463 | 1.9874 | 2.0302 | 2.2396 | 2.4494
|  |  |  | Base Case [MW] |  |  | 1.5321 | 1.5642 | 1.5976 | 1.6318 | 1.6672 | 1.7033 | 1.738 | 1.7734 | 1.8097 | 1.8472 | 1.8859 | 1.9256 | 1.9664 | 2.0079 | 2.051 | 2.0952 | 2.3135 | 2.5319
|  |  |  | Aggressive [MW] |  |  | 1.5321 | 1.5766 | 1.6227 | 1.6715 | 1.7218 | 1.7748 | 1.8121 | 1.8501 | 1.8897 | 1.93 | 1.972 | 2.0145 | 2.0588 | 2.1042 | 2.15 | 2.1984 | 2.4334 | 2.6689
| ROSSGEIR | 10 | 1 | Conservative [MW] |  |  | 6.4108 | 6.4263 | 6.438 | 6.453 | 6.4677 | 6.4822 | 6.5192 | 6.5545 | 6.5916 | 6.6269 | 6.664 | 6.7029 | 6.7396 | 6.7817 | 6.8215 | 6.859 | 7.0526 | 7.2458
|  |  |  | Best View [MW] |  |  | 6.4108 | 6.4437 | 6.4754 | 6.509 | 6.5413 | 6.5755 | 6.6252 | 6.6784 | 6.7316 | 6.7879 | 6.8437 | 6.8986 | 6.9602 | 7.0165 | 7.0791 | 7.1397 | 7.448 | 7.756
|  |  |  | Base Case [MW] |  |  | 6.4108 | 6.4448 | 6.4806 | 6.5182 | 6.5577 | 6.5951 | 6.6563 | 6.7157 | 6.7809 | 6.8478 | 6.9119 | 6.9806 | 7.054 | 7.1233 | 7.1963 | 7.2728 | 7.6458 | 8.0194
|  |  |  | Aggressive [MW] |  |  | 6.4108 | 6.4636 | 6.5196 | 6.5785 | 6.6365 | 6.6969 | 6.7672 | 6.8449 | 6.9215 | 7.0008 | 7.0817 | 7.1682 | 7.251 | 7.3419 | 7.4318 | 7.519 | 7.9621 | 8.4047
| SAGGART | 10 | 1 | Conservative [MW] |  |  | 6.5963 | 6.644 | 6.6924 | 6.7365 | 6.7856 | 6.8347 | 6.876 | 6.9144 | 6.9545 | 6.9964 | 7.035 | 7.075 | 7.1165 | 7.1592 | 7.2032 | 7.2482 | 7.4705 | 7.693
|  |  |  | Best View [MW] |  |  | 6.5963 | 6.6483 | 6.7043 | 6.7591 | 6.8173 | 6.8739 | 6.9215 | 6.9696 | 7.0135 | 7.0625 | 7.1116 | 7.1608 | 7.2098 | 7.2633 | 7.3167 | 7.364 | 7.6165 | 7.8681
|  |  |  | Base Case [MW] |  |  | 6.5963 | 6.6589 | 6.7193 | 6.7815 | 6.8457 | 6.9109 | 6.9624 | 7.0182 | 7.0732 | 7.1272 | 7.1797 | 7.2358 | 7.295 | 7.3522 | 7.4123 | 7.4692 | 7.7622 | 8.0547
|  |  |  | Aggressive [MW] |  |  | 6.5963 | 6.6847 | 6.7768 | 6.8669 | 6.9681 | 7.0642 | 7.1192 | 7.1685 | 7.2221 | 7.2747 | 7.3312 | 7.3861 | 7.4393 | 7.4956 | 7.5549 | 7.6111 | 7.9005 | 8.1894
| SALLINS | 10 | 1 | Conservative [MW] |  |  | 11.9202 | 12.0026 | 12.0826 | 12.1693 | 12.2581 | 12.3479 | 12.419 | 12.4849 | 12.5601 | 12.6301 | 12.704 | 12.782 | 12.8542 | 12.935 | 13.0095 | 13.092 | 13.4831 | 13.8756
|  |  |  | Best View [MW] |  |  | 11.9202 | 12.0118 | 12.1128 | 12.2085 | 12.3127 | 12.4156 | 12.5005 | 12.5831 | 12.6683 | 12.7553 | 12.8438 | 12.9341 | 13.0256 | 13.1181 | 13.211 | 13.3092 | 13.786 | 14.2637
|  |  |  | Base Case [MW] |  |  | 11.9202 | 12.0239 | 12.1342 | 12.2458 | 12.3635 | 12.4854 | 12.5796 | 12.6739 | 12.7683 | 12.8677 | 12.9707 | 13.0731 | 13.1785 | 13.2819 | 13.3931 | 13.5016 | 14.0513 | 14.6006
|  |  |  | Aggressive [MW] |  |  | 11.9202 | 12.0721 | 12.2357 | 12.4051 | 12.5785 | 12.7608 | 12.8537 | 12.9524 | 13.0461 | 13.1444 | 13.2423 | 13.3446 | 13.4456 | 13.5496 | 13.6567 | 13.7658 | 14.306 | 14.8465
| SALLYNOGGIN ROAD | 10 | 1 | Conservative [MW] |  |  | 11.3581 | 11.4295 | 11.496 | 11.5706 | 11.6441 | 11.7169 | 11.7775 | 11.8347 | 11.8973 | 11.9608 | 12.0205 | 12.085 | 12.1503 | 12.2159 | 12.2862 | 12.3518 | 12.6925 | 13.0324
|  |  |  | Best View [MW] |  |  | 11.3581 | 11.4369 | 11.5221 | 11.605 | 11.6894 | 11.7796 | 11.8487 | 11.9175 | 11.9901 | 12.0665 | 12.1419 | 12.221 | 12.2983 | 12.3787 | 12.4575 | 12.5436 | 12.9544 | 13.3665
|  |  |  | Base Case [MW] |  |  | 11.3581 | 11.4504 | 11.5388 | 11.636 | 11.7326 | 11.8331 | 11.9141 | 11.9932 | 12.0789 | 12.1626 | 12.2481 | 12.3398 | 12.4283 | 12.5224 | 12.6173 | 12.7127 | 13.1884 | 13.6642
|  |  |  | Aggressive [MW] |  |  | 11.3581 | 11.4889 | 11.6237 | 11.7658 | 11.9136 | 12.0704 | 12.1488 | 12.2299 | 12.3134 | 12.3996 | 12.4874 | 12.5723 | 12.6637 | 12.7562 | 12.8498 | 12.9436 | 13.4123 | 13.881
| SANDYFORD | 10 | 1 | Conservative [MW] |  |  | 12.5713 | 12.647 | 12.7258 | 12.8117 | 12.8952 | 12.9809 | 13.0445 | 13.1131 | 13.1858 | 13.2541 | 13.3271 | 13.3992 | 13.4709 | 13.5467 | 13.6217 | 13.6956 | 14.068 | 14.4402
|  |  |  | Best View [MW] |  |  | 12.5713 | 12.6584 | 12.755 | 12.8478 | 12.9449 | 13.046 | 13.1258 | 13.2087 | 13.2896 | 13.3729 | 13.4584 | 13.5465 | 13.6361 | 13.7274 | 13.8152 | 13.9088 | 14.3614 | 14.8149
|  |  |  | Base Case [MW] |  |  | 12.5713 | 12.6718 | 12.7755 | 12.8862 | 12.9943 | 13.1129 | 13.2038 | 13.2956 | 13.3887 | 13.4819 | 13.5802 | 13.6829 | 13.785 | 13.8862 | 13.9908 | 14.0979 | 14.6267 | 15.1559
|  |  |  | Aggressive [MW] |  |  | 12.5713 | 12.7184 | 12.8744 | 13.0331 | 13.2021 | 13.3794 | 13.4701 | 13.5626 | 13.6555 | 13.7493 | 13.8482 | 13.9468 | 14.0451 | 14.147 | 14.2475 | 14.3508 | 14.86 | 15.3696
| SANTRY | 10 | 1 | Conservative [MW] |  |  | 14.1804 | 14.2749 | 14.3733 | 14.4754 | 14.5806 | 14.684 | 14.7492 | 14.8108 | 14.8774 | 14.9399 | 15.0075 | 15.0709 | 15.1393 | 15.2077 | 15.2805 | 15.3489 | 15.7027 | 16.0557
|  |  |  | Best View [MW] |  |  | 14.1804 | 14.2827 | 14.3914 | 14.506 | 14.6215 | 14.7415 | 14.8162 | 14.89 | 14.9633 | 15.0403 | 15.1162 | 15.1955 | 15.2733 | 15.3543 | 15.4382 | 15.5201 | 15.9349 | 16.3493
|  |  |  | Base Case [MW] |  |  | 14.1804 | 14.2938 | 14.4157 | 14.5408 | 14.6685 | 14.8022 | 14.8853 | 14.9664 | 15.0543 | 15.1396 | 15.2266 | 15.3199 | 15.4101 | 15.5012 | 15.5977 | 15.6946 | 16.1779 | 16.6612
|  |  |  | Aggressive [MW] |  |  | 14.1804 | 14.3208 | 14.4714 | 14.6263 | 14.7887 | 14.9566 | 15.0342 | 15.1112 | 15.1868 | 15.2656 | 15.3477 | 15.4282 | 15.5112 | 15.5965 | 15.6798 | 15.7695 | 16.2008 | 16.6332
| SCARIFF | 10 | 1 | Conservative [MW] |  |  | 3.9694 | 3.9826 | 3.9952 | 4.0093 | 4.0229 | 4.0358 | 4.053 | 4.0735 | 4.0927 | 4.1106 | 4.1317 | 4.1513 | 4.1718 | 4.1929 | 4.2148 | 4.2374 | 4.3485 | 4.4596
|  |  |  | Best View [MW] |  |  | 3.9694 | 3.9841 | 3.9982 | 4.0114 | 4.0283 | 4.0422 | 4.0677 | 4.0952 | 4.1224 | 4.1513 | 4.1817 | 4.2114 | 4.2426 | 4.2725 | 4.306 | 4.3379 | 4.5016 | 4.6651
|  |  |  | Base Case [MW] |  |  | 3.9694 | 3.9919 | 4.0147 | 4.0378 | 4.0632 | 4.0888 | 4.1179 | 4.1485 | 4.1801 | 4.2128 | 4.2462 | 4.2804 | 4.3149 | 4.3496 | 4.3868 | 4.4233 | 4.6077 | 4.7919
|  |  |  | Aggressive [MW] |  |  | 3.9694 | 4.0088 | 4.049 | 4.0939 | 4.1388 | 4.1851 | 4.221 | 4.2549 | 4.2934 | 4.3295 | 4.3674 | 4.4068 | 4.4475 | 4.4891 | 4.5313 | 4.5735 | 4.7844 | 4.9954
| SCARTEEN | 10 | 1 | Conservative [MW] |  |  | 2.17 | 2.2157 | 2.2615 | 2.3089 | 2.3563 | 2.4045 | 2.4533 | 2.5027 | 2.5529 | 2.6037 | 2.6552 | 2.7072 | 2.7598 | 2.8128 | 2.8672 | 2.9208 | 3.1909 | 3.461
|  |  |  | Best View [MW] |  |  | 2.17 | 2.2183 | 2.2667 | 2.3166 | 2.3673 | 2.4189 | 2.4845 | 2.5507 | 2.6191 | 2.6888 | 2.7587 | 2.8306 | 2.9033 | 2.9768 | 3.0507 | 3.1258 | 3.4983 | 3.871
|  |  |  | Base Case [MW] |  |  | 2.17 | 2.2359 | 2.3027 | 2.3711 | 2.4411 | 2.5134 | 2.5813 | 2.6506 | 2.7211 | 2.7926 | 2.865 | 2.9392 | 3.014 | 3.0891 | 3.1641 | 3.2413 | 3.6216 | 4.0022
|  |  |  | Aggressive [MW] |  |  | 2.17 | 2.2612 | 2.3549 | 2.4509 | 2.5506 | 2.653 | 2.7256 | 2.7993 | 2.8738 | 2.9489 | 3.0255 | 3.1034 | 3.1813 | 3.2585 | 3.3375 | 3.415 | 3.8065 | 4.1978
| SCREEB | 10 | 1 | Conservative [MW] |  |  | 4.0704 | 4.0836 | 4.0982 | 4.1122 | 4.1255 | 4.1404 | 4.1601 | 4.1785 | 4.2001 | 4.2202 | 4.241 | 4.2626 | 4.2849 | 4.3054 | 4.3289 | 4.3506 | 4.4638 | 4.5768
|  |  |  | Best View [MW] |  |  | 4.0704 | 4.0866 | 4.104 | 4.1225 | 4.14 | 4.1586 | 4.1862 | 4.2157 | 4.2445 | 4.2747 | 4.3041 | 4.3369 | 4.3685 | 4.4009 | 4.4341 | 4.4702 | 4.6429 | 4.8162
|  |  |  | Base Case [MW] |  |  | 4.0704 | 4.0915 | 4.1131 | 4.1375 | 4.1601 | 4.183 | 4.2152 | 4.2461 | 4.2803 | 4.3129 | 4.3483 | 4.3816 | 4.4197 | 4.4553 | 4.4928 | 4.5321 | 4.7239 | 4.9159
|  |  |  | Aggressive [MW] |  |  | 4.0704 | 4.105 | 4.1399 | 4.1749 | 4.212 | 4.2508 | 4.2897 | 4.3279 | 4.3677 | 4.4085 | 4.4526 | 4.4946 | 4.539 | 4.5829 | 4.6282 | 4.6745 | 4.9034 | 5.1324
| SEMPERIT | 10 | 1 | Conservative [MW] |  |  | 31.7752 | 32.0306 | 32.2909 | 32.5548 | 32.8206 | 33.0927 | 33.2457 | 33.3974 | 33.5488 | 33.7057 | 33.8602 | 34.0193 | 34.1743 | 34.3334 | 34.4871 | 34.6349 | 35.3898 | 36.1437
|  |  |  | Best View [MW] |  |  | 31.7752 | 32.0573 | 32.3437 | 32.6318 | 32.9335 | 33.2299 | 33.4026 | 33.585 | 33.7598 | 33.9415 | 34.1214 | 34.299 | 34.4732 | 34.6511 | 34.8227 | 34.9951 | 35.8548 | 36.7146
|  |  |  | Base Case [MW] |  |  | 31.7752 | 32.0797 | 32.3998 | 32.718 | 33.0461 | 33.3766 | 33.5746 | 33.7748 | 33.9757 | 34.1755 | 34.3742 | 34.5693 | 34.767 | 34.9674 | 35.1501 | 35.3325 | 36.2453 | 37.1581
|  |  |  | Aggressive [MW] |  |  | 31.7752 | 32.1531 | 32.54 | 32.9358 | 33.3404 | 33.7483 | 33.926 | 34.1019 | 34.2842 | 34.4545 | 34.6367 | 34.8051 | 34.9832 | 35.1513 | 35.3135 | 35.4629 | 36.2439 | 37.0228
| SHANNON | 10 | 1 | Conservative [MW] |  |  | 9.1217 | 9.1876 | 9.2545 | 9.3224 | 9.3912 | 9.4622 | 9.5407 | 9.6226 | 9.7037 | 9.7882 | 9.8718 | 9.9587 | 10.0461 | 10.1352 | 10.2259 | 10.3166 | 10.7704 | 11.2241
|  |  |  | Best View [MW] |  |  | 9.1217 | 9.189 | 9.2573 | 9.3276 | 9.3978 | 9.4701 | 9.5785 | 9.6883 | 9.8008 | 9.916 | 10.0337 | 10.1535 | 10.277 | 10.4007 | 10.5293 | 10.6574 | 11.2995 | 11.9414
|  |  |  | Base Case [MW] |  |  | 9.1217 | 9.2144 | 9.3092 | 9.407 | 9.5055 | 9.6082 | 9.7344 | 9.8656 | 10.0001 | 10.1364 | 10.277 | 10.42 | 10.5668 | 10.7153 | 10.8666 | 11.0222 | 11.7886 | 12.5558
|  |  |  | Aggressive [MW] |  |  | 9.1217 | 9.2719 | 9.428 | 9.5902 | 9.7576 | 9.9312 | 10.0783 | 10.2294 | 10.384 | 10.5432 | 10.7048 | 10.8701 | 11.0382 | 11.2084 | 11.3817 | 11.5572 | 12.4289 | 13.3009
| SHERCOCK | 10 | 1 | Conservative [MW] |  |  | 7.9658 | 8.005 | 8.0413 | 8.0748 | 8.1156 | 8.1533 | 8.2022 | 8.2553 | 8.3073 | 8.3632 | 8.417 | 8.4691 | 8.5239 | 8.5762 | 8.6309 | 8.6818 | 8.9462 | 9.21
|  |  |  | Best View [MW] |  |  | 7.9658 | 8.0155 | 8.0607 | 8.1061 | 8.1566 | 8.2072 | 8.2745 | 8.3453 | 8.419 | 8.4951 | 8.5675 | 8.6405 | 8.7132 | 8.7857 | 8.8561 | 8.9295 | 9.2886 | 9.6481
|  |  |  | Base Case [MW] |  |  | 7.9658 | 8.0272 | 8.0816 | 8.1437 | 8.2028 | 8.2639 | 8.3447 | 8.4204 | 8.501 | 8.5856 | 8.6617 | 8.7455 | 8.8247 | 8.903 | 8.9786 | 9.05 | 9.4182 | 9.7857
|  |  |  | Aggressive [MW] |  |  | 7.9658 | 8.0544 | 8.1457 | 8.2437 | 8.337 | 8.429 | 8.5292 | 8.6247 | 8.7191 | 8.8169 | 8.909 | 9.0046 | 9.0883 | 9.1684 | 9.237 | 9.2901 | 9.5968 | 9.9009
| SHERIFF STREET | 10 | 1 | Conservative [MW] |  |  | 13.5433 | 13.5845 | 13.6238 | 13.6688 | 13.7114 | 13.7557 | 13.7946 | 13.8352 | 13.878 | 13.9227 | 13.969 | 14.013 | 14.059 | 14.1065 | 14.1554 | 14.206 | 14.4545 | 14.7032
|  |  |  | Best View [MW] |  |  | 13.5433 | 13.5896 | 13.6368 | 13.6892 | 13.7384 | 13.792 | 13.8368 | 13.8871 | 13.9345 | 13.9835 | 14.0374 | 14.0885 | 14.1405 | 14.1975 | 14.2554 | 14.3136 | 14.6039 | 14.8943
|  |  |  | Base Case [MW] |  |  | 13.5433 | 13.5968 | 13.6544 | 13.712 | 13.7732 | 13.8338 | 13.8849 | 13.941 | 13.9937 | 14.0512 | 14.1091 | 14.1674 | 14.2301 | 14.2927 | 14.3553 | 14.4219 | 14.7441 | 15.0669
|  |  |  | Aggressive [MW] |  |  | 13.5433 | 13.637 | 13.7352 | 13.8368 | 13.9491 | 14.067 | 14.1209 | 14.1796 | 14.2392 | 14.2988 | 14.3588 | 14.4232 | 14.4876 | 14.556 | 14.624 | 14.6916 | 15.0307 | 15.3698
| SHILLELAGH | 20 | 1 | Conservative [MW] |  |  | 2.4675 | 2.5048 | 2.5429 | 2.5819 | 2.6207 | 2.6611 | 2.712 | 2.7634 | 2.8164 | 2.8688 | 2.9226 | 2.9767 | 3.0322 | 3.088 | 3.1437 | 3.1992 | 3.4774 | 3.7556
|  |  |  | Best View [MW] |  |  | 2.4675 | 2.5146 | 2.5624 | 2.611 | 2.6604 | 2.7108 | 2.7784 | 2.8472 | 2.9181 | 2.9888 | 3.0613 | 3.1342 | 3.2087 | 3.2831 | 3.3574 | 3.4332 | 3.8083 | 4.1836
|  |  |  | Base Case [MW] |  |  | 2.4675 | 2.5271 | 2.5891 | 2.6509 | 2.7151 | 2.7795 | 2.8562 | 2.9337 | 3.0139 | 3.0943 | 3.1758 | 3.2581 | 3.3408 | 3.4247 | 3.5096 | 3.5931 | 4.0143 | 4.4353
|  |  |  | Aggressive [MW] |  |  | 2.4675 | 2.5491 | 2.6329 | 2.7188 | 2.807 | 2.8968 | 3.0008 | 3.1081 | 3.2155 | 3.3263 | 3.4371 | 3.5477 | 3.6583 | 3.7657 | 3.8698 | 3.9635 | 4.4599 | 4.9546
| SKIBBEREEN | 10 | 1 | Conservative [MW] |  |  | 2.4128 | 2.4599 | 8.9133 | 8.9739 | 9.0358 | 9.097 | 9.1595 | 9.2245 | 9.2889 | 9.356 | 9.4238 | 9.4925 | 9.562 | 9.6339 | 9.7065 | 9.7814 | 10.1498 | 10.5186
|  |  |  | Best View [MW] |  |  | 2.4128 | 2.4622 | 8.9202 | 8.9835 | 9.0493 | 9.1147 | 9.2002 | 9.2878 | 9.3773 | 9.4688 | 9.562 | 9.6586 | 9.7584 | 9.8598 | 9.962 | 10.0691 | 10.5916 | 11.1149
|  |  |  | Base Case [MW] |  |  | 2.4128 | 2.4816 | 8.9671 | 9.0563 | 9.1475 | 9.2406 | 9.3292 | 9.4197 | 9.5137 | 9.6095 | 9.7068 | 9.8073 | 9.909 | 10.0136 | 10.1209 | 10.2311 | 10.7743 | 11.318
|  |  |  | Aggressive [MW] |  |  | 2.4128 | 2.5076 | 9.0329 | 9.1583 | 9.2876 | 9.4237 | 9.5189 | 9.6157 | 9.7157 | 9.8188 | 9.923 | 10.03 | 10.1395 | 10.2509 | 10.3652 | 10.4812 | 11.0565 | 11.6321
| SLANE | 20 | 1 | Conservative [MW] |  |  | 0.85848 | 0.88578 | 0.91362 | 0.94209 | 0.97113 | 1.0007 | 1.0378 | 1.0781 | 1.1191 | 1.1608 | 1.2034 | 1.2469 | 1.2916 | 1.3371 | 1.3837 | 1.4314 | 1.6669 | 1.9026
|  |  |  | Best View [MW] |  |  | 0.85848 | 0.89076 | 0.92371 | 0.95751 | 0.9921 | 1.0275 | 1.0755 | 1.1271 | 1.1794 | 1.2332 | 1.2886 | 1.3456 | 1.404 | 1.4642 | 1.526 | 1.5892 | 1.9013 | 2.2137
|  |  |  | Base Case [MW] |  |  | 0.85848 | 0.90391 | 0.95085 | 0.99925 | 1.0494 | 1.1015 | 1.1613 | 1.2241 | 1.289 | 1.3561 | 1.4256 | 1.4971 | 1.5708 | 1.6466 | 1.7249 | 1.8052 | 2.2014 | 2.598
|  |  |  | Aggressive [MW] |  |  | 0.85848 | 0.92007 | 0.98449 | 1.0517 | 1.1217 | 1.1965 | 1.2756 | 1.3604 | 1.4488 | 1.5408 | 1.6361 | 1.7351 | 1.8376 | 1.9432 | 2.0519 | 2.163 | 2.7121 | 3.2616
|  |  | 2 | Conservative [MW] |  |  | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227
|  |  |  | Best View [MW] |  |  | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227
|  |  |  | Base Case [MW] |  |  | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227
|  |  |  | Aggressive [MW] |  |  | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227 | 3.227
| SMEARLA | 10 | 1 | Conservative [MW] |  |  | 8.4204 | 8.4504 | 8.4793 | 8.5094 | 8.5408 | 8.5706 | 8.629 | 8.6885 | 8.7491 | 8.8109 | 8.8753 | 8.9393 | 9.0059 | 9.072 | 9.1405 | 9.2116 | 9.5603 | 9.9095
|  |  |  | Best View [MW] |  |  | 8.4204 | 8.4722 | 8.5264 | 8.5806 | 8.6361 | 8.6913 | 8.7702 | 8.8502 | 8.9323 | 9.0183 | 9.1051 | 9.1939 | 9.2848 | 9.3794 | 9.4757 | 9.5738 | 10.0598 | 10.546
|  |  |  | Base Case [MW] |  |  | 8.4204 | 8.4793 | 8.5393 | 8.6006 | 8.6631 | 8.7265 | 8.8109 | 8.899 | 8.9892 | 9.0817 | 9.1761 | 9.274 | 9.3753 | 9.4783 | 9.5845 | 9.692 | 10.2259 | 10.76
|  |  |  | Aggressive [MW] |  |  | 8.4204 | 8.5122 | 8.6063 | 8.7055 | 8.8068 | 8.9114 | 9.0225 | 9.135 | 9.2538 | 9.3752 | 9.5009 | 9.6303 | 9.7654 | 9.9018 | 10.0451 | 10.1907 | 10.9124 | 11.6346
| SOUTH KING STREET | 10 | 1 | Conservative [MW] |  |  | 15.4091 | 15.4914 | 15.58 | 15.6659 | 15.7577 | 15.8508 | 15.9322 | 16.0202 | 16.1059 | 16.1936 | 16.2828 | 16.3734 | 16.4652 | 16.5624 | 16.6555 | 16.7534 | 17.2302 | 17.7077
|  |  |  | Best View [MW] |  |  | 15.4091 | 15.5065 | 15.6078 | 15.7128 | 15.8161 | 15.9271 | 16.0216 | 16.1165 | 16.2165 | 16.3157 | 16.4192 | 16.5216 | 16.6271 | 16.7357 | 16.8465 | 16.9541 | 17.5004 | 18.0462
|  |  |  | Base Case [MW] |  |  | 15.4091 | 15.5215 | 15.6388 | 15.7603 | 15.8857 | 16.0146 | 16.1191 | 16.2265 | 16.3364 | 16.4487 | 16.5624 | 16.6772 | 16.7924 | 16.912 | 17.036 | 17.1579 | 17.773 | 18.3877
|  |  |  | Aggressive [MW] |  |  | 15.4091 | 15.6027 | 15.808 | 16.0212 | 16.2438 | 16.4809 | 16.5897 | 16.7003 | 16.8121 | 16.9254 | 17.0392 | 17.1577 | 17.2747 | 17.39 | 17.5134 | 17.6332 | 18.2416 | 18.8494
| SPA ROAD | 10 | 1 | Conservative [MW] |  |  | 6.069 | 6.0962 | 6.1227 | 6.1513 | 6.1791 | 6.2062 | 6.2447 | 6.2848 | 6.3233 | 6.3631 | 6.4043 | 6.4469 | 6.4873 | 6.5323 | 6.575 | 6.6187 | 6.8344 | 7.0503
|  |  |  | Best View [MW] |  |  | 6.069 | 6.098 | 6.1289 | 6.1617 | 6.1936 | 6.2274 | 6.2769 | 6.3326 | 6.3883 | 6.4437 | 6.5017 | 6.5624 | 6.6222 | 6.6841 | 6.748 | 6.81 | 7.1248 | 7.4393
|  |  |  | Base Case [MW] |  |  | 6.069 | 6.11 | 6.1493 | 6.1927 | 6.2344 | 6.2771 | 6.3356 | 6.3966 | 6.4599 | 6.522 | 6.5859 | 6.6512 | 6.7212 | 6.7886 | 6.86 | 6.9316 | 7.289 | 7.6465
|  |  |  | Aggressive [MW] |  |  | 6.069 | 6.1303 | 6.1963 | 6.2639 | 6.3327 | 6.4024 | 6.4736 | 6.5425 | 6.6152 | 6.6915 | 6.7673 | 6.8458 | 6.9265 | 7.0088 | 7.0921 | 7.1757 | 7.593 | 8.0103
| SPIDDAL | 20 | 1 | Conservative [MW] |  |  | 4.218 | 4.242 | 4.2669 | 4.2919 | 4.318 | 4.3431 | 4.3788 | 4.4144 | 4.4511 | 4.4889 | 4.5267 | 4.5666 | 4.6053 | 4.6462 | 4.6882 | 4.7299 | 4.9391 | 5.1482
|  |  |  | Best View [MW] |  |  | 4.218 | 4.2487 | 4.2795 | 4.3113 | 4.3432 | 4.3761 | 4.4267 | 4.4794 | 4.5332 | 4.588 | 4.6436 | 4.7026 | 4.761 | 4.8226 | 4.8849 | 4.949 | 5.2646 | 5.5805
|  |  |  | Base Case [MW] |  |  | 4.218 | 4.257 | 4.2962 | 4.3374 | 4.3788 | 4.4212 | 4.4781 | 4.536 | 4.596 | 4.6581 | 4.7221 | 4.788 | 4.8545 | 4.924 | 4.9951 | 5.0676 | 5.4263 | 5.7852
|  |  |  | Aggressive [MW] |  |  | 4.218 | 4.2792 | 4.3417 | 4.4075 | 4.4754 | 4.5454 | 4.6146 | 4.6869 | 4.761 | 4.8367 | 4.9151 | 4.9962 | 5.0797 | 5.1654 | 5.253 | 5.3421 | 5.7835 | 6.2251
| SPRINGS | 20 | 1 | Conservative [MW] |  |  | 4.4208 | 4.4653 | 4.5108 | 4.5566 | 4.6032 | 4.6504 | 4.7138 | 4.7779 | 4.8438 | 4.9114 | 4.9795 | 5.0501 | 5.1212 | 5.194 | 5.2678 | 5.3433 | 5.7164 | 6.0898
|  |  |  | Best View [MW] |  |  | 4.4208 | 4.471 | 4.5222 | 4.5744 | 4.6275 | 4.6811 | 4.7686 | 4.859 | 4.9516 | 5.0463 | 5.144 | 5.2437 | 5.3469 | 5.452 | 5.5597 | 5.67 | 6.2145 | 6.7594
|  |  |  | Base Case [MW] |  |  | 4.4208 | 4.4871 | 4.5553 | 4.6249 | 4.6957 | 4.7686 | 4.8667 | 4.9673 | 5.0708 | 5.1774 | 5.2867 | 5.3997 | 5.5154 | 5.6344 | 5.7559 | 5.8805 | 6.4953 | 7.1106
|  |  |  | Aggressive [MW] |  |  | 4.4208 | 4.5245 | 4.6319 | 4.7434 | 4.859 | 4.9782 | 5.0941 | 5.2133 | 5.337 | 5.4644 | 5.5952 | 5.7293 | 5.8675 | 6.0102 | 6.1553 | 6.3051 | 7.0417 | 7.779
| SRAH | 10 | 1 | Conservative [MW] |  |  | 3.2888 | 3.3167 | 3.3446 | 3.3736 | 3.4037 | 3.4326 | 3.4709 | 3.5102 | 3.5506 | 3.5921 | 3.6334 | 3.6758 | 3.7191 | 3.7635 | 3.8088 | 3.855 | 4.0836 | 4.3124
|  |  |  | Best View [MW] |  |  | 3.2888 | 3.3238 | 3.3598 | 3.3969 | 3.4341 | 3.4734 | 3.5237 | 3.5761 | 3.6295 | 3.685 | 3.7413 | 3.7997 | 3.8588 | 3.9198 | 3.9828 | 4.046 | 4.3613 | 4.6768
|  |  |  | Base Case [MW] |  |  | 3.2888 | 3.3306 | 3.3736 | 3.4176 | 3.4639 | 3.5101 | 3.5707 | 3.6321 | 3.6968 | 3.7622 | 3.8307 | 3.8995 | 3.9714 | 4.0446 | 4.1207 | 4.1977 | 4.5804 | 4.9632
|  |  |  | Aggressive [MW] |  |  | 3.2888 | 3.343 | 3.3984 | 3.4559 | 3.5157 | 3.5775 | 3.652 | 3.7296 | 3.8087 | 3.892 | 3.9777 | 4.0657 | 4.1555 | 4.2485 | 4.3442 | 4.4423 | 4.9263 | 5.4108
|  |  | 2 | Conservative [MW] |  |  | 6.2121 | 6.2375 | 6.2637 | 6.2905 | 6.317 | 6.3441 | 6.3796 | 6.4156 | 6.4518 | 6.4894 | 6.5284 | 6.5677 | 6.6071 | 6.6477 | 6.6896 | 6.7315 | 6.941 | 7.1505
|  |  |  | Best View [MW] |  |  | 6.2121 | 6.2447 | 6.2779 | 6.3115 | 6.3455 | 6.381 | 6.4281 | 6.4761 | 6.5248 | 6.5755 | 6.6279 | 6.6808 | 6.7353 | 6.7926 | 6.85 | 6.9086 | 7.1983 | 7.4883
|  |  |  | Base Case [MW] |  |  | 6.2121 | 6.2511 | 6.2905 | 6.3311 | 6.3719 | 6.4149 | 6.4695 | 6.5268 | 6.5854 | 6.6463 | 6.7095 | 6.7734 | 6.8393 | 6.9081 | 6.9784 | 7.0498 | 7.4038 | 7.7579
|  |  |  | Aggressive [MW] |  |  | 6.2121 | 6.2615 | 6.3127 | 6.3657 | 6.4202 | 6.4775 | 6.5451 | 6.6165 | 6.6904 | 6.7663 | 6.8455 | 6.9274 | 7.0115 | 7.0976 | 7.188 | 7.279 | 7.7323 | 8.1857
| STICKILLEN | 10 | 1 | Conservative [MW] |  |  | 5.6105 | 5.6368 | 5.6656 | 5.6973 | 5.7272 | 5.7554 | 5.7898 | 5.8227 | 5.8577 | 5.8949 | 5.9295 | 5.9662 | 6.0049 | 6.0453 | 6.0829 | 6.1222 | 6.314 | 6.5062
|  |  |  | Best View [MW] |  |  | 5.6105 | 5.6386 | 5.6734 | 5.7061 | 5.741 | 5.7737 | 5.8224 | 5.8673 | 5.9168 | 5.9662 | 6.0195 | 6.0724 | 6.1289 | 6.1843 | 6.2382 | 6.2997 | 6.5869 | 6.8754
|  |  |  | Base Case [MW] |  |  | 5.6105 | 5.6556 | 5.7008 | 5.7502 | 5.8038 | 5.8522 | 5.9107 | 5.9638 | 6.0243 | 6.0829 | 6.1437 | 6.2063 | 6.2704 | 6.3403 | 6.4062 | 6.4768 | 6.8172 | 7.1585
|  |  |  | Aggressive [MW] |  |  | 5.6105 | 5.6724 | 5.7351 | 5.8024 | 5.8739 | 5.9488 | 6.0143 | 6.085 | 6.1554 | 6.2296 | 6.307 | 6.3871 | 6.4689 | 6.5519 | 6.6353 | 6.7229 | 7.1497 | 7.5773
| STRANORLAR | 20 | 1 | Conservative [MW] |  |  | 4.3376 | 4.3597 | 4.3824 | 4.4058 | 4.4288 | 4.4523 | 4.5077 | 4.5647 | 4.6224 | 4.6822 | 4.7426 | 4.8048 | 4.8681 | 4.9321 | 4.9979 | 5.0648 | 5.3963 | 5.728
|  |  |  | Best View [MW] |  |  | 4.3376 | 4.3875 | 4.4385 | 4.4907 | 4.5439 | 4.5982 | 4.6806 | 4.7656 | 4.853 | 4.9427 | 5.0347 | 5.13 | 5.2274 | 5.3275 | 5.4298 | 5.5351 | 6.0534 | 6.5723
|  |  |  | Base Case [MW] |  |  | 4.3376 | 4.3933 | 4.4501 | 4.5088 | 4.568 | 4.6292 | 4.7271 | 4.8284 | 4.933 | 5.0411 | 5.1527 | 5.2674 | 5.3859 | 5.5076 | 5.6331 | 5.7626 | 6.3996 | 7.0371
|  |  |  | Aggressive [MW] |  |  | 4.3376 | 4.4227 | 4.5105 | 4.6016 | 4.6962 | 4.7938 | 4.9136 | 5.0372 | 5.1654 | 5.2985 | 5.4364 | 5.5784 | 5.7264 | 5.8783 | 6.0347 | 6.1955 | 6.9878 | 7.7808
| SUTTON | 10 | 1 | Conservative [MW] |  |  | 12.3998 | 12.4819 | 12.565 | 12.6541 | 12.7439 | 12.8379 | 12.8919 | 12.9471 | 13.004 | 13.0577 | 13.1171 | 13.1735 | 13.2354 | 13.2937 | 13.3578 | 13.4178 | 13.7286 | 14.0388
|  |  |  | Best View [MW] |  |  | 12.3998 | 12.4896 | 12.5832 | 12.6812 | 12.7825 | 12.8858 | 12.9496 | 13.0138 | 13.0784 | 13.1432 | 13.2128 | 13.2823 | 13.3518 | 13.421 | 13.4944 | 13.5718 | 13.9479 | 14.3248
|  |  |  | Base Case [MW] |  |  | 12.3998 | 12.5008 | 12.6036 | 12.7133 | 12.8242 | 12.9388 | 13.012 | 13.0845 | 13.1605 | 13.2354 | 13.3138 | 13.3908 | 13.4707 | 13.5534 | 13.6384 | 13.7257 | 14.1561 | 14.5869
|  |  |  | Aggressive [MW] |  |  | 12.3998 | 12.5214 | 12.6527 | 12.7845 | 12.9282 | 13.0732 | 13.1387 | 13.2089 | 13.2748 | 13.3449 | 13.4148 | 13.4888 | 13.5626 | 13.6355 | 13.712 | 13.7923 | 14.1836 | 14.5756
| SWINFORD | 10 | 1 | Conservative [MW] |  |  | 6.7415 | 6.7541 | 6.7667 | 6.7788 | 6.7862 | 6.8019 | 6.841 | 6.8772 | 6.9194 | 6.9631 | 7.0032 | 7.0494 | 7.0919 | 7.1353 | 7.1843 | 7.2291 | 7.4645 | 7.6993
|  |  |  | Best View [MW] |  |  | 6.7415 | 6.7688 | 6.7949 | 6.8197 | 6.8476 | 6.8735 | 6.9261 | 6.9783 | 7.0345 | 7.0897 | 7.1438 | 7.2012 | 7.2614 | 7.3198 | 7.3804 | 7.4433 | 7.7517 | 8.0605
|  |  |  | Base Case [MW] |  |  | 6.7415 | 6.7744 | 6.8142 | 6.8468 | 6.8862 | 6.9221 | 6.9822 | 7.0487 | 7.1123 | 7.1815 | 7.2466 | 7.3167 | 7.3913 | 7.4649 | 7.5372 | 7.6123 | 7.9802 | 8.3486
|  |  |  | Aggressive [MW] |  |  | 6.7415 | 6.8092 | 6.8774 | 6.9498 | 7.0261 | 7.0997 | 7.1888 | 7.2812 | 7.3713 | 7.4723 | 7.5685 | 7.6732 | 7.7742 | 7.8814 | 7.9866 | 8.0918 | 8.6177 | 9.1436
| SWORDS | 10 | 1 | Conservative [MW] |  |  | 15.2363 | 15.3748 | 15.5151 | 15.6609 | 15.8011 | 15.9473 | 16.0286 | 16.1095 | 16.1916 | 16.2728 | 16.3531 | 16.4378 | 16.5161 | 16.5921 | 16.6713 | 16.7479 | 17.1379 | 17.5274
|  |  |  | Best View [MW] |  |  | 15.2363 | 15.391 | 15.5475 | 15.704 | 15.8637 | 16.0231 | 16.117 | 16.2065 | 16.3033 | 16.3957 | 16.4828 | 16.5756 | 16.6616 | 16.7519 | 16.8343 | 16.9129 | 17.3163 | 17.719
|  |  |  | Base Case [MW] |  |  | 15.2363 | 15.4042 | 15.578 | 15.7502 | 15.9229 | 16.0987 | 16.2076 | 16.3082 | 16.4113 | 16.5165 | 16.6169 | 16.7113 | 16.8101 | 16.9002 | 16.9864 | 17.0726 | 17.5037 | 17.9347
|  |  |  | Aggressive [MW] |  |  | 15.2363 | 15.4405 | 15.6526 | 15.8685 | 16.083 | 16.295 | 16.3842 | 16.4794 | 16.5686 | 16.6577 | 16.7453 | 16.8246 | 16.9066 | 16.9843 | 17.0617 | 17.1295 | 17.4943 | 17.8574
| TALBOTS INCH | 10 | 1 | Conservative [MW] |  |  | 1.5137 | 1.5475 | 1.5819 | 1.6164 | 1.2427 | 1.2779 | 1.3305 | 1.3829 | 1.4359 | 1.4903 | 1.5453 | 1.6007 | 1.6574 | 1.7133 | 1.7704 | 1.8287 | 2.1171 | 2.4057
|  |  |  | Best View [MW] |  |  | 1.5137 | 1.5549 | 1.5968 | 1.6395 | 1.2741 | 1.3176 | 1.3879 | 1.4602 | 1.5328 | 1.6074 | 1.6827 | 1.7586 | 1.8359 | 1.9146 | 1.993 | 2.0707 | 2.461 | 2.8512
|  |  |  | Base Case [MW] |  |  | 1.5137 | 1.5624 | 1.6127 | 1.6638 | 1.3066 | 1.3592 | 1.4429 | 1.5294 | 1.6164 | 1.7057 | 1.797 | 1.8878 | 1.981 | 2.0737 | 2.1666 | 2.259 | 2.7223 | 3.1856
|  |  |  | Aggressive [MW] |  |  | 1.5137 | 1.5955 | 1.6795 | 1.7646 | 1.4452 | 1.5351 | 1.6419 | 1.7511 | 1.862 | 1.9751 | 2.0882 | 2.2016 | 2.3139 | 2.4233 | 2.5309 | 2.6307 | 3.1507 | 3.6693
| TALBOTS INCH/ROSEHILL | 20 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 18.525 | 18.8453 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 18.525 | 18.8453 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 18.525 | 18.8453 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 18.525 | 18.8453 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162 | 19.162
| TELAYDON | 10 | 1 | Conservative [MW] |  |  | 7.0477 | 7.0636 | 7.0809 | 7.0996 | 7.1176 | 7.137 | 7.1612 | 7.1881 | 7.2156 | 7.2437 | 7.2724 | 7.2994 | 7.3291 | 7.3612 | 7.3915 | 7.4221 | 7.5745 | 7.7269
|  |  |  | Best View [MW] |  |  | 7.0477 | 7.0691 | 7.0914 | 7.1147 | 7.1389 | 7.1618 | 7.1995 | 7.2365 | 7.2748 | 7.3144 | 7.355 | 7.3966 | 7.441 | 7.4842 | 7.532 | 7.5779 | 7.8126 | 8.0469
|  |  |  | Base Case [MW] |  |  | 7.0477 | 7.0735 | 7.1038 | 7.1325 | 7.1613 | 7.1922 | 7.2332 | 7.2747 | 7.319 | 7.3636 | 7.4107 | 7.4599 | 7.509 | 7.5599 | 7.6122 | 7.668 | 7.9377 | 8.208
|  |  |  | Aggressive [MW] |  |  | 7.0477 | 7.0889 | 7.134 | 7.181 | 7.2298 | 7.2798 | 7.3332 | 7.3872 | 7.4458 | 7.5046 | 7.5675 | 7.6318 | 7.697 | 7.7671 | 7.8371 | 7.9111 | 8.2706 | 8.6307
|  | 20 | 1 | Conservative [MW] |  |  | 7.6951 | 7.7252 | 7.756 | 7.7854 | 7.8172 | 7.8476 | 6.9084 | 6.9536 | 6.9996 | 7.0465 | 7.0941 | 7.1424 | 7.193 | 7.2423 | 7.2937 | 7.3452 | 7.6026 | 7.86
|  |  |  | Best View [MW] |  |  | 7.6951 | 7.7336 | 7.7718 | 7.8118 | 7.8534 | 7.8943 | 6.9712 | 7.0348 | 7.1003 | 7.166 | 7.2331 | 7.303 | 7.3738 | 7.4449 | 7.5178 | 7.5921 | 7.9601 | 8.3283
|  |  |  | Base Case [MW] |  |  | 7.6951 | 7.7442 | 7.7915 | 7.8411 | 7.8908 | 7.9427 | 7.0305 | 7.1021 | 7.1745 | 7.2488 | 7.3248 | 7.4036 | 7.4831 | 7.5626 | 7.6454 | 7.7289 | 8.1444 | 8.56
|  |  |  | Aggressive [MW] |  |  | 7.6951 | 7.7688 | 7.8462 | 7.9241 | 8.0064 | 8.0901 | 7.1985 | 7.2878 | 7.3822 | 7.4773 | 7.5739 | 7.6731 | 7.7716 | 7.8739 | 7.975 | 8.077 | 8.5847 | 9.0925
| TEMPLEMORE | 10 | 1 | Conservative [MW] |  |  | 12.5321 | 12.561 | 12.1916 | 12.219 | 12.249 | 12.2779 | 12.3169 | 12.358 | 12.4009 | 12.4422 | 12.4889 | 12.5306 | 12.5774 | 12.6259 | 12.6727 | 12.7211 | 12.9588 | 13.1968
|  |  |  | Best View [MW] |  |  | 12.5321 | 12.567 | 12.2032 | 12.2393 | 12.2743 | 12.3111 | 12.3694 | 12.4282 | 12.4904 | 12.5564 | 12.6222 | 12.6914 | 12.7599 | 12.8351 | 12.9094 | 12.9864 | 13.3642 | 13.7425
|  |  |  | Base Case [MW] |  |  | 12.5321 | 12.5797 | 12.2273 | 12.2741 | 12.3223 | 12.3714 | 12.4383 | 12.505 | 12.5712 | 12.6438 | 12.7157 | 12.7935 | 12.8699 | 12.9523 | 13.0363 | 13.122 | 13.5458 | 13.9699
|  |  |  | Aggressive [MW] |  |  | 12.5321 | 12.604 | 12.2802 | 12.356 | 12.4365 | 12.5178 | 12.5913 | 12.6673 | 12.7454 | 12.829 | 12.914 | 13.0006 | 13.0917 | 13.1836 | 13.2793 | 13.3788 | 13.8662 | 14.3542
| TEMPLEOGUE | 10 | 1 | Conservative [MW] |  |  | 11.662 | 11.7204 | 11.779 | 11.8424 | 11.9059 | 11.9693 | 12.0312 | 12.0896 | 12.1528 | 12.2165 | 12.2807 | 12.3446 | 12.4133 | 12.4818 | 12.5541 | 12.622 | 12.9732 | 13.3236
|  |  |  | Best View [MW] |  |  | 11.662 | 11.7307 | 11.7985 | 11.8737 | 11.9477 | 12.0241 | 12.0938 | 12.1592 | 12.2326 | 12.3054 | 12.377 | 12.4522 | 12.5302 | 12.6112 | 12.6947 | 12.7765 | 13.1902 | 13.6035
|  |  |  | Base Case [MW] |  |  | 11.662 | 11.7387 | 11.8206 | 11.9082 | 11.9966 | 12.0854 | 12.1642 | 12.2411 | 12.3166 | 12.3991 | 12.4836 | 12.5698 | 12.6579 | 12.7475 | 12.838 | 12.9293 | 13.3835 | 13.8379
|  |  |  | Aggressive [MW] |  |  | 11.662 | 11.7972 | 11.9377 | 12.0896 | 12.2517 | 12.4218 | 12.5004 | 12.5863 | 12.6697 | 12.7554 | 12.8428 | 12.9317 | 13.022 | 13.1175 | 13.209 | 13.31 | 13.7896 | 14.2708
| TERMONFECKIN ROAD | 10 | 1 | Conservative [MW] |  |  | 3.1794 | 3.2224 | 3.2662 | 3.309 | 2.7496 | 2.7944 | 2.8498 | 2.9105 | 2.971 | 3.0328 | 3.0941 | 3.1564 | 3.2194 | 3.2831 | 3.3472 | 3.4094 | 3.7255 | 4.0413
|  |  |  | Best View [MW] |  |  | 3.1794 | 3.2293 | 3.2813 | 3.3337 | 2.7819 | 2.8354 | 2.9071 | 2.9832 | 3.0593 | 3.1369 | 3.2155 | 3.295 | 3.3749 | 3.4546 | 3.5335 | 3.6108 | 4.0017 | 4.3923
|  |  |  | Base Case [MW] |  |  | 3.1794 | 3.2508 | 3.3232 | 3.3962 | 2.8694 | 2.9458 | 3.0325 | 3.1231 | 3.2169 | 3.3097 | 3.4026 | 3.4965 | 3.5886 | 3.6798 | 3.7686 | 3.8528 | 4.2862 | 4.7188
|  |  |  | Aggressive [MW] |  |  | 3.1794 | 3.2753 | 3.3751 | 3.4766 | 2.9763 | 3.0836 | 3.1974 | 3.3155 | 3.4327 | 3.5512 | 3.6666 | 3.781 | 3.8852 | 3.9824 | 4.0647 | 4.1269 | 4.4914 | 4.8526
| TIMOLEAGUE | 10 | 1 | Conservative [MW] |  |  | 4.4097 | 4.4327 | 4.4583 | 4.4816 | 4.5073 | 4.533 | 4.5578 | 4.5825 | 4.6095 | 4.6362 | 4.6624 | 4.688 | 4.713 | 4.7398 | 4.7655 | 4.7928 | 4.9253 | 5.0579
|  |  |  | Best View [MW] |  |  | 4.4097 | 4.4332 | 4.459 | 4.4871 | 4.5125 | 4.5401 | 4.5749 | 4.6073 | 4.6422 | 4.6794 | 4.7132 | 4.7488 | 4.7857 | 4.821 | 4.8542 | 4.8904 | 5.0635 | 5.237
|  |  |  | Base Case [MW] |  |  | 4.4097 | 4.4442 | 4.4788 | 4.5157 | 4.5523 | 4.5907 | 4.6254 | 4.66 | 4.6939 | 4.7296 | 4.767 | 4.8028 | 4.8366 | 4.8709 | 4.9082 | 4.9421 | 5.1207 | 5.2987
|  |  |  | Aggressive [MW] |  |  | 4.4097 | 4.4573 | 4.5055 | 4.556 | 4.6083 | 4.6616 | 4.6979 | 4.7329 | 4.7693 | 4.8066 | 4.8415 | 4.8767 | 4.9114 | 4.9484 | 4.9809 | 5.0113 | 5.169 | 5.3264
|  | 20 | 1 | Conservative [MW] |  |  | 4.4706 | 4.4706 | 4.4706 | 4.4706 | 4.4706 | 4.4705 | 4.4705 | 4.4705 | 4.4704 | 4.4704 | 4.4704 | 4.4704 | 4.4703 | 4.4703 | 4.4703 | 4.4702 | 4.4697 | 4.4693
|  |  |  | Best View [MW] |  |  | 4.4706 | 4.4706 | 4.4706 | 4.4706 | 4.4705 | 4.4705 | 4.4705 | 4.4704 | 4.4704 | 4.4704 | 4.4703 | 4.4703 | 4.4702 | 4.4701 | 4.47 | 4.4699 | 4.4694 | 4.469
|  |  |  | Base Case [MW] |  |  | 4.4706 | 4.4706 | 4.4706 | 4.4705 | 4.4705 | 4.4705 | 4.4704 | 4.4704 | 4.4704 | 4.4703 | 4.4703 | 4.4702 | 4.4701 | 4.47 | 4.4699 | 4.4697 | 4.4691 | 4.4684
|  |  |  | Aggressive [MW] |  |  | 4.4706 | 4.4706 | 4.4706 | 4.4705 | 4.4704 | 4.4704 | 4.4704 | 4.4703 | 4.4703 | 4.4702 | 4.4701 | 4.47 | 4.4698 | 4.4697 | 4.4696 | 4.4696 | 4.4694 | 4.4692
| TINAHASK | 10 | 1 | Conservative [MW] |  |  | 6.1274 | 6.1596 | 6.1938 | 6.2265 | 6.2613 | 5.7024 | 5.75 | 5.7954 | 5.8415 | 5.8913 | 5.9384 | 5.9891 | 6.0403 | 6.0914 | 6.1427 | 6.1937 | 6.4495 | 6.7053
|  |  |  | Best View [MW] |  |  | 6.1274 | 6.1691 | 6.2084 | 6.2526 | 6.2979 | 5.7486 | 5.8083 | 5.8701 | 5.9335 | 5.9987 | 6.0652 | 6.1328 | 6.2011 | 6.2699 | 6.3423 | 6.4106 | 6.7631 | 7.1148
|  |  |  | Base Case [MW] |  |  | 6.1274 | 6.18 | 6.2326 | 6.2881 | 6.3433 | 5.8101 | 5.8792 | 5.9492 | 6.0227 | 6.0963 | 6.1729 | 6.2485 | 6.3263 | 6.402 | 6.4824 | 6.5633 | 6.9664 | 7.3697
|  |  |  | Aggressive [MW] |  |  | 6.1274 | 6.1981 | 6.2724 | 6.3501 | 6.4267 | 5.9159 | 6.0112 | 6.108 | 6.2091 | 6.3099 | 6.4163 | 6.5197 | 6.6258 | 6.729 | 6.8356 | 6.9341 | 7.4482 | 7.961
| TOGHER | 10 | 1 | Conservative [MW] |  |  | 13.7459 | 13.8113 | 13.8807 | 13.95 | 14.0233 | 14.0962 | 14.1682 | 14.2399 | 14.315 | 14.3937 | 14.4713 | 14.5482 | 14.6279 | 14.7106 | 14.7915 | 14.875 | 15.2857 | 15.6968
|  |  |  | Best View [MW] |  |  | 13.7459 | 13.8157 | 13.889 | 13.962 | 14.0381 | 14.1176 | 14.2149 | 14.3162 | 14.4172 | 14.5218 | 14.629 | 14.7388 | 14.851 | 14.9646 | 15.0794 | 15.199 | 15.7843 | 16.3704
|  |  |  | Base Case [MW] |  |  | 13.7459 | 13.8424 | 13.9426 | 14.0464 | 14.1533 | 14.2628 | 14.3636 | 14.4681 | 14.5714 | 14.6815 | 14.7898 | 14.9044 | 15.0201 | 15.1366 | 15.2575 | 15.3782 | 15.9822 | 16.5863
|  |  |  | Aggressive [MW] |  |  | 13.7459 | 13.8666 | 13.9906 | 14.1209 | 14.2573 | 14.3948 | 14.5292 | 14.6651 | 14.8052 | 14.9489 | 15.0953 | 15.2474 | 15.3993 | 15.5548 | 15.7162 | 15.8734 | 16.6706 | 17.467
| TOOMEVARA | 10 | 1 | Conservative [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Best View [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Base Case [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
|  |  |  | Aggressive [MW] |  |  | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001
| TRAMORE | 10 | 1 | Conservative [MW] |  |  | 4.3072 | 4.3593 | 4.4116 | 4.4648 | 4.5193 | 4.5749 | 4.6458 | 4.7189 | 4.7941 | 4.8705 | 4.948 | 5.0274 | 5.1079 | 5.1905 | 5.2751 | 5.3604 | 5.7849 | 6.2096
|  |  |  | Best View [MW] |  |  | 4.3072 | 4.3648 | 4.4227 | 4.4816 | 4.5418 | 4.604 | 4.6954 | 4.79 | 4.8868 | 4.9858 | 5.0878 | 5.1918 | 5.2988 | 5.4088 | 5.5215 | 5.6358 | 6.2033 | 6.771
|  |  |  | Base Case [MW] |  |  | 4.3072 | 4.3747 | 4.4437 | 4.5136 | 4.5859 | 4.6593 | 4.7667 | 4.8776 | 4.9924 | 5.1105 | 5.2316 | 5.3565 | 5.4841 | 5.6167 | 5.7515 | 5.891 | 6.5762 | 7.2621
|  |  |  | Aggressive [MW] |  |  | 4.3072 | 4.4142 | 4.5237 | 4.6385 | 4.756 | 4.8787 | 5.0154 | 5.1573 | 5.3041 | 5.4568 | 5.614 | 5.7756 | 5.9432 | 6.1156 | 6.2918 | 6.4727 | 7.3646 | 8.2573
| TRIM | 10 | 1 | Conservative [MW] |  |  | 6.1009 | 6.1271 | 6.1522 | 6.1806 | 6.2079 | 6.2338 | 6.2844 | 6.3432 | 6.4009 | 6.4567 | 6.5154 | 6.5768 | 6.6355 | 6.6959 | 6.7629 | 6.826 | 7.1519 | 7.4772
|  |  |  | Best View [MW] |  |  | 6.1009 | 6.1351 | 6.1676 | 6.2025 | 6.2351 | 6.2704 | 6.3326 | 6.3965 | 6.4618 | 6.5327 | 6.599 | 6.6699 | 6.7401 | 6.8142 | 6.8862 | 6.9621 | 7.3313 | 7.7011
|  |  |  | Base Case [MW] |  |  | 6.1009 | 6.1658 | 6.2323 | 6.2953 | 6.3635 | 6.437 | 6.5053 | 6.5736 | 6.6462 | 6.7175 | 6.792 | 6.8694 | 6.9492 | 7.0255 | 7.1017 | 7.1773 | 7.557 | 7.9366
|  |  |  | Aggressive [MW] |  |  | 6.1009 | 6.1885 | 6.2799 | 6.3735 | 6.4732 | 6.5728 | 6.6562 | 6.7393 | 6.8221 | 6.9141 | 6.9992 | 7.0852 | 7.1768 | 7.2672 | 7.3543 | 7.4365 | 7.8606 | 8.2839
|  | 20 | 1 | Conservative [MW] |  |  | 3.7775 | 3.785 | 3.7944 | 3.8035 | 3.8143 | 3.0861 | 3.106 | 3.1264 | 3.1475 | 3.1692 | 3.1914 | 3.2141 | 3.2374 | 3.261 | 3.2862 | 3.3118 | 3.4386 | 3.5655
|  |  |  | Best View [MW] |  |  | 3.7775 | 3.7883 | 3.8006 | 3.8124 | 3.8236 | 3.1003 | 3.1237 | 3.1476 | 3.1719 | 3.1977 | 3.2238 | 3.2503 | 3.2781 | 3.3071 | 3.3366 | 3.3671 | 3.5167 | 3.6665
|  |  |  | Base Case [MW] |  |  | 3.7775 | 3.7984 | 3.8214 | 3.8466 | 3.8718 | 3.1615 | 3.1872 | 3.2132 | 3.2416 | 3.2691 | 3.299 | 3.329 | 3.3605 | 3.3927 | 3.4247 | 3.4589 | 3.624 | 3.7894
|  |  |  | Aggressive [MW] |  |  | 3.7775 | 3.8084 | 3.8417 | 3.8752 | 3.9106 | 3.2135 | 3.245 | 3.2776 | 3.3112 | 3.3458 | 3.3822 | 3.4191 | 3.4578 | 3.4967 | 3.5384 | 3.58 | 3.7881 | 3.9962
| TRIMMS LANE | 10 | 1 | Conservative [MW] |  |  | 14.1219 | 14.1692 | 14.2141 | 14.2571 | 14.3068 | 14.3502 | 14.4148 | 14.4839 | 14.5489 | 14.6187 | 14.6881 | 14.7574 | 14.8305 | 14.9031 | 14.9798 | 15.0553 | 15.4358 | 15.8162
|  |  |  | Best View [MW] |  |  | 14.1219 | 14.179 | 14.2375 | 14.2926 | 14.3531 | 14.4146 | 14.5063 | 14.6028 | 14.6992 | 14.7997 | 14.8996 | 15.0072 | 15.1128 | 15.2257 | 15.3399 | 15.4558 | 16.031 | 16.6065
|  |  |  | Base Case [MW] |  |  | 14.1219 | 14.1941 | 14.2658 | 14.3407 | 14.4189 | 14.4959 | 14.5995 | 14.7059 | 14.8144 | 14.9293 | 15.0409 | 15.162 | 15.2831 | 15.4078 | 15.5358 | 15.666 | 16.3111 | 16.9565
|  |  |  | Aggressive [MW] |  |  | 14.1219 | 14.2362 | 14.3512 | 14.4701 | 14.5925 | 14.7222 | 14.8472 | 14.9792 | 15.1129 | 15.2519 | 15.3947 | 15.5404 | 15.6928 | 15.8459 | 16.0024 | 16.1616 | 16.9505 | 17.7398
| TUAM NORTH | 10 | 1 | Conservative [MW] |  |  | 1.3881 | 1.4143 | 1.442 | 1.469 | 1.4968 | 14.0786 | 14.137 | 14.1967 | 14.2578 | 14.3203 | 14.3842 | 14.4494 | 14.5158 | 14.585 | 14.6554 | 14.7271 | 15.0823 | 15.4376
|  |  |  | Best View [MW] |  |  | 1.3881 | 1.4267 | 1.4654 | 1.5057 | 1.5461 | 14.1535 | 14.2356 | 14.3203 | 14.4078 | 14.4967 | 14.5895 | 14.6862 | 14.7855 | 14.8874 | 14.9917 | 15.0998 | 15.6303 | 16.1614
|  |  |  | Base Case [MW] |  |  | 1.3881 | 1.4382 | 1.4893 | 1.5412 | 1.5948 | 14.2281 | 14.322 | 14.4198 | 14.5217 | 14.6261 | 14.7359 | 14.8482 | 14.9643 | 15.0855 | 15.2089 | 15.339 | 15.9715 | 16.6052
|  |  |  | Aggressive [MW] |  |  | 1.3881 | 1.4718 | 1.5589 | 1.6492 | 1.7418 | 14.4583 | 14.5835 | 14.7139 | 14.8497 | 14.9902 | 15.1373 | 15.2903 | 15.4512 | 15.6176 | 15.7895 | 15.9702 | 16.8501 | 17.7314
| TUAM SOUTH | 10 | 1 | Conservative [MW] |  |  | 4.7758 | 4.7917 | 4.8088 | 4.8244 | 4.8413 | 4.8565 | 4.8827 | 4.9123 | 4.9365 | 4.9636 | 4.9875 | 5.0141 | 5.0369 | 5.0617 | 5.0814 | 5.1024 | 5.2038 | 5.3055
|  |  |  | Best View [MW] |  |  | 4.7758 | 4.7998 | 4.8235 | 4.8468 | 4.8694 | 4.8913 | 4.927 | 4.9638 | 4.9982 | 5.0294 | 5.0629 | 5.0908 | 5.1157 | 5.1362 | 5.151 | 5.1615 | 5.2255 | 5.2887
|  |  |  | Base Case [MW] |  |  | 4.7758 | 4.806 | 4.8365 | 4.8671 | 4.8945 | 4.9242 | 4.9647 | 5.003 | 5.041 | 5.0741 | 5.104 | 5.1294 | 5.1482 | 5.1617 | 5.163 | 5.1562 | 5.1439 | 5.1302
|  |  |  | Aggressive [MW] |  |  | 4.7758 | 4.826 | 4.8748 | 4.924 | 4.9723 | 5.018 | 5.0596 | 5.0961 | 5.1287 | 5.1505 | 5.1647 | 5.1617 | 5.1342 | 5.0794 | 4.9708 | 4.7731 | 4.0222 | 3.2564
| TUBBERCURRY | 10 | 1 | Conservative [MW] |  |  | 4.146 | 4.152 | 4.1578 | 4.1658 | 4.1714 | 4.179 | 4.2009 | 4.2233 | 4.2462 | 4.2694 | 4.2952 | 4.319 | 4.3429 | 4.3692 | 4.3956 | 4.4218 | 4.5531 | 4.6844
|  |  |  | Best View [MW] |  |  | 4.146 | 4.1606 | 4.1744 | 4.1898 | 4.2065 | 4.2224 | 4.2503 | 4.2798 | 4.3107 | 4.3405 | 4.3739 | 4.4059 | 4.4388 | 4.4723 | 4.5061 | 4.5403 | 4.7102 | 4.8802
|  |  |  | Base Case [MW] |  |  | 4.146 | 4.1659 | 4.1844 | 4.206 | 4.2261 | 4.2492 | 4.2827 | 4.3186 | 4.3569 | 4.3924 | 4.4321 | 4.4708 | 4.5108 | 4.5516 | 4.5927 | 4.6339 | 4.8396 | 5.0453
|  |  |  | Aggressive [MW] |  |  | 4.146 | 4.1828 | 4.2235 | 4.2631 | 4.3058 | 4.3491 | 4.3983 | 4.45 | 4.5011 | 4.5556 | 4.6104 | 4.6641 | 4.7212 | 4.7748 | 4.832 | 4.8853 | 5.162 | 5.438
| TULLA | 10 | 1 | Conservative [MW] |  |  | 6.3044 | 6.3202 | 6.3437 | 6.3621 | 6.3839 | 6.4048 | 6.4318 | 6.4615 | 6.4937 | 6.5242 | 6.5529 | 6.584 | 6.6174 | 6.6489 | 6.6827 | 6.7187 | 6.8928 | 7.0672
|  |  |  | Best View [MW] |  |  | 6.3044 | 6.3248 | 6.3442 | 6.3668 | 6.3927 | 6.4132 | 6.4578 | 6.4991 | 6.5412 | 6.5839 | 6.6314 | 6.6792 | 6.7273 | 6.7751 | 6.8271 | 6.8787 | 7.1376 | 7.3964
|  |  |  | Base Case [MW] |  |  | 6.3044 | 6.3373 | 6.372 | 6.4082 | 6.4459 | 6.4851 | 6.5337 | 6.578 | 6.631 | 6.6791 | 6.7311 | 6.7866 | 6.8411 | 6.8985 | 6.9588 | 7.017 | 7.3137 | 7.6101
|  |  |  | Aggressive [MW] |  |  | 6.3044 | 6.3613 | 6.4275 | 6.4936 | 6.5633 | 6.6406 | 6.6938 | 6.7503 | 6.8049 | 6.8667 | 6.9262 | 6.992 | 7.0546 | 7.123 | 7.1919 | 7.2608 | 7.6055 | 7.9503
| TULLOW | 20 | 1 | Conservative [MW] |  |  | 3.215 | 3.2693 | 3.3246 | 3.3809 | 3.4382 | 3.4992 | 3.5771 | 3.6553 | 3.7347 | 3.8147 | 3.8954 | 3.9781 | 4.0617 | 4.1479 | 4.2349 | 4.3238 | 4.7633 | 5.2031
|  |  |  | Best View [MW] |  |  | 3.215 | 3.2831 | 3.3531 | 3.4236 | 3.4961 | 3.5737 | 3.6772 | 3.7822 | 3.8877 | 3.996 | 4.1072 | 4.2201 | 4.3364 | 4.4553 | 4.5773 | 4.7006 | 5.3136 | 5.9269
|  |  |  | Base Case [MW] |  |  | 3.215 | 3.3021 | 3.3914 | 3.4832 | 3.577 | 3.6765 | 3.7949 | 3.9125 | 4.0334 | 4.1579 | 4.2852 | 4.4158 | 4.5495 | 4.6873 | 4.8273 | 4.9685 | 5.6712 | 6.3742
|  |  |  | Aggressive [MW] |  |  | 3.215 | 3.3338 | 3.4564 | 3.5835 | 3.7154 | 3.8549 | 4.0142 | 4.1794 | 4.3491 | 4.5252 | 4.7075 | 4.8937 | 5.0834 | 5.2782 | 5.4771 | 5.6879 | 6.7103 | 7.7346
| TULLYNAMALRA | 10 | 1 | Conservative [MW] |  |  | 4.8367 | 4.8638 | 4.8935 | 4.9217 | 4.9527 | 4.9819 | 5.0244 | 5.0664 | 5.1094 | 5.155 | 5.2 | 5.2459 | 5.2927 | 5.3403 | 5.3886 | 5.4377 | 5.6812 | 5.9248
|  |  |  | Best View [MW] |  |  | 4.8367 | 4.8719 | 4.9097 | 4.9473 | 4.9859 | 5.0257 | 5.0835 | 5.1433 | 5.2052 | 5.2674 | 5.3314 | 5.3989 | 5.4663 | 5.535 | 5.605 | 5.6781 | 6.0353 | 6.3931
|  |  |  | Base Case [MW] |  |  | 4.8367 | 4.8814 | 4.9271 | 4.9753 | 5.0244 | 5.0729 | 5.1395 | 5.2063 | 5.2748 | 5.3465 | 5.4195 | 5.4936 | 5.5706 | 5.6501 | 5.7298 | 5.8116 | 6.2151 | 6.6189
|  |  |  | Aggressive [MW] |  |  | 4.8367 | 4.9071 | 4.9793 | 5.0546 | 5.1328 | 5.214 | 5.2977 | 5.3836 | 5.4733 | 5.5647 | 5.6591 | 5.7561 | 5.855 | 5.9553 | 6.0583 | 6.1629 | 6.6817 | 7.2008
| TURLOUGH ROAD | 10 | 1 | Conservative [MW] |  |  | 6.4146 | 6.4222 | 6.4296 | 6.4369 | 6.4442 | 5.8547 | 5.8838 | 5.9119 | 5.942 | 5.9712 | 6.0021 | 6.0349 | 6.0665 | 6.0999 | 6.1351 | 6.1689 | 6.3417 | 6.5143
|  |  |  | Best View [MW] |  |  | 6.4146 | 6.4337 | 6.4479 | 6.4657 | 6.483 | 5.9034 | 5.9385 | 5.975 | 6.0158 | 6.0549 | 6.0952 | 6.1367 | 6.1792 | 6.2226 | 6.2701 | 6.315 | 6.5464 | 6.7773
|  |  |  | Base Case [MW] |  |  | 6.4146 | 6.4409 | 6.4618 | 6.4899 | 6.5123 | 5.9418 | 5.9875 | 6.0339 | 6.0807 | 6.1308 | 6.1841 | 6.2374 | 6.2905 | 6.3496 | 6.4079 | 6.4685 | 6.7656 | 7.063
|  |  |  | Aggressive [MW] |  |  | 6.4146 | 6.4657 | 6.5119 | 6.5656 | 6.6179 | 6.078 | 6.1452 | 6.2134 | 6.2852 | 6.3604 | 6.4382 | 6.5217 | 6.6068 | 6.6927 | 6.7859 | 6.882 | 7.3547 | 7.8278
| TYCOR | 10 | 1 | Conservative [MW] |  |  | 6.9214 | 6.9465 | 6.9748 | 7.0016 | 7.0271 | 19.4945 | 19.5356 | 19.5786 | 19.6234 | 19.6667 | 19.7118 | 19.7588 | 19.8078 | 19.8544 | 19.907 | 19.9571 | 20.2144 | 20.4713
|  |  |  | Best View [MW] |  |  | 6.9214 | 6.9491 | 6.9797 | 7.0088 | 7.0404 | 19.5114 | 19.5651 | 19.6196 | 19.6752 | 19.7351 | 19.796 | 19.8573 | 19.9189 | 19.9848 | 20.0547 | 20.1248 | 20.4745 | 20.8244
|  |  |  | Base Case [MW] |  |  | 6.9214 | 6.9551 | 6.9913 | 7.0249 | 7.0606 | 19.5436 | 19.6055 | 19.6713 | 19.7367 | 19.8097 | 19.8819 | 19.9534 | 20.0317 | 20.1124 | 20.1958 | 20.2817 | 20.7046 | 21.1279
|  |  |  | Aggressive [MW] |  |  | 6.9214 | 6.9766 | 7.0306 | 7.0874 | 7.1466 | 19.6709 | 19.754 | 19.835 | 19.9252 | 20.0161 | 20.1116 | 20.2112 | 20.3142 | 20.4206 | 20.5335 | 20.6489 | 21.2193 | 21.7902
| TYMON | 10 | 1 | Conservative [MW] |  |  | 13.3933 | 13.4712 | 13.5519 | 13.6314 | 13.7131 | 13.7973 | 13.8624 | 13.9277 | 13.9977 | 14.0636 | 14.1337 | 14.2038 | 14.278 | 14.3519 | 14.4249 | 14.4974 | 14.8611 | 15.2248
|  |  |  | Best View [MW] |  |  | 13.3933 | 13.4835 | 13.5744 | 13.6663 | 13.7629 | 13.8639 | 13.9417 | 14.0184 | 14.1023 | 14.1847 | 14.2648 | 14.3518 | 14.436 | 14.527 | 14.6148 | 14.709 | 15.1628 | 15.6176
|  |  |  | Base Case [MW] |  |  | 13.3933 | 13.4935 | 13.5969 | 13.7034 | 13.8121 | 13.9226 | 14.0128 | 14.104 | 14.197 | 14.2901 | 14.3841 | 14.4828 | 14.5812 | 14.6838 | 14.7854 | 14.8901 | 15.4054 | 15.9212
|  |  |  | Aggressive [MW] |  |  | 13.3933 | 13.5391 | 13.6904 | 13.8498 | 14.016 | 14.1869 | 14.2772 | 14.3643 | 14.4576 | 14.5516 | 14.6463 | 14.7412 | 14.841 | 14.9402 | 15.0388 | 15.1414 | 15.6436 | 16.1466
| UNIDARE | 10 | 1 | Conservative [MW] |  |  | 14.1381 | 14.2182 | 14.3042 | 14.3914 | 14.4799 | 14.5729 | 14.624 | 14.6814 | 14.7357 | 14.7913 | 14.8484 | 14.9069 | 14.9665 | 15.0271 | 15.0889 | 15.1471 | 15.4476 | 15.7475
|  |  |  | Best View [MW] |  |  | 14.1381 | 14.2262 | 14.3231 | 14.4194 | 14.5197 | 14.6225 | 14.6839 | 14.7459 | 14.8126 | 14.8756 | 14.9432 | 15.0109 | 15.0829 | 15.1549 | 15.2267 | 15.2977 | 15.6548 | 16.0117
|  |  |  | Base Case [MW] |  |  | 14.1381 | 14.2377 | 14.3397 | 14.448 | 14.5579 | 14.6728 | 14.744 | 14.8146 | 14.8887 | 14.9665 | 15.0433 | 15.1236 | 15.2021 | 15.2836 | 15.3674 | 15.4539 | 15.8793 | 16.3052
|  |  |  | Aggressive [MW] |  |  | 14.1381 | 14.2589 | 14.3857 | 14.5217 | 14.6613 | 14.8074 | 14.871 | 14.9393 | 15.0076 | 15.076 | 15.149 | 15.2168 | 15.2934 | 15.3645 | 15.4395 | 15.5183 | 15.9023 | 16.2869
| URLINGFORD | 20 | 1 | Conservative [MW] |  |  | 0 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325
|  |  |  | Best View [MW] |  |  | 0 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325
|  |  |  | Base Case [MW] |  |  | 0 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325
|  |  |  | Aggressive [MW] |  |  | 0 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325 | 3.325
| VIRGINIA | 10 | 1 | Conservative [MW] |  |  | 7.9812 | 8.0158 | 8.0577 | 8.0959 | 8.1309 | 8.1727 | 8.2241 | 8.2793 | 8.3322 | 8.3881 | 8.4409 | 8.4962 | 8.5479 | 8.6008 | 8.6553 | 8.7104 | 8.9844 | 9.2585
|  |  |  | Best View [MW] |  |  | 7.9812 | 8.0274 | 8.0784 | 8.1292 | 8.1739 | 8.2286 | 8.2993 | 8.3715 | 8.4451 | 8.519 | 8.5923 | 8.6639 | 8.7389 | 8.8034 | 8.8732 | 8.9353 | 9.2664 | 9.5962
|  |  |  | Base Case [MW] |  |  | 7.9812 | 8.0396 | 8.0996 | 8.1616 | 8.2247 | 8.289 | 8.3682 | 8.451 | 8.5307 | 8.6117 | 8.6866 | 8.7661 | 8.8415 | 8.9103 | 8.9771 | 9.0331 | 9.3417 | 9.6485
|  |  |  | Aggressive [MW] |  |  | 7.9812 | 8.0738 | 8.1666 | 8.264 | 8.3587 | 8.4599 | 8.5552 | 8.6528 | 8.7446 | 8.8327 | 8.9196 | 8.9953 | 9.0616 | 9.1123 | 9.1469 | 9.1552 | 9.267 | 9.3743
| WALTERSTOWN | 20 | 0 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 12.35 | 12.35 | 12.2196 | 12.2093 | 12.1985 | 12.1872 | 12.1755 | 12.1613 | 12.1483 | 12.1348 | 12.1205 | 12.0512 | 11.9817
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 12.35 | 12.35 | 12.207 | 12.1943 | 12.1808 | 12.1667 | 12.1518 | 12.136 | 12.1194 | 12.1018 | 12.0833 | 11.9932 | 11.903
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 12.35 | 12.35 | 12.1899 | 12.1762 | 12.1599 | 12.1425 | 12.1241 | 12.1046 | 12.0839 | 12.0637 | 12.0403 | 11.9319 | 11.823
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 12.35 | 12.35 | 12.1631 | 12.1472 | 12.1304 | 12.1144 | 12.0955 | 12.0755 | 12.0542 | 12.0334 | 12.0093 | 11.8977 | 11.7855
| WATERFORD | 10 | 1 | Conservative [MW] |  |  | 6.8709 | 6.8896 | 6.9076 | 6.9249 | 6.9415 | 6.9615 | 6.9837 | 7.0088 | 7.0327 | 7.0593 | 7.0847 | 7.1128 | 7.1393 | 7.1643 | 7.1921 | 7.2223 | 7.3668 | 7.5116
|  |  |  | Best View [MW] |  |  | 6.8709 | 6.8905 | 6.9093 | 6.9312 | 6.9483 | 6.9685 | 6.9989 | 7.0312 | 7.0657 | 7.0979 | 7.1318 | 7.1678 | 7.201 | 7.2401 | 7.2764 | 7.3184 | 7.5134 | 7.7093
|  |  |  | Base Case [MW] |  |  | 6.8709 | 6.8927 | 6.9174 | 6.9409 | 6.9632 | 6.9883 | 7.0249 | 7.0629 | 7.0978 | 7.1379 | 7.1791 | 7.221 | 7.2636 | 7.311 | 7.3586 | 7.4062 | 7.6444 | 7.8825
|  |  |  | Aggressive [MW] |  |  | 6.8709 | 6.9063 | 6.9429 | 6.9804 | 7.019 | 7.0625 | 7.1078 | 7.1528 | 7.2057 | 7.2577 | 7.3087 | 7.3669 | 7.4232 | 7.4818 | 7.5421 | 7.6085 | 7.9243 | 8.2411
| WATERFORD IND EST | 10 | 1 | Conservative [MW] |  |  | 15.5519 | 15.6158 | 15.6801 | 15.7488 | 15.8134 | 15.8835 | 15.973 | 16.0591 | 16.1516 | 16.2449 | 16.339 | 16.4334 | 16.5279 | 16.6267 | 16.7247 | 16.8218 | 17.3095 | 17.797
|  |  |  | Best View [MW] |  |  | 15.5519 | 15.6205 | 15.6932 | 15.7689 | 15.8448 | 15.92 | 16.0337 | 16.1487 | 16.2639 | 16.3841 | 16.5034 | 16.6263 | 16.752 | 16.8793 | 17.0019 | 17.1297 | 17.7547 | 18.3807
|  |  |  | Base Case [MW] |  |  | 15.5519 | 15.6363 | 15.7233 | 15.8061 | 15.8963 | 15.9883 | 16.1206 | 16.2537 | 16.3921 | 16.5292 | 16.6741 | 16.8151 | 16.9615 | 17.1115 | 17.2583 | 17.4059 | 18.1417 | 18.8777
|  |  |  | Aggressive [MW] |  |  | 15.5519 | 15.6817 | 15.8216 | 15.9601 | 16.1074 | 16.252 | 16.4168 | 16.586 | 16.7579 | 16.9297 | 17.1043 | 17.2844 | 17.4616 | 17.6387 | 17.811 | 17.9801 | 18.8341 | 19.6876
| WATLING STREET | 10 | 1 | Conservative [MW] |  |  | 6.0775 | 6.1371 | 6.1985 | 6.2614 | 6.3266 | 4.7471 | 4.8078 | 4.8697 | 4.9333 | 4.9984 | 5.0646 | 5.1327 | 5.2021 | 5.2735 | 5.3462 | 5.4204 | 5.7875 | 6.1549
|  |  |  | Best View [MW] |  |  | 6.0775 | 6.1471 | 6.2189 | 6.2932 | 6.3698 | 4.803 | 4.8721 | 4.9428 | 5.0155 | 5.0899 | 5.1665 | 5.245 | 5.3253 | 5.4076 | 5.4921 | 5.5784 | 6.005 | 6.4319
|  |  |  | Base Case [MW] |  |  | 6.0775 | 6.1585 | 6.2424 | 6.3295 | 6.4196 | 4.8677 | 4.9445 | 5.0235 | 5.1053 | 5.1888 | 5.2748 | 5.3631 | 5.4537 | 5.5465 | 5.6423 | 5.7405 | 6.2251 | 6.7101
|  |  |  | Aggressive [MW] |  |  | 6.0775 | 6.2155 | 6.3617 | 6.5175 | 6.6828 | 5.2126 | 5.2948 | 5.3795 | 5.4661 | 5.5547 | 5.6461 | 5.7393 | 5.8353 | 5.9327 | 6.0329 | 6.1359 | 6.6436 | 7.1517
| WESTPORT | 20 | 1 | Conservative [MW] |  |  | 12.3836 | 12.3967 | 12.4099 | 12.4224 | 12.435 | 12.4468 | 12.4978 | 12.5502 | 12.6076 | 12.6619 | 12.7211 | 12.7769 | 12.8377 | 12.8988 | 12.9646 | 13.0263 | 13.3459 | 13.6648
|  |  |  | Best View [MW] |  |  | 12.3836 | 12.4103 | 12.4441 | 12.4727 | 12.5047 | 12.5345 | 12.6028 | 12.6704 | 12.7416 | 12.8158 | 12.8887 | 12.9645 | 13.0425 | 13.1231 | 13.2101 | 13.2943 | 13.7226 | 14.1505
|  |  |  | Base Case [MW] |  |  | 12.3836 | 12.427 | 12.4682 | 12.5155 | 12.561 | 12.6071 | 12.6883 | 12.7751 | 12.8624 | 12.9544 | 13.0502 | 13.1501 | 13.249 | 13.3549 | 13.4632 | 13.573 | 14.118 | 14.6632
|  |  |  | Aggressive [MW] |  |  | 12.3836 | 12.4679 | 12.5599 | 12.6554 | 12.7576 | 12.8607 | 12.9803 | 13.1058 | 13.241 | 13.3801 | 13.5219 | 13.6737 | 13.8299 | 13.9935 | 14.1621 | 14.3386 | 15.2002 | 16.0631
| WHITECHURCH | 20 | 1 | Conservative [MW] |  |  | 8.0932 | 8.1633 | 8.234 | 8.3072 | 8.3796 | 8.4544 | 8.5303 | 8.6069 | 8.6842 | 8.7637 | 8.8437 | 8.9259 | 9.0084 | 9.0948 | 9.1794 | 9.2679 | 9.7 | 10.1327
|  |  |  | Best View [MW] |  |  | 8.0932 | 8.1673 | 8.2421 | 8.3192 | 8.3971 | 8.4757 | 8.5778 | 8.6815 | 8.7882 | 8.8979 | 9.0084 | 9.1235 | 9.2391 | 9.3588 | 9.4804 | 9.6037 | 10.2156 | 10.8278
|  |  |  | Base Case [MW] |  |  | 8.0932 | 8.1946 | 8.2975 | 8.4053 | 8.5144 | 8.6265 | 8.7325 | 8.8399 | 8.95 | 9.0628 | 9.1799 | 9.2974 | 9.417 | 9.5403 | 9.665 | 9.793 | 10.4242 | 11.0559
|  |  |  | Aggressive [MW] |  |  | 8.0932 | 8.2326 | 8.3769 | 8.5276 | 8.6827 | 8.8452 | 8.9579 | 9.0734 | 9.1911 | 9.3109 | 9.4346 | 9.5598 | 9.6861 | 9.8176 | 9.9495 | 10.0834 | 10.7475 | 11.4119
| WHITEHALL | 10 | 1 | Conservative [MW] |  |  | 8.0289 | 8.067 | 8.1065 | 8.1496 | 8.1919 | 8.2348 | 8.2733 | 8.3134 | 8.355 | 8.3959 | 8.4383 | 8.4817 | 8.5265 | 8.5698 | 8.6165 | 8.6616 | 8.8914 | 9.121
|  |  |  | Best View [MW] |  |  | 8.0289 | 8.0744 | 8.1204 | 8.1687 | 8.2194 | 8.2696 | 8.3147 | 8.3604 | 8.4068 | 8.454 | 8.5036 | 8.5515 | 8.6038 | 8.6539 | 8.706 | 8.7599 | 9.0245 | 9.2895
|  |  |  | Base Case [MW] |  |  | 8.0289 | 8.0821 | 8.1363 | 8.1937 | 8.2519 | 8.3124 | 8.3619 | 8.4117 | 8.4634 | 8.5171 | 8.5702 | 8.6271 | 8.6828 | 8.7397 | 8.7995 | 8.8598 | 9.16 | 9.4603
|  |  |  | Aggressive [MW] |  |  | 8.0289 | 8.1192 | 8.2134 | 8.3147 | 8.4217 | 8.5321 | 8.5842 | 8.6357 | 8.6913 | 8.7461 | 8.8022 | 8.8592 | 8.9172 | 8.9758 | 9.0345 | 9.0955 | 9.3944 | 9.6936
| WHITESTOWN | 10 | 1 | Conservative [MW] |  |  | 13.0336 | 13.0773 | 13.1188 | 13.1619 | 13.2027 | 13.2492 | 13.2843 | 13.322 | 13.3581 | 13.3967 | 13.4335 | 13.4729 | 13.5144 | 13.5542 | 13.5961 | 13.6404 | 13.8555 | 14.071
|  |  |  | Best View [MW] |  |  | 13.0336 | 13.0824 | 13.1323 | 13.1791 | 13.2308 | 13.2872 | 13.3303 | 13.3711 | 13.418 | 13.4625 | 13.5085 | 13.5565 | 13.6059 | 13.6527 | 13.7047 | 13.7585 | 14.0227 | 14.2872
|  |  |  | Base Case [MW] |  |  | 13.0336 | 13.0885 | 13.1438 | 13.199 | 13.2582 | 13.3211 | 13.3696 | 13.4194 | 13.47 | 13.5222 | 13.575 | 13.6287 | 13.6874 | 13.7426 | 13.8026 | 13.8671 | 14.1774 | 14.4884
|  |  |  | Aggressive [MW] |  |  | 13.0336 | 13.1116 | 13.1935 | 13.2789 | 13.3674 | 13.4621 | 13.5118 | 13.5627 | 13.6148 | 13.6681 | 13.7225 | 13.7778 | 13.8342 | 13.8951 | 13.9529 | 14.0153 | 14.3148 | 14.6151
| WILTON | 10 | 1 | Conservative [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Best View [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Base Case [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
|  |  |  | Aggressive [MW] |  |  | 0 | 0 | 0 | 0 | 0 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525 | 18.525
| WINDSOR | 20 | 1 | Conservative [MW] |  |  | 3.1798 | 3.1942 | 3.2096 | 3.2238 | 3.2391 | 3.2458 | 3.3048 | 3.3637 | 3.4223 | 3.4818 | 3.542 | 3.6029 | 3.6627 | 3.7226 | 3.7826 | 3.8422 | 4.1412 | 4.4401
|  |  |  | Best View [MW] |  |  | 3.1798 | 3.214 | 3.2489 | 3.2834 | 3.3187 | 3.3458 | 3.4183 | 3.4907 | 3.5644 | 3.6373 | 3.7107 | 3.7841 | 3.857 | 3.9291 | 3.9994 | 4.0673 | 4.4134 | 4.759
|  |  |  | Base Case [MW] |  |  | 3.1798 | 3.2293 | 3.2791 | 3.3293 | 3.381 | 3.4222 | 3.5107 | 3.5988 | 3.6873 | 3.7756 | 3.8628 | 3.9495 | 4.033 | 4.1136 | 4.1876 | 4.257 | 4.6163 | 4.9748
|  |  |  | Aggressive [MW] |  |  | 3.1798 | 3.2791 | 3.3808 | 3.4839 | 3.5872 | 3.6817 | 3.7994 | 3.9131 | 4.0254 | 4.1297 | 4.2258 | 4.3117 | 4.3785 | 4.4184 | 4.4205 | 4.3663 | 4.2452 | 4.1147
| WOODFORD | 10 | 1 | Conservative [MW] |  |  | 13.1891 | 13.2317 | 13.2768 | 13.3244 | 13.3698 | 13.4178 | 13.4864 | 13.5549 | 13.6274 | 13.7041 | 13.7753 | 13.8548 | 13.9288 | 14.0107 | 14.0912 | 14.1697 | 14.5675 | 14.965
|  |  |  | Best View [MW] |  |  | 13.1891 | 13.2438 | 13.2961 | 13.354 | 13.4088 | 13.4695 | 13.5672 | 13.6646 | 13.7701 | 13.8749 | 13.9825 | 14.0924 | 14.2044 | 14.3178 | 14.4321 | 14.5515 | 15.1347 | 15.7187
|  |  |  | Base Case [MW] |  |  | 13.1891 | 13.2651 | 13.344 | 13.4254 | 13.5093 | 13.5956 | 13.6942 | 13.7967 | 13.9024 | 14.011 | 14.1217 | 14.2341 | 14.3526 | 14.4672 | 14.5861 | 14.7093 | 15.3137 | 15.9189
|  |  |  | Aggressive [MW] |  |  | 13.1891 | 13.2976 | 13.4159 | 13.5345 | 13.6572 | 13.7834 | 13.9043 | 14.0286 | 14.1603 | 14.289 | 14.4284 | 14.5628 | 14.7061 | 14.8518 | 14.9986 | 15.1458 | 15.8808 | 16.6159
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0
[23 empty] | 0 | 0

## 3. Capacity Search
| Substation Selector | [14 empty] | Geographical Substation Search
[16 empty] | Leave "Select Substation" as dash for geographical search. Enter your site coordinates below to find the capacity at the nearest HV substation. |  |  |  |  | Sequence of Available Connection Methods | List of Available Connection Methods | Voltages Available at Substation | This list forms the Station Selector Options. Automatically updates. Do not touch
| Select Substation |  | Substation Connection Voltages (10,20,38) | Connection Method Selector (Max: 1) | [12 empty] | Latitude | Longitude |  |  | 1 | ATHENRY-T42_5_MVA_ATHENRY | 10 | -
Select Station here → | - |  | 10 | 1 | [11 empty] | Enter Coordinates here → | 53.2863 | -8.7358 |  |  |  |  | 20 | ABBEYFEALE
[23 empty] | 38 | ABBEYLAND
ABBEYLEIX
| Nth Closest Substation | Station Configuration | Normal Feeding 110 kV Node | [13 empty] | Coordinate System | Nth closest | [5 empty] | ACADEMY STREET
Search Result: | ATHENRY 38 KV | 38/10 kV - 2 x 5 MVA | GALWAY | [13 empty] | Latitude/Longitude | 1 | [5 empty] | ACHILL
ADAMSTOWN
AGHAGAD
AGHAMORE
[17 empty] | Easting | Northing | [5 empty] | AHANE
[16 empty] | Enter Irish Grid Reference here → | 316711 | 233306 | [5 empty] | ARDFINNAN
ARDGEEHA
ARDNACRUSHA
Substation Generation Headroom Capacity | [20 empty] | Transformer name | Sheet name | Firm/Non-Firm Connection | ARDNAGAPPARY
ATHENRY 38 KV substation. Local 38/10 kV transformer headroom capacity [MW] | [20 empty] | T42_5_MVA_ATHENRY | Mixed-Dual-38-MV | Firm | ARDNAREE
38/MV Transformer | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050 | [5 empty] | ARIGNA
conservative | 6.2275 | 6.2487 | 6.269 | 6.2886 | 6.3074 | 6.3311 | 6.3657 | 6.4024 | 6.4409 | 6.4767 | 6.5189 | 6.5581 | 6.5988 | 6.6413 | 6.6801 | 6.7252 | 6.9339 | 7.1436 | [5 empty] | ARKLOW
best view | 6.2275 | 6.2551 | 6.2854 | 6.3141 | 6.3457 | 6.3769 | 6.4248 | 6.4767 | 6.5327 | 6.5878 | 6.6418 | 6.6989 | 6.7591 | 6.8172 | 6.8778 | 6.9404 | 7.2481 | 7.556 | [5 empty] | ARTANE
base case | 6.2275 | 6.2664 | 6.3025 | 6.3403 | 6.3798 | 6.4222 | 6.4817 | 6.5394 | 6.5992 | 6.6657 | 6.7293 | 6.7938 | 6.8641 | 6.9348 | 7.005 | 7.0796 | 7.4409 | 7.8029 | [5 empty] | ASHBOURNE
aggressive | 6.2275 | 6.2878 | 6.3538 | 6.4206 | 6.4925 | 6.5612 | 6.6387 | 6.7142 | 6.7968 | 6.8809 | 6.9656 | 7.0501 | 7.1383 | 7.2339 | 7.3262 | 7.4184 | 7.8796 | 8.3407 | [5 empty] | ATHBOY
ATHENRY
ATHGARVAN
- | [23 empty] | ATHLONE
110/MV Transformer | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050 | [5 empty] | ATHY
conservative | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | BAGENALSTOWN
best view | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  | Nth Closest Substation | Connection Method Selected | Trafo Type | BAILIEBORO
base case | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  | ATHENRY | ATHENRY-T42_5_MVA_ATHENRY | 38 kV - MV | BALBRIGGAN
aggressive | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 38 KV |  |  | BALGADDY
BALLAGHADERREEN
BALLINACURRA
BSP: | GALWAY | GALWAY | GALWAY | GALWAY | GALWAY | GALWAY | GALWAY | GALWAY | GALWAY | GALWAY | GALWAY | GALWAY | GALWAY | GALWAY | GALWAY | GALWAY | [7 empty] | BALLINASLOE
GALWAY 110/38 kV transformer headroom capacity [MW] | [23 empty] | BALLINCLEA
110/38 Transformer - at Bulk Supply Point | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050 |  |  | Transformer Primary Voltage | Transformer Secondary Voltage (Connection Voltage) |  | BALLINCOLLIG
conservative | 87.3691 | 87.6903 | 88.01 | 88.337 | 88.6622 | 86.2831 | 86.7116 | 87.1459 | 87.5806 | 88.0259 | 88.4788 | 88.929 | 89.3914 | 89.8578 | 90.3308 | 90.805 | 93.1729 | 95.5409 |  |  | 41.6 | 10.7 |  | BALLINDERRY
best view | 87.3691 | 87.7834 | 88.2032 | 88.6248 | 89.0514 | 86.7127 | 87.3234 | 87.9423 | 88.5715 | 89.2128 | 89.8652 | 90.5255 | 91.1927 | 91.8659 | 92.5412 | 93.2166 | 96.5934 | 99.9703 | [5 empty] | BALLINROBE
base case | 87.3691 | 87.8993 | 88.436 | 88.9818 | 89.5365 | 87.2791 | 87.9556 | 88.643 | 89.3406 | 90.0551 | 90.7776 | 91.5068 | 92.2391 | 92.9772 | 93.7088 | 94.4365 | 98.0855 | 101.7338 | [5 empty] | BALLINVALLY
aggressive | 87.3691 | 88.2047 | 89.0605 | 89.9293 | 90.828 | 88.7633 | 89.5638 | 90.3846 | 91.2112 | 92.0491 | 92.8855 | 93.7198 | 94.5506 | 95.3651 | 96.1574 | 96.9201 | 100.8126 | 104.7001 | [5 empty] | BALLYARD
BALLYBAILIE
BALLYBAY
BALLYBEG
BALLYBEGGAN
BALLYBODEN
BALLYBUNION
BALLYCONNELL
BALLYCONRA
BALLYCOOLIN
BALLYCROSSAUN
BALLYCUMMIN
BALLYDEHOB
BALLYDINE
Consolidated Generation Capacity | [23 empty] | BALLYGAR
Weakest capacity in the chain | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2045 | 2050 | first year of power flow results | last year of power flow results |  |  |  | BALLYHALE
conservative | 6.2275 | 6.2487 | 6.269 | 6.2886 | 6.3074 | 6.3311 | 6.3657 | 6.4024 | 6.4409 | 6.4767 | 6.5189 | 6.5581 | 6.5988 | 6.6413 | 6.6801 | 6.7252 | 6.9339 | 7.1436 | 2025 | 2040 |  |  |  | BALLYHAUNIS
best view | 6.2275 | 6.2551 | 6.2854 | 6.3141 | 6.3457 | 6.3769 | 6.4248 | 6.4767 | 6.5327 | 6.5878 | 6.6418 | 6.6989 | 6.7591 | 6.8172 | 6.8778 | 6.9404 | 7.2481 | 7.556 | 2025 | 2040 |  |  |  | BALLYJAMESDUFF
base case | 6.2275 | 6.2664 | 6.3025 | 6.3403 | 6.3798 | 6.4222 | 6.4817 | 6.5394 | 6.5992 | 6.6657 | 6.7293 | 6.7938 | 6.8641 | 6.9348 | 7.005 | 7.0796 | 7.4409 | 7.8029 | 2025 | 2040 |  |  |  | BALLYLICKEY
aggressive | 6.2275 | 6.2878 | 6.3538 | 6.4206 | 6.4925 | 6.5612 | 6.6387 | 6.7142 | 6.7968 | 6.8809 | 6.9656 | 7.0501 | 7.1383 | 7.2339 | 7.3262 | 7.4184 | 7.8796 | 8.3407 | 2025 | 2040 |  |  |  | BALLYMACARRY
BALLYMAHON
BALLYMAKENNY
BALLYMOTE
BALLYMOUNT
BALLYMUN
BALLYRAGGET
BALLYRAINE
BALLYRICKARD
BALLYSHANNON
BALLYTIVNAN
BALTINGLASS
BALTRASNA
BANAGHER
BANDON
BANGOR ERRIS
BANOGE
BANTRY
BARNAHELY_A
BARNAHELY_B
BARODA
BARRYMORE
BATTER LANE
BEALISTOWN
BEALNABLATH
BEDFORD ROW
BELFIELD
BELGARD
BELLACORRICK
BELLFIELD
BELMAYNE
BELMULLET
BELVIEW
BETTYSTOWN
BINBANE
BIRDHILL
BIRR
BISHOPSTOWN
BLACKROCK
BLAKE
BLANCHFIELD
BLESSINGTON
BLUNDELSTOWN
BOGGERAGH
BOGHALL ROAD
BOOLTIAGH
BORRISOLEIGH
BOYLE
BRACKLONE
BRAY
BREWERY ROAD
BRUFF
BUNCLODY
BUNCRANA
BUNDORAN
BUSH
BUSHFIELD
BUTLERSTOWN
BUTTEVANT
CABRA
CAHERDAVIN
CAHIR
CAHIRCALLA
CALLAN
CAMDEN ROW
CAPPAMORE
CARLOW
CARNDONAGH
CAROLINE STREET
CARRAROE
CARRICK ON SHANNON
CARRICKMACROSS
CARRICKMINES
CARRIGALINE
CARRIGALLEN
CARRIGLAWN
CARRIGSHANE
CARRIGTWOHILL
CARROWBEG
CASHEL
CASTLEBAR
CASTLEBLAYNEY
CASTLECOMER
CASTLEISLAND
CASTLEKNOCK
CASTLELYONS
CASTLEREA
CASTLETOWNBERE
CASTLETOWNROCHE
CASTLETROY
CASTLEVIEW
CATHALEENS FALL
CAUSEWAY
CAUTEEN
CAVAN
CELBRIDGE
CENTRAL PARK
CHARLESTOWN
CHARLEVILLE
CHERRYWOOD
CHURCHTOWN
CITYWEST
CLADY
CLARA
CLAREGALWAY
CLARKSTOWN
CLIFDEN
CLOGHBOOLA
CLONAKILTY
CLONARD
CLONDALKIN
CLONES
CLONMINCH
CLONROCHE
CLONSHAUGH
CLONTARF
CLOON
CLOONBANNIN
CLOONLOUGH
CLOYNE
COES ROAD
COLLEGE PARK
COLLIGAN
COLLINSTOWN
COLLOONEY
CONG
CONVOY
COOKSTOWN
COOLCARRON
COOLCORCORAN
COOLMINE
COOLOCK
COOLROE
COOMATAGGERT
CORBALLY
CORDAL
CORDERRY
CORDUFF
CORKERMORE
COURTLOUGH
COW CROSS
CRANE
CRANMORE
CRANNY
CRATLOE
CREAGH
CREESLOUGH
CREGG ROAD
CRORY
CROSSMOLINA
CRUMLIN
CULLION
CURRA
CURRAGLASS
CURRALEIGH
DALLOW
DALTON
DEANSGRANGE
DEERPARK
DELVIN
DENNEHYS CROSS
DERRYBEG
DERRYCRAMPH
DERRYIRON
DINGLE
DOCK ROAD
DODDER ROAD
DONEGAL
DONNYBROOK
DONORE ROAD
DOON
DOUGLAS
DROMBEG
DROMTHACKER
DRUMBEAR
DRUMCONDRA
DRUMLINE
DRUMQUIN
DRYBRIDGE
DULEEK
DUN LAOGHAIRE
DUNDALK
DUNDRUM
DUNFIRTH
DUNGARVAN
DUNGLOE
DUNLEER
DUNMANWAY
DUNSINK
EAST ATHLONE
EAST GALWAY
EAST WALL ROAD
EASTMONT
EDENDERRY
EDGEWORTHSTOWN
EMYVALE
ENNIS
ENNIS NORTH
ENNISCRONE
ENNISKEANE
ENNISTYMON
ERRIGAL
FACTORY CROSS
FAIRHILL
FAIRVIEW
FASSAROE
FERMOY
FERMOY NORTH
FERNS
FINGLAS
FINISKLIN
FINNEA
FORTUNESTOWN
FOSTERSTOWN
FOXHOLE
FOYNES
FRANCIS STREET
GALWAY
GARRANACANTY
GARROW
GARRYCASTLE
GARRYOWEN
GARRYSPILLANE
GARVAGH
GARVILLE AVENUE
GILLOGUE
GLASMORE
GLASNEVIN
GLEBE
GLENAMADDY
GLENGARRIFF
GLENGOOLE
GLENLARA
GLENREE
GLENTIES
GLOUCESTER PLACE
GORESBRIDGE
GORT
GORTAWEE
GORTLEE
GRAIGUE
GRAIGUENAMANAGH
GRANAGH
GRANBY ROW
GRANGE (DR)
GRANGE (SR)
GRANGE CASTLE
GREAT ISLAND
GREENHILLS
GREYSTONES
GRIFFINRATH
GURRANEBANE
GURTEEN
GWEEDORE
HAROLDS CROSS
HARTNETTS CROSS
HEADFORD
HEADFORD ROAD
HEUSTON SQUARE
HOLYCROSS ROAD
HOWTH JUNCTION
IKERRIN
INCH
INCHICORE
JENKINSTOWN
JOHNSTOWN
JULIANSTOWN
KANTURK
KELLS
KENMARE
KILBARRY
KILCAR
KILCARAGH
KILCLOHER
KILCOCK
KILCOLGAN
KILCOOLE
KILCULLEN
KILDARE
KILFLYNN
KILGARVAN
KILKEE
KILKENNY
KILLACLOYNE
KILLESHANDRA
KILLIN HILL
KILLINICK
KILLOTERAN
KILLYBEGS
KILLYGARRY
KILMACTHOMAS
KILMAGIG
KILMALLOCK
KILMARTIN
KILMEADEN
KILMONEY
KILMORE
KILNAP
KILPADDOGE
KILROSS ROAD
KILRUSH
KILSARAN
KILSHANNY
KILTEEL
KILTIMAGH
KIMMAGE
KINGSBRIDGE
KINGSCOURT
KINSALE
KNOCKAPHUNTA
KNOCKEARAGH
KNOCKMULLEN
KNOCKNAGEE
KYLEERAGH
LANESBOROUGH
LAWLESSTOWN
LEESON STREET
LEIXLIP
LETTERKENNY
LIBERTY STREET
LIFFEY VALLEY
LIMERICK
LISDRUM
LISHEEN
LISMORE
LITTLE BRAY
LITTLE MILLS
LLOYD
LONGFORD
LOUGHANALLA
LOUGHLINSTOWN
LOUGHREA
LOUGHSHINNY
LOUGHTAGALLA
LUCAN EAST
LUMCLOON
MACETOWN
MACROOM
MALAHIDE
MALLOW
MANGANS
MANOR STREET
MANORHAMILTON
MARINA
MARROWBONE LANE
MARSHES
MAYFIELD
MCDERMOTT
MCDONAGH
MEATH HILL
MERRION SQUARE
MERVILLE
MIDLETON
MILFORD (MWR)
MILFORD (NR)
MILLTOWN (DR)
MILLTOWN (SR)
MILLTOWN MALBAY
MISERY HILL
MOATE
MOHILL
MONEENAGHIESHA
MONEYCOOLEY
MONFIN
MONKSTOWN
MONREAD
MORNINGTON ROAD
MORRISTOWN
MOUNT MERRION
MOUNT MISERY
MOUNTGORRY
MOUNTMELLICK
MOUNTRATH
MOVILLE
MOY
MOYLISH
MULGANNON
MULLAGH
MULLAGHARLIN
MULLINGAR
NAAS
NAVAN
NENAGH
NEW CASTLEBAR
NEW GURRANEBANE
NEW KILLINICK
NEW KILMONEY-CARRIGALINE STATION
NEW MAYFIELD-RIVERSTOWN STATION
NEW MONAGHAN
NEW TINAHASK
NEWBRIDGE
NEWBRIDGE EAST
NEWBROOK
NEWCASTLEWEST
NEWMARKET (DR)
NEWMARKET (SR)
NEWPORT
NEWTOWNCUNNINGHAM
NORTH CITY JUNCTION
NORTH EAST CASHEL
NORTH QUAYS
NUTLEY LANE
OAKFIELD
OLDBAWN
OLDCASTLE
ORANMORE
OUGHTERARD
OUGHTRAGH
PALLAS
PALMERSTOWN
PARKMORE
PATRICKSWELL
PELLETSTOWN
PEMBROKE
PHIBSBORO
POLLERTON
POPPINTREE
PORTARLINGTON
PORTLAOISE
PORTLAW
POTTERY ROAD
PURCELLS INCH
RAHANS
RAHEEN
RAMPARTS
RANDALSTOWN
RATHDOWNEY
RATHDRUM
RATHKEALE
RATHMORE
RATHMULLAN
REAMORE
RECESS
RICHMOND
RINAWADE
RINEANNA
RINGASKIDDY 110KV
RINGSEND
RIVERSTOWN
ROCHES STREET
ROOSKY
ROSBERCON
ROSCOMMON
ROSCREA
ROSEHILL
ROSS CARBERY
ROSSGEIR
SAGGART
SALLINS
SALLYNOGGIN ROAD
SALTHILL
SANDYFORD
SANTRY
SCARIFF
SCARTEEN
SCREEB
SEMPERIT
SHANKILL
SHANNON
SHERCOCK
SHERIFF STREET
SHILLELAGH
SINGLAND
SKIBBEREEN
SLANE
SLIGO
SMEARLA
SOMERSET
SORNE HILL
SOUTH EAST CARLOW
SOUTH KING STREET
SOUTH NAVAN
SPA ROAD
SPIDDAL
SPRINGS
SRAH
STEEVENS LANE
STEPHENSTOWN
STICKILLEN
STRANORLAR
STRATFORD
SUTTON
SWINFORD
SWORDS
TALBOTS INCH
TALBOTS INCH/ROSEHILL
TANEY
TAWNAGHMORE
TELAYDON
TEMPLEMORE
TEMPLEOGUE
TERMONFECKIN ROAD
THORNSBERRY
THURLES
TIMOLEAGUE
TINAHASK
TIPPERARY
TOGHER
TONROE
TOOMEVARA
TRABEG
TRALEE
TRAMORE
TRIEN
TRILLICK
TRIM
TRIMMS LANE
TRINITY
TUAM NORTH
TUAM SOUTH
TUBBERCURRY
TULLA
TULLABRACK
TULLOW
TULLYNAMALRA
TURLOUGH ROAD
TYCOR
TYMON
UNIDARE
URLINGFORD
VIRGINIA
WALTERSTOWN
WATERFORD
WATERFORD IND EST
WATLING STREET
WEST PORTLAOISE
WESTPORT
WEXFORD
WHITECHURCH
WHITEHALL
WHITESTOWN
WILTON
WINDSOR
WOLFE TONE STREET
WOODFORD
YELLOWMEADOWS
Note on B3: Leave as dash for geographical search. Otherwise select prefered substation

## Station Coordinates (hidden)
Station Name | Present in demand results? | Present in generation results? | Functional Location | Google Maps | Latitude | Longitude | Substation Voltage Level | Distance in km from Selected Latitude/Longitude Site | Distance in km from Selected Easting/Northing Site | Easting (X) | Northing (Y) | Latitude | Longitude | Easting | Northing
ABBEYFEALE | 32 | 64 | 429000 | Google Maps | 52.3927 | -9.3029 | 38 KV | 106.4108 | 230.9911 | 111355 | 127543 | 51.9353 | -10.2319 | 46524.3791 | 83209.4089
ABBEYLAND | 32 | 64 | 270000 | Google Maps | 53.6632 | -6.6949 | 38 KV | 141.4138 | 46.83 | 286321 | 268936
ABBEYLEIX | 32 | 64 | 565000 | Google Maps | 52.9109 | -7.3586 | 38 KV | 100.9766 | 88.1824 | 243200 | 184600
ACADEMY STREET | 32 | 64 | 617000 | Google Maps | 53.6471 | -6.6777 | 38 KV | 142.0109 | 44.7241 | 287492 | 267166
ACHILL | 32 | 64 | 495000 | Google Maps | 53.9411 | -9.8934 | 38 KV | 105.5098 | 250.2517 | 75713 | 300729
ADAMSTOWN | 32 | 64 | 497000 | Google Maps | 53.3403 | -6.4789 | 110 KV | 150.0417 | 15.359 | 301352 | 233285
AGANNYGAL | 0 | 0 | 984000 | Google Maps | 53.0362 | -8.5497 | 110 KV | 30.4469 | 157.4308 | 163176 | 198500
AGHADA | 0 | 0 | 631000 | Google Maps | 51.835 | -8.228 | 220 KV | 164.977 | 214.3518 | 184331 | 64717
AGHADA 110KV | 0 | 0 | 637000 | Google Maps | 51.835 | -8.228 | 110 KV | 164.9771 | 214.3518 | 184331 | 64717
AGHAGAD | 32 | 64 | 645000 | Google Maps | 54.3657 | -8.5142 | 38 KV | 120.9107 | 187.9638 | 166624 | 346462
AGHAMORE | 32 | 64 | 124000 | Google Maps | 53.6736 | -7.9758 | 38 KV | 66.2078 | 120.5622 | 201646 | 269296
AHANE | 0 | 64 | 900000 | Google Maps | 52.6618 | -8.5077 | 110 KV | 71.093 | 169.2798 | 165698 | 156816
AIRTON | 0 | 0 | 326000 | Google Maps | 53.2969 | -6.3675 | 110 KV | 157.4082 | 9.1256 | 308884 | 228614
ALLENWOOD | 0 | 0 |  | Google Maps | 53.2893 | -6.8818 | 38 KV | 123.2344 | 42.5539 | 274611 | 227107
ANALOG | 0 | 0 | 609000 | Google Maps | 52.6258 | -8.6578 | 38 KV | 73.6248 | 180.1498 | 155506 | 152889
ANNABELLA | 0 | 0 | 464000 | Google Maps | 52.1409 | -8.6532 | 38 KV | 127.4809 | 210.0082 | 155325 | 98926
ANNER | 0 | 0 | 779000 | Google Maps | 52.372 | -7.6492 | 110 KV | 125.155 | 142.9905 | 223940 | 124495
ARDFINNAN | 32 | 64 | 386000 | Google Maps | 52.3089 | -7.892 | 38 KV | 122.5941 | 159.2916 | 207418 | 117423
ARDGEEHA | 32 | 64 | 034000 | Google Maps | 52.3724 | -7.6998 | 38 KV | 123.1595 | 145.2201 | 220495 | 124534
ARDMORE | 0 | 0 | 540000 | Google Maps | 54.6402 | -7.8985 |  | 160.2043 | 180.9521 | 206600 | 376900
ARDNACRUSHA | 32 | 64 | 990000 | Google Maps | 52.7059 | -8.6134 | 110 KV | 65.0471 | 173.551 | 158585 | 161779
ARDNAGAPPARY | 32 | 64 | 819000 | Google Maps | 55.0565 | -8.2692 | 110 KV | 199.1711 | 232.3968 | 182841 | 423272
ARDNAREE | 32 | 64 | 089000 | Google Maps | 54.1128 | -9.1431 | 38 KV | 95.7408 | 209.6423 | 125289 | 318790
ARIGNA | 0 | 64 | 417000 | Google Maps | 54.0947 | -8.0752 | 110 KV | 99.862 | 147.1353 | 195129 | 316171
ARKLOW | 32 | 64 | 917000 | Google Maps | 52.8151 | -6.1474 | 220 KV | 180.7545 | 58.5328 | 324957 | 175357
ARKLOW BANKS | 0 | 0 | 376000 | Google Maps | 52.7939 | -6.1412 | 38 KV | 181.8828 | 60.9168 | 325434 | 173017
ARTANE | 32 | 64 | 966000 | Google Maps | 53.3823 | -6.2095 | 110 KV | 168.0735 | 5.6454 | 319192 | 238377
ARTHURSTOWN | 0 | 0 | 085000 | Google Maps | 53.2282 | -6.5711 | 38 KV | 144.1319 | 24.7071 | 295476 | 220676
ARVA | 0 | 0 | 811000 | Google Maps | 53.9086 | -7.4944 | 110 KV | 107.2343 | 104.1113 | 233277 | 295579
ASHBOURNE | 96 | 64 | 335000 | Google Maps | 53.4907 | -6.3702 | 38 KV | 158.5009 | 18.8846 | 308222 | 250175
ASHE ROAD | 0 | 0 | 052000 | Google Maps | 53.5289 | -7.3585 | 38 KV | 95.1934 | 76.7957 | 242588 | 253390
ASKEATON | 0 | 0 | 437000 | Google Maps | 52.6093 | -8.9842 | 38 KV | 77.0923 | 200.8398 | 133374 | 151305
ATHBOY | 32 | 64 | 177000 | Google Maps | 53.6374 | -6.9389 | 38 KV | 125.1948 | 56.7031 | 270237 | 265793
ATHEA | 0 | 0 | 106000 | Google Maps | 52.4376 | -9.3005 | 110 KV | 101.6955 | 228.5196 | 111609 | 132537
ATHENRY | 32 | 64 | 142000 | Google Maps | 53.2863 | -8.7358 | 38 KV | 0 | 165.8752 | 150978 | 226440
ATHGARVAN | 32 | 64 | 394000 | Google Maps | 53.162 | -6.7955 | 38 KV | 129.8967 | 41.3983 | 280613 | 213039
ATHLONE | 32 | 64 | 897000 | Google Maps | 53.423 | -7.9745 | 110 KV | 52.7623 | 115.251 | 201745 | 241406
ATHY | 32 | 12 | 927000 | Google Maps | 52.9934 | -6.9994 | 110 KV | 120.3046 | 63.1443 | 267238 | 194068
AUGHINISH | 0 | 0 | 780000 | Google Maps | 52.6251 | -9.0511 | 110 KV | 76.4939 | 204.2386 | 128870 | 153124
AVOCA | 0 | 0 | 218000 | Google Maps | 52.8725 | -6.2211 | 38 KV | 174.1441 | 51.7719 | 319811 | 181627
AVONCORE | 0 | 0 | 029000 | Google Maps | 51.933 | -8.1853 | 38 KV | 154.995 | 203.9948 | 187304 | 75611
BAGENALSTOWN | 32 | 64 | 389000 | Google Maps | 52.6987 | -6.9343 | 38 KV | 137.1284 | 84.6822 | 272094 | 161331
BAILIEBORO | 32 | 64 | 138000 | Google Maps | 53.8957 | -6.9679 | 38 KV | 134.9247 | 78.2861 | 267901 | 294513
BALBRIGGAN | 32 | 12 | 065000 | Google Maps | 53.6097 | -6.19 | 38 KV | 172.3706 | 30.5634 | 319848 | 263708
BALGADDY | 32 | 64 | 623000 | Google Maps | 53.3362 | -6.4344 | 38 KV | 152.9886 | 12.3751 | 304343 | 232887
BALGRIFFIN | 0 | 0 | 710000 |  |  |  | 220 kV | 5980.1028 | 393.3669
BALLAGHADERREEN | 32 | 20 | 433000 | Google Maps | 53.9085 | -8.5732 | 38 KV | 70.0142 | 166.4263 | 162380 | 295593
BALLINACURRA | 96 | 64 | 126000 | Google Maps | 52.6492 | -8.6366 | 38 KV | 71.1491 | 177.6968 | 156964 | 155479
BALLINASLOE | 32 | 64 | 118000 | Google Maps | 53.3214 | -8.1875 | 38 KV | 36.6405 | 129.1954 | 187555 | 230116
BALLINCLEA | 32 | 64 | 396000 | Google Maps | 53.2709 | -6.122 | 38 KV | 173.7789 | 11.2237 | 325341 | 226130
BALLINCOLLIG | 32 | 64 | 341000 | Google Maps | 51.8768 | -8.6179 | 38 KV | 156.9238 | 228.3959 | 157519 | 69530
BALLINCOLLIG HILL | 0 | 0 | 319000 |  |  |  | 38 KV | 5980.1028 | 393.3669
BALLINDERRY | 32 | 64 | 383000 | Google Maps | 53.518 | -7.3242 | 38 KV | 97.0593 | 74.2767 | 244876 | 252194
BALLINEEN | 0 | 0 | 476000 | Google Maps | 51.7328 | -8.9815 | 38 KV | 173.5346 | 257.4112 | 132243 | 53773
BALLINROBE | 32 | 64 | 238000 | Google Maps | 53.6275 | -9.2084 | 38 KV | 49.1802 | 199.1233 | 120101 | 264843
BALLINVALLY | 0 | 64 | 408000 | Google Maps | 52.796 | -6.2914 | 38 KV | 172.2599 | 60.3225 | 315300 | 173000
BALLYARD | 32 | 20 | 278000 | Google Maps | 52.2566 | -9.7039 | 38 KV | 131.7183 | 262.2519 | 83698 | 112969
BALLYBAILIE | 32 | 64 | 269000 | Google Maps | 53.8717 | -6.534 | 38 KV | 159.2604 | 62.4101 | 296480 | 292346
BALLYBAY | 32 | 20 | 061000 | Google Maps | 54.1208 | -6.9074 | 38 KV | 151.9623 | 97.4424 | 271494 | 319622
BALLYBEG | 32 | 64 | 781000 | Google Maps | 52.991 | -6.0959 | 110 KV | 179.1149 | 39.8909 | 327912 | 195020
BALLYBEGGAN | 32 | 64 | 462000 | Google Maps | 52.2708 | -9.6797 | 38 KV | 129.5398 | 260.0426 | 85392 | 114505
BALLYBODEN | 32 | 64 | 198000 | Google Maps | 53.2798 | -6.2882 | 38 KV | 162.7084 | 6.9305 | 314232 | 226834
BALLYBRIT | 0 | 0 | 627000 | Google Maps | 53.2919 | -9.0111 | 38 KV | 18.3131 | 184.1863 | 132623 | 227290
BALLYBUNION | 32 | 64 | 363000 | Google Maps | 52.5035 | -9.6562 | 38 KV | 106.7125 | 247.2475 | 87596 | 140367
BALLYCADDEN | 0 | 0 | 566000 |  |  |  | 110 kV | 5980.1028 | 393.3669
BALLYCONNELL | 32 | 64 | 571000 | Google Maps | 54.1126 | -7.5897 | 38 KV | 118.883 | 123.6204 | 226883 | 318235
BALLYCONRA | 0 | 64 | 479000 | Google Maps | 52.801 | -7.3539 | 38 KV | 106.9866 | 95.15 | 243631 | 172373
BALLYCOOLIN | 32 | 64 | 514000 | Google Maps | 53.4043 | -6.3563 | 38 KV | 158.4899 | 10.3394 | 309367 | 240584
BALLYCROSSAUN | 32 | 64 | 250000 | Google Maps | 53.1509 | -8.1908 | 38 KV | 39.2854 | 131.3103 | 187286 | 211135
BALLYCUMMIN | 0 | 44 | 928000 | Google Maps | 52.6239 | -8.6622 | 110 kV | 73.8183 | 180.5066 | 155207 | 152689
BALLYDEHOB | 32 | 64 | 535000 | Google Maps | 51.5667 | -9.4726 | 38 KV | 197.6276 | 294.6981 | 97938 | 35859
BALLYDINE | 32 | 64 | 727000 | Google Maps | 52.3614 | -7.5211 | 110 KV | 131.2833 | 138.3702 | 232677 | 123376
BALLYDOORLIS | 0 | 0 | 381000 | Google Maps | 52.5272 | -9.0986 | 38 KV | 87.8383 | 211.7811 | 125489 | 142282
BALLYGAR | 32 | 20 | 324000 | Google Maps | 53.5199 | -8.3223 | 38 KV | 37.7661 | 139.3336 | 178670 | 252241
BALLYHALE | 32 | 64 | 010000 | Google Maps | 52.4701 | -7.1953 | 38 KV | 137.5566 | 115.6487 | 254738 | 135664
BALLYHAUNIS | 32 | 20 | 368000 | Google Maps | 53.7588 | -8.7525 | 38 KV | 52.5547 | 172.471 | 150415 | 279043
BALLYJAMESDUFF | 32 | 64 | 139000 | Google Maps | 53.8499 | -7.1955 | 38 KV | 119.4676 | 84.7721 | 252996 | 289223
BALLYKEERAN | 0 | 0 | 257000 | Google Maps | 55.0171 | -7.7389 | 38 KV | 203.1125 | 210.787 | 216753 | 418885
BALLYKETT | 0 | 0 | 398000 | Google Maps | 52.6793 | -9.4781 | 38 KV | 83.8154 | 228.8072 | 100080 | 159660
BALLYLICKEY | 32 | 64 | 728000 | Google Maps | 51.7241 | -9.4296 | 110 KV | 179.9372 | 280.7373 | 101264 | 53317
BALLYLINAN ROAD | 0 | 0 | 013000 | Google Maps | 52.9888 | -6.9934 | 38 KV | 120.8354 | 63.148 | 267646 | 193553
BALLYMACARRY | 32 | 64 | 607000 | Google Maps | 55.1237 | -7.4509 | 38 KV | 220.7382 | 213.7552 | 235082 | 430861
BALLYMAHON | 32 | 64 | 076000 | Google Maps | 53.5894 | -7.8214 | 38 KV | 69.3126 | 108.1668 | 211875 | 259942
BALLYMAKENNY | 0 | 52 |  | Google Maps | 53.7379 | -6.363 | 38 KV | 164.7257 | 45.2282 | 308054 | 277698
BALLYMOTE | 32 | 64 | 496000 | Google Maps | 54.0881 | -8.5341 | 38 KV | 90.1488 | 172.4909 | 165101 | 315571
BALLYMOUNT | 32 | 64 | 436000 | Google Maps | 53.3147 | -6.3454 | 38 KV | 158.8692 | 6.9256 | 310325 | 230626
BALLYMUN | 32 | 64 | 093000 | Google Maps | 53.3893 | -6.264 | 38 KV | 164.5016 | 5.8755 | 315547 | 239065
BALLYNAHULLA | 0 | 0 | 918000 | Google Maps | 52.1633 | -9.2897 | 110 KV | 130.3219 | 243.3717 | 111800 | 102000
BALLYRAGGET | 32 | 64 | 329000 | Google Maps | 52.799 | -7.3418 | 38 KV | 107.7934 | 94.6658 | 244443 | 172159
BALLYRAINE | 32 | 64 | 442000 | Google Maps | 54.9566 | -7.7144 | 38 KV | 197.298 | 204.1152 | 218346 | 412156
BALLYRICKARD | 32 | 64 | 173000 | Google Maps | 52.2703 | -9.724 | 38 KV | 131.0691 | 262.6889 | 82415 | 114517
BALLYSHANNON | 32 | 64 | 108000 | Google Maps | 54.4964 | -8.1933 | 38 KV | 139.1768 | 181.5942 | 187505 | 360908
BALLYTIVNAN | 32 | 64 | 445000 | Google Maps | 54.2845 | -8.4638 | 38 KV | 112.4283 | 180.0137 | 169843 | 337396
BALLYVOUSKILL | 0 | 0 | 906000 | Google Maps | 52.0054 | -9.0793 | 220 KV | 144.3035 | 242.1406 | 125930 | 84193
BALLYWATER | 0 | 0 | 814000 |  |  |  | 110 KV | 5980.1028 | 393.3669
BALTINGLASS | 4 | 4 | 294000 | Google Maps | 52.9368 | -6.6927 | 38 KV | 141.788 | 53.5838 | 287947 | 188097
BALTRASNA | 32 | 64 | 371000 | Google Maps | 53.5455 | -6.4404 | 110 KV | 154.8214 | 26.4411 | 303434 | 256172
BANAGHER | 32 | 64 | 305000 | Google Maps | 53.201 | -8.0132 | 38 KV | 49.0046 | 118.7139 | 199165 | 216695
BANCROFT | 0 | 0 | 882000 | Google Maps | 53.2936 | -6.3518 | 110 KV | 158.4522 | 8.4393 | 309936 | 228274
BANDON | 64 | 64 | 729000 | Google Maps | 51.7738 | -8.7338 | 110 KV | 168.1774 | 242.1704 | 149477 | 58151
BANGOR ERRIS | 32 | 64 | 206000 | Google Maps | 54.1461 | -9.7431 | 38 KV | 116.3386 | 247.5044 | 86146 | 323296
BANOGE | 32 | 64 | 809000 | Google Maps | 52.6502 | -6.2724 | 110 KV | 179.4769 | 76.5084 | 316969 | 156798
BANTRY | 32 | 64 | 111000 | Google Maps | 51.6877 | -9.4321 | 38 KV | 183.899 | 283.5426 | 101012 | 49267
BARNAHELY_A | 32 | 64 | 772000 | Google Maps | 51.8285 | -8.3446 | 110 KV | 164.2357 | 219.9427 | 176290 | 64023
BARNAHELY_B | 32 | 64 | 772000 | Google Maps | 51.8285 | -8.3446 | 110 KV | 164.2356 | 219.9427 | 176290 | 64023
BARNAKYLE | 0 | 0 | 879000 |  |  |  | 110 KV | 5980.1028 | 393.3669
BARNTOWN | 0 | 0 | 007000 | Google Maps | 52.3348 | -6.546 | 38 KV | 181.2408 | 113.3688 | 299160 | 121304
BARODA | 20 | 44 | 995000 | Google Maps | 53.1861 | -6.7751 | 110 KV | 130.9574 | 38.9634 | 281933 | 215738
BARRYMORE | 32 | 12 | 905000 | Google Maps | 52.0959 | -8.2547 | 110 KV | 136.2792 | 193.5565 | 182596 | 93745
BATTER LANE | 16 | 56 | 831000 | Google Maps | 53.4907 | -6.2062 | 110 KV | 169.2754 | 17.3 | 319095 | 250441
NEW CASTLEBAR | 0 | 44 |  | Google Maps | 53.8505 | -9.2792 | 38 KV | 72.2799 | 208.613 | 115878 | 289746
BAYSIDE | 0 | 0 | 553000 | Google Maps | 53.3914 | -6.1359 | 38 KV | 172.9983 | 9.6219 | 324064 | 239512
BEALISTOWN | 32 | 64 | 375000 | Google Maps | 52.2718 | -6.867 | 38 KV | 168.8826 | 125.7185 | 277393 | 113894
BEALNABLATH | 64 | 0 | 235000 | Google Maps | 51.8341 | -8.8788 | 38 KV | 161.7632 | 244.4519 | 139472 | 64952
BEAM HILL | 0 | 0 | 709000 | Google Maps | 55.1982 | -7.4404 | 38 KV | 228.6455 | 221.2239 | 235684 | 439157
BEDFORD ROW | 32 | 64 | 068000 | Google Maps | 53.3458 | -6.2614 | 38 KV | 164.4897 | 1.2697 | 315836 | 234226
BEENAGEEHA | 0 | 0 | 418000 | Google Maps | 52.2976 | -9.5516 | 38 kV | 122.8542 | 250.9353 | 94200 | 117300
BELFIELD | 32 | 64 | 310000 | Google Maps | 53.3062 | -6.2131 | 38 KV | 167.6594 | 4.1988 | 319165 | 229899
BELGARD | 32 | 64 | 331000 | Google Maps | 53.292 | -6.3673 | 38 KV | 157.4258 | 9.3817 | 308923 | 228075
BELLACORRICK | 0 | 20 | 896000 | Google Maps | 54.1209 | -9.5787 | 110 KV | 108.1249 | 236.448 | 96822 | 320234
BELLFIELD | 32 | 64 | 006000 | Google Maps | 52.5044 | -6.5774 | 38 KV | 168.8746 | 95.3144 | 296653 | 140126
BELMAYNE | 0 | 44 | 15K000 | Google Maps | 53.4053 | -6.1877 | 110 KV | 169.6537 | 8.5722 | 320563 | 240964
BELMULLET | 32 | 64 | 500000 | Google Maps | 54.2119 | -9.9635 | 38 KV | 130.8053 | 263.5372 | 71950 | 330999
BELVIEW | 32 | 64 | 605000 | Google Maps | 52.2655 | -7.037 | 38 KV | 161.0489 | 130.6468 | 265852 | 112965
BETTYSTOWN | 0 | 44 |  | Google Maps | 53.6942 | -6.262 | 38 KV | 169.8185 | 39.7301 | 314839 | 272992
BINBANE | 32 | 64 | 666000 | Google Maps | 54.719 | -8.2634 | 110 KV | 162.2805 | 202.6869 | 183077 | 385700
BIRDHILL | 32 | 64 | 153000 | Google Maps | 52.7694 | -8.4305 | 38 KV | 60.9918 | 159.3781 | 170992 | 168751
BIRR | 32 | 64 | 056000 | Google Maps | 53.0897 | -7.8905 | 38 KV | 60.4082 | 113.1033 | 207385 | 204320
BISHOPSTOWN | 20 | 20 | 254000 | Google Maps | 51.8871 | -8.5441 | 38 KV | 156.1136 | 224.0938 | 162587 | 70629
BLACKPOOL | 0 | 0 | 973000 | Google Maps | 52.3753 | -8.5368 | 110 kV | 102.1675 | 187.6638 | 163490 | 124950
BLACKROCK | 32 | 64 | 338000 | Google Maps | 53.2917 | -6.1746 | 110 KV | 170.2311 | 7.0856 | 321771 | 228346
BLACKWATER BRIDGE | 0 | 0 | 030000 | Google Maps | 51.9705 | -7.9068 | 38 KV | 156.6368 | 189.0238 | 206455 | 79769
BLAKE | 32 | 20 | 120000 | Google Maps | 53.2887 | -6.8814 | 110 KV | 123.2639 | 42.5239 | 274651 | 227042
BLANCHFIELD | 0 | 64 | 432000 | Google Maps | 52.6618 | -7.5086 | 38 KV | 107.576 | 113.179 | 233300 | 156807
BLANE | 0 | 0 | 510000 | Google Maps | 52.4899 | -9.2751 | 38 kV | 95.6539 | 224.3647 | 113440 | 138330
BLESSINGTON | 32 | 8 | 430000 | Google Maps | 53.1844 | -6.5255 | 38 KV | 147.5294 | 25.1284 | 298620 | 215866
BLUNDELSTOWN | 0 | 44 | 406000 | Google Maps | 53.404 | -6.1704 | 38 KV | 170.792 | 9.0611 | 321718 | 240858
BOGGERAGH | 0 | 64 | 572000 | Google Maps | 52.0388 | -8.908 | 110 KV | 139.2022 | 230.7254 | 137720 | 87716
BOGHALL ROAD | 32 | 64 | 969000 | Google Maps | 53.1869 | -6.1078 | 38 KV | 175.2319 | 19.203 | 326533 | 216805
BOOLTIAGH | 0 | 64 | 887000 | Google Maps | 52.7754 | -9.2428 | 110 KV | 66.1576 | 210.2723 | 116178 | 170053
BORRISOLEIGH | 0 | 60 | 636000 | Google Maps | 52.7634 | -7.9652 | 38 KV | 77.6917 | 131.6506 | 202400 | 168000
BOTHAR | 0 | 0 | 529000 | Google Maps | 53.1306 | -8.6319 | 38 kV | 18.6388 | 160.801 | 157750 | 209050
BOYLE | 32 | 64 | 047000 | Google Maps | 53.9636 | -8.3005 | 38 KV | 80.6012 | 152.5401 | 180323 | 301620
BRACKLONE | 20 | 56 | 988000 |  |  |  | 110 kV | 5980.1028 | 393.3669
BRAY | 32 | 64 | 002000 | Google Maps | 53.1936 | -6.1279 | 38 KV | 173.8406 | 17.9163 | 325173 | 217514
BREWERY ROAD | 32 | 64 | 773000 | Google Maps | 53.2795 | -6.1986 | 38 KV | 168.6599 | 7.2482 | 320204 | 226955
BRINNY | 0 | 0 | 782000 | Google Maps | 51.7854 | -8.7046 | 38 KV | 166.9035 | 239.921 | 151425 | 59402
BROCK | 0 | 0 | 577000 |  |  |  | 38 kV | 5980.1028 | 393.3669
BRUFF | 32 | 64 | 151000 | Google Maps | 52.5131 | -8.5081 | 38 KV | 87.3148 | 177.4925 | 165557 | 140268
BUCKLEYS CROSS | 0 | 0 | 491000 | Google Maps | 53.1871 | -6.7779 | 38 KV | 130.7612 | 39.0816 | 281745 | 215849
BUNCLODY | 32 | 64 | 470000 | Google Maps | 52.6512 | -6.6192 | 38 KV | 158.3518 | 80.3282 | 293501 | 156404
BUNCRANA | 32 | 64 | 204000 | Google Maps | 55.1304 | -7.4416 | 38 KV | 221.6498 | 214.2217 | 235670 | 431607
BUNDORAN | 32 | 64 | 350000 | Google Maps | 54.4726 | -8.2659 | 38 KV | 135.4595 | 183.1508 | 182810 | 358265
BURNWOOD | 0 | 0 | 744000 | Google Maps | 53.0187 | -7.2982 | 38 KV | 100.3673 | 78.6355 | 247146 | 196642
BUSH | 32 | 64 | 488000 | Google Maps | 54.0083 | -6.1843 | 38 KV | 186.3392 | 74.8079 | 319092 | 308076
BUSHFIELD | 32 | 64 | 478000 | Google Maps | 53.4292 | -7.9024 | 38 KV | 57.5399 | 110.5272 | 206534 | 242098
BUTLERSTOWN | 32 | 12 | 667000 | Google Maps | 52.2286 | -7.1704 | 110 KV | 157.8754 | 138.1865 | 256736 | 108813
BUTTEVANT | 32 | 64 | 024000 | Google Maps | 52.2378 | -8.6642 | 38 KV | 116.6854 | 203.7923 | 154673 | 109714
CABRA | 32 | 64 | 231000 | Google Maps | 53.3726 | -6.3004 | 110 KV | 161.9991 | 5.2203 | 313167 | 237139
CAHERDAVIN | 32 | 64 | 098000 | Google Maps | 52.6692 | -8.6534 | 38 KV | 68.8387 | 177.7396 | 155848 | 157712
CAHIR | 32 | 64 | 668000 | Google Maps | 52.3769 | -7.8987 | 110 KV | 115.7007 | 154.2092 | 206947 | 124990
CAHIRCALLA | 32 | 64 | 186000 | Google Maps | 52.8305 | -8.992 | 38 KV | 53.4883 | 192.2826 | 133188 | 175931
CAHIRCIVEEN | 0 | 0 | 239000 |  |  |  | 38 KV | 5980.1028 | 393.3669
CALLAN | 32 | 64 | 460000 | Google Maps | 52.5389 | -7.3836 | 38 KV | 122.9859 | 117.1355 | 241873 | 143195
CALLEE | 0 | 0 | 589000 | Google Maps | 52.177 | -8.1042 | 38 KV | 130.4663 | 179.9141 | 192920 | 102750
CAMDEN ROW | 32 | 64 | 103000 | Google Maps | 53.3365 | -6.2667 | 38 KV | 164.1233 | 1.2037 | 315514 | 233179
CAPPAMORE | 32 | 64 | 152000 | Google Maps | 52.6089 | -8.3336 | 38 KV | 79.9962 | 161.8424 | 177447 | 150853
CARK | 0 | 0 | 705000 | Google Maps | 54.8814 | -7.8839 | 38 KV | 185.8709 | 202.4333 | 207500 | 403753
CARLISLE | 0 | 0 | 659000 | Google Maps | 53.2057 | -6.1017 | 38 KV | 175.4827 | 17.6306 | 326889 | 218910
CARLOW | 32 | 64 | 669000 | Google Maps | 52.8325 | -6.8445 | 110 KV | 136.0779 | 68.9341 | 277926 | 176318
CARNA | 0 | 0 | 885000 | Google Maps | 53.3234 | -9.8984 | 110 kV | 77.3628 | 243.1645 | 73550 | 232000
CARNDONAGH | 32 | 64 | 266000 | Google Maps | 55.2435 | -7.2763 | 38 KV | 237.3649 | 222.4946 | 246083 | 444293
CARNSORE | 0 | 0 | 642000 | Google Maps | 52.1829 | -6.3641 | 38 KV | 201.3543 | 128.7345 | 311939 | 104660
CAROLINE STREET | 0 | 44 | 313000 | Google Maps | 51.8986 | -8.4694 | 10 KV | 155.3429 | 219.669 | 167736 | 71872
CARRANSTOWN | 0 | 0 | 441000 | Google Maps | 53.678 | -6.3923 | 38 KV | 161.0579 | 39.1006 | 306285 | 270991
CARRAROE | 32 | 64 | 475000 | Google Maps | 53.2788 | -9.5287 | 38 KV | 52.7217 | 218.7416 | 98077 | 226446
CARRICK ON SHANNON | 32 | 64 | 074000 | Google Maps | 53.9378 | -8.1089 | 110 KV | 83.4151 | 140.0257 | 192897 | 298707
CARRICKMACROSS | 32 | 64 | 210000 | Google Maps | 53.9805 | -6.735 | 38 KV | 152.8348 | 78.4811 | 283042 | 304198
CARRICKMINES | 32 | 64 | 649000 | Google Maps | 53.2565 | -6.1951 | 110 KV | 168.9708 | 9.6828 | 320504 | 224397
CARRIGADROHID | 0 | 0 | 783000 | Google Maps | 51.8964 | -8.8614 | 110 KV | 154.7772 | 238.7961 | 140749 | 71872
CARRIGALINE | 32 | 64 | 166000 | Google Maps | 51.8273 | -8.3819 | 38 KV | 163.9812 | 221.6854 | 173719 | 63902
CARRIGALLEN | 32 | 64 | 157000 | Google Maps | 53.9668 | -7.6797 | 38 KV | 102.8429 | 117.7453 | 221071 | 301986
CARRIGCANNON | 0 | 0 | 640000 | Google Maps | 52.0639 | -8.898 | 38 KV | 136.3597 | 228.3765 | 138460 | 90539
CARRIGLAWN | 32 | 64 | 188000 | Google Maps | 52.3426 | -6.4854 | 38 KV | 184.0568 | 111.8601 | 303273 | 122256
CARRIGSHANE | 32 | 64 | 459000 | Google Maps | 51.9094 | -8.1433 | 38 KV | 158.2451 | 204.2412 | 190189 | 72973
CARRIGTHOMAS | 0 | 0 | 507000 | Google Maps | 51.9545 | -8.9126 | 38 KV | 148.5661 | 237.0395 | 137310 | 78377
CARRIGTWOHILL | 32 | 0 | 351000 | Google Maps | 51.897 | -8.248 | 38 KV | 157.948 | 209.8238 | 182980 | 71621
CARROWBEG | 32 | 64 | 699000 | Google Maps | 53.8093 | -9.5062 | 110 KV | 77.2855 | 222.0935 | 100826 | 285452
CARTRONTROY | 0 | 0 | 050000 | Google Maps | 53.4223 | -7.9053 | 38 KV | 57.1542 | 110.6599 | 206343 | 241338
CASHEL | 32 | 64 | 169000 | Google Maps | 52.5099 | -7.8727 | 38 KV | 103.9364 | 142.8658 | 208695 | 139801
CASHLA | 0 | 0 | 784000 | Google Maps | 53.3082 | -8.8537 | 220 KV | 8.2092 | 173.6263 | 143139 | 228964
CASTLEBAR | 0 | 20 | 520000 | Google Maps | 53.8667 | -9.2695 | 110 KV | 73.5373 | 208.4784 | 116531 | 291540
CASTLEBLAYNEY | 32 | 64 | 184000 | Google Maps | 54.1201 | -6.756 | 38 KV | 159.9305 | 93.3505 | 281394 | 319718
CASTLECOMER | 32 | 20 | 144000 | Google Maps | 52.8381 | -7.1922 | 38 KV | 114.5511 | 84.1723 | 254490 | 176618
CASTLEDOCKRILL | 0 | 0 | 568000 |  |  |  | 110 kV | 5980.1028 | 393.3669
CASTLEFARM | 0 | 0 | 597000 | Google Maps | 52.2679 | -8.2812 | 38 KV | 117.29 | 181.5408 | 180849 | 112896
CASTLEFARM 110KV | 0 | 0 | 563000 | Google Maps | 52.6298 | -9.0547 | 110 KV | 76.0572 | 204.2482 | 128635 | 153652
CASTLEISLAND | 32 | 20 | 233000 | Google Maps | 52.2318 | -9.4702 | 38 KV | 127.2428 | 249.7537 | 99601 | 109855
CASTLEKNOCK | 32 | 64 | 154000 | Google Maps | 53.3713 | -6.3775 | 38 KV | 156.8874 | 9.3735 | 308044 | 236876
CASTLELYONS | 32 | 64 | 455000 | Google Maps | 52.084 | -8.2228 | 38 KV | 138.0822 | 193.0195 | 184774 | 92419
CASTLEREA | 32 | 64 | 256000 | Google Maps | 53.7577 | -8.4535 | 38 KV | 55.6377 | 153.4597 | 170134 | 278749
CASTLETOWNBERE | 32 | 64 | 513000 | Google Maps | 51.6572 | -9.8953 | 38 KV | 197.4296 | 310.2941 | 68879 | 46593
CASTLETOWNROCHE | 32 | 64 | 080000 | Google Maps | 52.1619 | -8.4508 | 38 KV | 126.49 | 198.0483 | 169200 | 101156
CASTLETROY | 32 | 64 | 558000 | Google Maps | 52.6764 | -8.5563 | 38 KV | 68.8645 | 171.4799 | 162424 | 158467
CASTLEVIEW | 32 | 64 | 600000 | Google Maps | 51.9007 | -8.3701 | 110 KV | 156.035 | 214.9444 | 174578 | 72063
CATHALEENS FALL | 32 | 12 | 143000 | Google Maps | 54.4987 | -8.1768 | 110 KV | 139.7029 | 180.9968 | 188592 | 361155
CATHALEENS FALL 38 | 0 | 0 | 843000 | Google Maps | 54.4988 | -8.1769 | 38 KV | 139.7154 | 180.9968 | 188592 | 361155
CAUSEWAY | 32 | 64 | 483000 | Google Maps | 52.4085 | -9.7356 | 38 KV | 118.4656 | 256.527 | 81940 | 129920
CAUTEEN | 0 | 64 | 573000 | Google Maps | 52.5375 | -8.1941 | 110 KV | 90.8335 | 158.2164 | 186882 | 142880
CAVAN | 32 | 64 | 059000 | Google Maps | 54.0013 | -7.3528 | 38 KV | 120.9615 | 103.8699 | 242490 | 305971
CELBRIDGE | 32 | 64 | 016000 | Google Maps | 53.3361 | -6.5353 | 38 KV | 146.2872 | 19.1005 | 297619 | 232735
CENTRAL PARK | 32 | 64 | 993000 | Google Maps | 53.2702 | -6.2061 | 110 KV | 168.1908 | 7.9933 | 319733 | 225906
CENTRE PARK ROAD | 0 | 0 | 632000 | Google Maps | 51.898 | -8.4462 | 38 KV | 155.607 | 218.6492 | 169337 | 71787
CHARLESLAND | 0 | 0 | 726000 |  |  |  | 110 kV | 5980.1028 | 393.3669
CHARLESTOWN | 32 | 64 | 078000 | Google Maps | 53.9463 | -8.7811 | 38 KV | 73.4545 | 180.6853 | 148759 | 299934
CHARLEVILLE | 32 | 64 | 456000 | Google Maps | 52.3301 | -8.6939 | 110 KV | 106.3556 | 199.3053 | 152741 | 120008
CHEEVERSTOWN | 0 | 0 | 425000 | Google Maps | 53.2993 | -6.4037 | 38 KV | 154.9982 | 11.1824 | 306463 | 228831
CHERRYWOOD | 32 | 64 | 499000 | Google Maps | 53.2434 | -6.1569 | 110 KV | 171.5732 | 12.1161 | 323093 | 223007
CHURCHTOWN | 32 | 64 | 971000 | Google Maps | 52.4604 | -9.0582 | 38 KV | 94.3468 | 212.7616 | 128124 | 134805
CITYWEST | 32 | 64 | 454000 | Google Maps | 53.2892 | -6.4166 | 110 KV | 154.1528 | 12.4153 | 305642 | 227683
CLADY | 0 | 64 | 438000 | Google Maps | 55.0381 | -8.2718 | 38 KV | 197.1219 | 230.8239 | 182669 | 421222
CLAHANE | 0 | 0 | 023000 | Google Maps | 52.3788 | -9.5482 | 110 KV | 114.7177 | 246.5126 | 94621 | 126327
CLARA | 32 | 64 | 051000 | Google Maps | 53.3444 | -7.5889 | 38 KV | 76.4592 | 89.2818 | 227431 | 232739
CLARECASTLE | 0 | 0 | 453000 | Google Maps | 52.8116 | -8.9643 | 38 KV | 54.9483 | 191.1822 | 135027 | 173795
CLAREGALWAY | 32 | 64 | 251000 | Google Maps | 53.3613 | -8.9241 | 38 KV | 15.0352 | 178.1915 | 138527 | 234938
CLAREMORRIS | 0 | 0 | 041000 | Google Maps | 53.7234 | -8.981 | 38 KV | 51.2406 | 186.2137 | 135291 | 275286
CLARKSTOWN | 32 | 64 | 620000 | Google Maps | 53.4625 | -6.6823 | 38 KV | 137.62 | 32.043 | 287559 | 246607
CLASH (Created to allow 019 series Subs) | 0 | 0 | 019000 |  |  |  | 38 KV | 5980.1028 | 393.3669
CLASHAVOON | 0 | 0 | 931000 | Google Maps | 51.9381 | -8.9141 | 220 KV | 150.3909 | 238.3277 | 137186 | 76555
CLASHMORE | 0 | 0 | 474000 | Google Maps | 52.0038 | -7.8083 | 38 KV | 155.7211 | 182.0688 | 213215 | 83514
CLIFDEN | 32 | 64 | 252000 | Google Maps | 53.4885 | -9.9981 | 38 KV | 86.6824 | 249.8849 | 67422 | 250553
CLIFF | 0 | 0 | 785000 | Google Maps | 54.488 | -8.1036 | 110 KV | 139.8951 | 176.8022 | 193288 | 359899
CLOGHBAN | 0 | 0 | 866000 | Google Maps | 53.4036 | -6.361 | 110 KV | 158.178 | 10.5143 | 309045 | 240502
CLOGHBOOLA | 0 | 64 | 875000 | Google Maps | 52.3305 | -9.4381 | 110 KV | 116.2859 | 242.3925 | 102010 | 120800
CLOGHER | 0 | 0 | 889000 |  |  |  | 110 KV | 5980.1028 | 393.3669
CLONAKILTY | 16 | 20 | 165000 | Google Maps | 51.638 | -8.8948 | 38 KV | 183.5945 | 260.8869 | 138100 | 43148
CLONARD | 32 | 64 | 547000 | Google Maps | 52.3301 | -6.487 | 38 KV | 184.7869 | 113.2585 | 303194 | 120857
CLONDALKIN | 32 | 64 | 072000 | Google Maps | 53.3248 | -6.3947 | 38 KV | 155.6002 | 9.8345 | 307011 | 231685
CLONEE | 0 | 0 | 860000 |  |  |  | 220 KV | 5980.1028 | 393.3669
CLONES | 32 | 64 | 246000 | Google Maps | 54.1787 | -7.2223 | 38 KV | 140.5584 | 113.5615 | 250827 | 325802
CLONKEEN | 0 | 0 | 796000 | Google Maps | 51.9842 | -9.299 | 110 KV | 149.687 | 255.5182 | 110761 | 82064
CLONMINCH | 32 | 64 | 650000 | Google Maps | 53.2556 | -7.4862 | 38 KV | 83.1638 | 83.0245 | 234342 | 222894
CLONROCHE | 32 | 64 | 515000 | Google Maps | 52.4533 | -6.7084 | 38 KV | 164.5995 | 103.1461 | 287860 | 134277
CLONSHAUGH | 32 | 64 | 411000 | Google Maps | 53.403 | -6.2217 | 38 KV | 167.3893 | 7.5261 | 318325 | 240657
CLONTARF | 32 | 64 | 283000 | Google Maps | 53.3693 | -6.1938 | 38 KV | 169.0528 | 5.0986 | 320272 | 236955
CLOON | 32 | 64 | 907000 | Google Maps | 53.4834 | -8.8482 | 110 KV | 23.1572 | 173.6351 | 143739 | 248466
CLOONBANNIN | 32 | 64 | 070000 | Google Maps | 52.129 | -9.0405 | 38 KV | 130.3127 | 231.6167 | 128791 | 97909
CLOONFAUGHNA | 0 | 0 | 543000 | Google Maps | 53.7632 | -8.9072 | 38 kV | 54.2269 | 182.4723 | 140222 | 279650
CLOONLOUGH | 32 | 64 | 369000 | Google Maps | 52.2577 | -8.2773 | 38 KV | 118.4604 | 182.1007 | 181116 | 111755
CLOUGHKEATING | 0 | 0 | 178000 |  |  |  | 38 KV | 5980.1028 | 393.3669
CLOYNE | 32 | 16 | 232000 | Google Maps | 51.8641 | -8.1063 | 38 KV | 163.7544 | 206.7072 | 192731 | 67907
COBH | 32 | 0 | 028000 | Google Maps | 51.855 | -8.2956 | 38 KV | 161.9063 | 215.5232 | 179682 | 66953
COES ROAD | 32 | 64 | 367000 | Google Maps | 53.9996 | -6.382 | 38 KV | 174.2453 | 74.2455 | 306153 | 306797
COLLEGE PARK | 32 | 64 | 670000 | Google Maps | 53.4105 | -6.376 | 110 KV | 157.238 | 11.7548 | 308044 | 241247
COLLIGAN | 32 | 64 | 516000 | Google Maps | 52.0933 | -7.6251 | 38 KV | 152.3112 | 166.7955 | 225747 | 93498
COLLINSTOWN | 32 | 20 | 267000 | Google Maps | 53.4274 | -6.2282 | 38 KV | 167.1462 | 10.1138 | 317827 | 243358
COLLOONEY | 32 | 64 | 117000 | Google Maps | 54.1824 | -8.4839 | 38 KV | 101.0128 | 174.8718 | 168452 | 326039
COLLOPS | 0 | 0 | 591000 | Google Maps | 53.9253 | -6.8278 | 38 kV | 144.5396 | 75.8364 | 277052 | 297946
CONG | 32 | 64 | 590000 | Google Maps | 53.5545 | -9.2672 | 38 KV | 46.1489 | 202.0136 | 116067 | 256790
CONVOY | 32 | 64 | 162000 | Google Maps | 54.8645 | -7.6667 | 38 KV | 188.8419 | 193.6585 | 221452 | 401916
COOKSTOWN | 32 | 64 | 672000 | Google Maps | 53.2932 | -6.3781 | 110 KV | 156.7038 | 9.9334 | 308197 | 228189
COOLCARRON | 32 | 64 | 234000 | Google Maps | 52.129 | -8.2773 | 38 KV | 132.3401 | 192.0043 | 181043 | 97439
COOLCORCORAN | 32 | 64 | 020000 | Google Maps | 52.0809 | -9.5075 | 38 KV | 143.772 | 260.8733 | 96706 | 93118
COOLEA | 0 | 0 | 451000 | Google Maps | 51.9356 | -9.3174 | 38 KV | 155.2384 | 259.7826 | 109440 | 76699
COOLGREANEY ROAD | 0 | 0 | 004000 | Google Maps | 52.798 | -6.1666 | 38 KV | 180.1236 | 60.2861 | 323714 | 173428
COOLMINE | 32 | 64 | 407000 | Google Maps | 53.3826 | -6.4005 | 38 KV | 155.426 | 11.2921 | 306487 | 238100
COOLNABACKY | 0 | 0 | 189000 |  |  |  | 400 KV | 5980.1028 | 393.3669
COOLOCK | 32 | 64 | 277000 | Google Maps | 53.3934 | -6.1957 | 38 KV | 169.0486 | 7.1628 | 320080 | 239627
COOLROE | 32 | 64 | 131000 | Google Maps | 51.886 | -8.6361 | 110 KV | 155.8505 | 228.5547 | 156249 | 70551
COOMAGEARLAGHY | 0 | 0 | 912000 | Google Maps | 51.9384 | -9.3115 | 110 KV | 154.8349 | 259.2667 | 109857 | 77003
COOMATAGGERT | 0 | 64 | 877000 | Google Maps | 51.8736 | -9.3148 | 110 KV | 161.8837 | 263.9589 | 109495 | 69795
COOTEHILL | 0 | 0 | 060000 | Google Maps | 54.0693 | -7.0791 | 38 KV | 139.5902 | 98.2136 | 260341 | 313732
CORBALLY | 32 | 64 | 195000 | Google Maps | 52.6703 | -8.6159 | 38 KV | 68.9622 | 175.4069 | 158381 | 157813
CORDAL | 0 | 64 | 865000 | Google Maps | 52.2299 | -9.2813 | 110 KV | 123.0677 | 238.8615 | 112500 | 109400
CORDERRY | 0 | 64 | 972000 | Google Maps | 54.1987 | -8.1974 | 110 KV | 107.4616 | 160.3255 | 187168 | 327767
CORDUFF | 32 | 64 | 932000 | Google Maps | 53.4195 | -6.365 | 220 KV | 158.041 | 11.978 | 308755 | 242260
CORKAGH | 0 | 0 | 690000 |  |  |  | 110 KV | 5980.1028 | 393.3669
CORKERMORE | 0 | 64 | 419000 | Google Maps | 54.717 | -8.3521 | 38 kV | 161.0552 | 206.3568 | 177355 | 385500
CORRACLASSY | 0 | 0 | 812000 | Google Maps | 54.1527 | -7.7446 | 110 KV | 116.3415 | 134.0878 | 216734 | 322660
CORRAWARRIN | 0 | 0 | 037000 | Google Maps | 52.8565 | -8.9657 | 38 KV | 50.1938 | 189.703 | 135005 | 178807
COURTLOUGH | 0 | 44 |  | Google Maps | 53.5644 | -6.2076 | 110 KV | 170.3345 | 25.4127 | 318796 | 258633
COW CROSS | 32 | 64 | 908000 | Google Maps | 51.8651 | -8.3013 | 110 KV | 160.724 | 214.8966 | 179296 | 68086
CRANE | 32 | 64 | 886000 | Google Maps | 52.5325 | -6.5143 | 110 KV | 170.9196 | 91.3541 | 300869 | 143336
CRANMORE | 32 | 64 | 046000 | Google Maps | 54.2681 | -8.4621 | 38 KV | 110.6495 | 178.8831 | 169943 | 335572
CRANNY | 32 | 64 | 582000 | Google Maps | 52.6898 | -9.231 | 38 KV | 74.1459 | 212.7386 | 116812 | 160518
CRATLOE | 32 | 64 | 273000 | Google Maps | 52.6921 | -8.771 | 38 KV | 66.107 | 183.9142 | 147890 | 160341
CREAGH | 32 | 64 | 519000 | Google Maps | 53.3351 | -8.1979 | 38 KV | 36.1458 | 129.8704 | 186851 | 231662
CREESLOUGH | 32 | 64 | 258000 | Google Maps | 55.1243 | -7.9139 | 38 KV | 211.2513 | 226.6214 | 205544 | 430788
CREGG ROAD | 32 | 64 | 181000 | Google Maps | 52.3524 | -7.4069 | 38 KV | 136.9511 | 134.5629 | 240465 | 122429
CROCKAHENNY | 0 | 0 | 731000 | Google Maps | 55.1435 | -7.2824 | 38 KV | 227.097 | 212.0558 | 245808 | 433157
CROMCASTLE | 0 | 0 | 994000 | Google Maps | 53.4002 | -6.2165 | 110 KV | 167.7145 | 7.3183 | 318678 | 240355
CRORY | 0 | 64 | 473000 | Google Maps | 52.5792 | -6.5358 | 110 KV | 167.0863 | 86.5644 | 299303 | 148510
CROSSANA | 0 | 0 | 612000 |  |  |  | 38 KV | 5980.1028 | 393.3669
CROSSLEA | 0 | 0 | 755000 | Google Maps | 51.8761 | -9.2567 |  | 160.7 | 260.6898 | 113502 | 70011
CROSSMOLINA | 96 | 64 | 220000 | Google Maps | 54.1092 | -9.3248 | 38 KV | 99.3883 | 220.4792 | 113398 | 318599
CROUGHMARKE | 0 | 0 | 751000 | Google Maps | 52.6391 | -8.051 | 38 KV | 85.3312 | 143.8439 | 196594 | 154167
CRUMLIN | 32 | 64 | 259000 | Google Maps | 53.3255 | -6.3159 | 38 KV | 160.8354 | 4.6735 | 312261 | 231878
CULLENAGH | 0 | 0 | 933000 | Google Maps | 52.2495 | -7.2802 | 220 KV | 151.2537 | 139.6449 | 249212 | 111058
CULLION | 32 | 64 | 099000 | Google Maps | 54.9337 | -7.7098 | 38 KV | 195.0094 | 201.7343 | 218653 | 409605
CUNGHILL | 0 | 0 | 934000 | Google Maps | 54.1112 | -8.6493 | 110 KV | 91.907 | 180.3555 | 157586 | 318202
CURRA | 32 | 64 | 528000 | Google Maps | 53.1215 | -8.4387 | 38 KV | 26.9598 | 148.2282 | 170669 | 207942
CURRABWEE | 0 | 0 | 702000 | Google Maps | 51.6763 | -9.1145 | 38 KV | 180.8455 | 268.3645 | 122959 | 47619
CURRAGLASS | 32 | 64 | 586000 | Google Maps | 52.0933 | -8.0725 | 38 KV | 139.9779 | 185.3619 | 195078 | 93433
CURRALEIGH | 32 | 20 | 450000 | Google Maps | 51.9065 | -8.6703 | 38 KV | 153.4813 | 228.5827 | 153897 | 72864
CUSHALING | 0 | 0 | 813000 | Google Maps | 53.2894 | -7.0846 | 110 KV | 109.7577 | 55.9749 | 261100 | 226934
DALKEY | 0 | 0 | 664000 | Google Maps | 53.2751 | -6.1014 | 38 KV | 175.1339 | 12.017 | 326701 | 226627
DALLIGAN | 0 | 0 | 753000 |  |  |  | 38 kV | 5980.1028 | 393.3669
DALLOW | 32 | 64 | 673000 | Google Maps | 53.1259 | -7.9282 | 110 KV | 56.6627 | 114.6059 | 204857 | 208342
DALTON | 32 | 64 | 909000 | Google Maps | 53.7201 | -8.9816 | 110 KV | 50.9021 | 186.1708 | 135250 | 274917
DARDISTOWN | 0 | 0 | 820000 | Google Maps | 53.4211 | -6.2338 | 110 KV | 166.7207 | 9.3717 | 317469 | 242647
DEANSGRANGE | 32 | 64 | 001000 | Google Maps | 53.2765 | -6.1615 | 38 KV | 171.1359 | 8.9271 | 322689 | 226676
DEERPARK | 32 | 20 | 033000 | Google Maps | 52.3529 | -7.4222 | 38 KV | 136.2389 | 135.1178 | 239421 | 122477
DELVIN | 96 | 12 | 123000 | Google Maps | 53.597 | -7.0716 | 38 KV | 115.5078 | 61.8318 | 261517 | 261177
DENNEHYS CROSS | 32 | 64 | 311000 | Google Maps | 51.8887 | -8.5044 | 38 KV | 156.1834 | 222.1053 | 165324 | 70786
DEREEN | 0 | 0 | 449000 | Google Maps | 51.8759 | -9.144 | 38 KV | 159.228 | 254.7826 | 121263 | 69861
DERRYBEG | 32 | 64 | 399000 | Google Maps | 55.0631 | -8.2839 | 38 KV | 199.7539 | 233.5397 | 181906 | 424011
DERRYBRIEN | 0 | 0 | 986000 |  |  |  | 110 KV | 5980.1028 | 393.3669
DERRYCRAMPH | 32 | 64 | 545000 | Google Maps | 53.9793 | -7.3833 | 38 KV | 117.8548 | 103.6039 | 240511 | 303501
DERRYFRENCH | 0 | 0 | 996000 | Google Maps | 53.1667 | -8.3864 | 110 KV | 26.791 | 143.9486 | 174209 | 212950
DERRYIRON | 0 | 52 | 724000 | Google Maps | 53.3592 | -7.2133 | 110 KV | 101.4438 | 64.3319 | 252390 | 234489
DERRYULK | 0 | 0 | 380000 | Google Maps | 52.9319 | -8.7611 | 38 kV | 39.4403 | 174.1063 | 148870 | 187020
DINGLE | 32 | 64 | 426000 | Google Maps | 52.148 | -10.2578 | 38 KV | 162.8706 | 301.3562 | 45503 | 101922
DOCK ROAD | 32 | 8 | 635000 | Google Maps | 52.6551 | -8.6584 | 38 KV | 70.3761 | 178.7323 | 155492 | 156146
DODDER ROAD | 32 | 64 | 330000 | Google Maps | 53.304 | -6.2675 | 38 KV | 164.0427 | 3.9184 | 315542 | 229566
DONEGAL | 32 | 64 | 149000 | Google Maps | 54.6578 | -8.0901 | 38 KV | 158.2451 | 190.2266 | 194231 | 378856
DONNYBROOK | 32 | 64 | 308000 | Google Maps | 53.3201 | -6.2323 | 38 KV | 166.3831 | 2.2046 | 317846 | 231416
DONORE ROAD | 12 | 44 |  | Google Maps | 53.4132 | -6.2505 | 110 KV | 165.5534 | 8.4452 | 316363 | 241744
DOOCHARN | 0 | 0 | 578000 | Google Maps | 54.1907 | -6.7005 | 38 kV | 167.4175 | 99.5593 | 284875 | 327638
DOON | 32 | 64 | 674000 | Google Maps | 52.3836 | -7.6677 | 110 KV | 123.3758 | 142.8418 | 222676 | 125783
DORNEY | 0 | 0 | 580000 | Google Maps | 52.3275 | -9.5759 | 38 kV | 120.6431 | 250.8212 | 92609 | 120658
DOUGLAS | 32 | 64 | 281000 | Google Maps | 51.8785 | -8.4366 | 38 KV | 157.8316 | 219.8223 | 169982 | 69622
DOWNES | 0 | 0 | 403000 |  |  |  | 110 KV | 5980.1028 | 393.3669
DROMADA | 0 | 0 | 692000 | Google Maps | 52.4436 | -9.2344 | 110 KV | 99.4989 | 224.2226 | 116113 | 133125
DROMBEG | 0 | 64 | 855000 | Google Maps | 52.4879 | -9.4801 | 110 KV | 101.8569 | 237.0285 | 99520 | 138382
DROMDEEVEEN | 0 | 0 | 440000 | Google Maps | 52.3274 | -9.0304 | 38 KV | 108.4438 | 218.5843 | 129799 | 119979
DROMTHACKER | 0 | 56 |  | Google Maps | 52.2883 | -9.6661 | 38 KV | 127.3911 | 258.2832 | 86375 | 116449
DRUMBEAR | 32 | 16 | 156000 | Google Maps | 54.2312 | -6.969 | 38 KV | 156.6079 | 110.2494 | 267282 | 331854
DRUMCONDRA | 32 | 64 | 344000 | Google Maps | 53.363 | -6.2604 | 38 KV | 164.6129 | 2.9596 | 315858 | 236140
DRUMDOWNEY | 0 | 0 | 155000 |  |  |  | 38 KV | 5980.1028 | 393.3669
DRUMKEEN | 0 | 0 | 725000 | Google Maps | 54.8714 | -7.7567 | 110 KV | 187.4667 | 197.1991 | 215671 | 402653
DRUMLINE | 32 | 64 | 629000 | Google Maps | 52.724 | -8.8615 | 110 KV | 63.081 | 188.1137 | 141844 | 163964
DRUMLOUGH HILL | 0 | 0 | 706000 | Google Maps | 55.1991 | -7.4438 | 38 KV | 228.6536 | 221.3922 | 235466 | 439252
DRUMQUIN | 32 | 64 | 214000 | Google Maps | 52.7595 | -9.0368 | 38 KV | 61.9334 | 197.7273 | 130055 | 168071
DRYBRIDGE | 32 | 64 | 064000 | Google Maps | 53.725 | -6.4006 | 110 KV | 161.9421 | 44.3139 | 305618 | 276209
DRYNAM | 0 | 0 | 926000 | Google Maps | 53.4516 | -6.2177 | 110 KV | 168.0589 | 12.8801 | 318451 | 246068
DUBLIN AIRPORT | 0 | 0 | 707000 | Google Maps | 53.4266 | -6.2425 | 38 KV | 166.1907 | 9.9473 | 316874 | 243252
DULEEK | 32 | 64 | 546000 | Google Maps | 53.6603 | -6.4278 | 38 KV | 158.3052 | 37.8687 | 303987 | 268973
DUN LAOGHAIRE | 32 | 64 | 284000 | Google Maps | 53.2934 | -6.1414 | 38 KV | 172.4342 | 8.664 | 323979 | 228590
DUNDALK | 32 | 64 | 062000 | Google Maps | 54.0053 | -6.4237 | 110 KV | 172.0867 | 75.2554 | 303401 | 307375
DUNDERROW | 0 | 0 | 594000 | Google Maps | 51.7274 | -8.5807 | 38 KV | 173.6583 | 239.0342 | 159928 | 52872
DUNDRUM | 32 | 64 | 134000 | Google Maps | 53.2924 | -6.2444 | 38 KV | 165.5938 | 5.0115 | 317117 | 228311
DUNFIRTH | 32 | 8 | 771000 | Google Maps | 53.3883 | -6.8291 | 38 KV | 127.0963 | 39.0631 | 277954 | 238187
DUNGARVAN | 32 | 16 | 675000 | Google Maps | 52.1082 | -7.6537 | 110 KV | 149.9123 | 166.5072 | 223774 | 95149
DUNGLOE | 32 | 64 | 340000 | Google Maps | 54.9505 | -8.3465 | 38 KV | 186.7875 | 225.9073 | 177846 | 411493
DUNLAVIN | 0 | 0 | 974000 | Google Maps | 53.0593 | -6.7121 | 38 KV | 137.2175 | 43.7915 | 286400 | 201700
DUNLEER | 32 | 64 | 237000 | Google Maps | 53.8403 | -6.3918 | 38 KV | 166.5968 | 56.7821 | 305908 | 289051
DUNMANWAY | 32 | 64 | 676000 | Google Maps | 51.7234 | -9.0896 | 110 KV | 175.4263 | 263.4706 | 124760 | 52830
DUNMOYLAN | 0 | 0 | 392000 | Google Maps | 52.541 | -9.0699 | 38 KV | 85.8463 | 209.3583 | 127458 | 143784
DUNSINK | 0 | 44 | 960000 | Google Maps | 53.3887 | -6.3404 | 110 KV | 159.4411 | 8.3612 | 310469 | 238869
DUNSTOWN | 0 | 0 | 787000 | Google Maps | 53.1542 | -6.6876 | 400 KV | 137.1459 | 35.6969 | 287849 | 212300
EAST ATHLONE | 0 | 44 | 897000 | Google Maps | 53.4162 | -7.9099 | 110 KV | 56.6847 | 110.9176 | 206037 | 240653
EAST GALWAY | 0 | 44 |  | Google Maps | 53.2716 | -8.729 | 110 KV | 1.6891 | 165.5103 | 151419 | 224809
EAST WALL ROAD | 32 | 64 | 112000 | Google Maps | 53.3532 | -6.2257 | 38 KV | 166.8823 | 2.3304 | 318196 | 235102
EASTMONT | 0 | 44 |  | Google Maps | 51.8985 | -8.3667 | 110 KV | 156.3133 | 214.9579 | 174812 | 71839
EDENDERRY | 32 | 64 | 203000 | Google Maps | 53.3468 | -7.0191 | 38 KV | 114.2305 | 51.333 | 265378 | 233373
EDGEWORTHSTOWN | 32 | 64 | 130000 | Google Maps | 53.7038 | -7.6137 | 38 KV | 87.5439 | 99.3081 | 225561 | 272724
EMYVALE | 32 | 64 | 502000 | Google Maps | 54.3457 | -7.0297 | 38 KV | 162.5388 | 123.4586 | 263152 | 344542
ENNIS | 32 | 8 | 677000 | Google Maps | 52.8602 | -8.9359 | 110 KV | 49.2271 | 187.6719 | 137014 | 179179
ENNIS NORTH | 32 | 64 | 413000 | Google Maps | 52.863 | -8.9838 | 38 KV | 49.8974 | 190.6617 | 133789 | 179534
ENNISCRONE | 32 | 64 | 492000 | Google Maps | 54.2129 | -9.0782 | 38 KV | 105.4668 | 210.4626 | 129704 | 329861
ENNISKEANE | 32 | 64 | 090000 | Google Maps | 51.7387 | -8.9315 | 38 KV | 172.5947 | 254.5012 | 135716 | 54388
ENNISTYMON | 32 | 20 | 158000 | Google Maps | 52.9303 | -9.2907 | 38 KV | 54.2052 | 208.5791 | 113256 | 187357
ERRIGAL | 32 | 64 | 517000 | Google Maps | 54.0667 | -7.0957 | 38 KV | 138.5588 | 98.5963 | 259252 | 313429
ESK | 0 | 0 | 639000 |  |  |  | 38 kV | 5980.1028 | 393.3669
FACTORY CROSS | 32 | 64 | 370000 | Google Maps | 51.8233 | -8.3377 | 38 KV | 164.883 | 220.0905 | 176762 | 63441
FAIRHILL | 32 | 64 | 486000 | Google Maps | 51.9055 | -8.4787 | 38 KV | 154.5139 | 219.5376 | 167102 | 72639
FAIRVIEW | 32 | 64 | 113000 | Google Maps | 53.3645 | -6.2288 | 38 KV | 166.7149 | 3.2979 | 317958 | 236359
FASSAROE | 32 | 64 | 678000 | Google Maps | 53.1989 | -6.1547 | 110 KV | 172.0182 | 16.6446 | 323369 | 218051
FERMOY | 0 | 44 |  | Google Maps | 52.148 | -8.2608 | 110 KV | 130.5461 | 189.6808 | 182199 | 99570
FERMOY NORTH | 32 | 64 | 562000 | Google Maps | 52.1464 | -8.2857 | 38 KV | 130.3201 | 190.9636 | 180507 | 99457
FERNS | 32 | 64 | 075000 | Google Maps | 52.5913 | -6.5029 | 38 KV | 168.3983 | 84.7824 | 301507 | 149898
FIDDANDARRY | 0 | 0 | 490000 |  |  |  | 38 KV | 5980.1028 | 393.3669
FINAWN | 0 | 0 | 467000 |  |  |  | 38 KV | 5980.1028 | 393.3669
FINGLAS | 32 | 64 | 318000 | Google Maps | 53.4057 | -6.3143 | 110 KV | 161.2809 | 8.7733 | 312159 | 240806
FINISKLIN | 32 | 64 | 511000 | Google Maps | 54.2784 | -8.4957 | 38 KV | 111.4438 | 181.3385 | 167759 | 336732
FINNEA | 32 | 64 | 587000 | Google Maps | 53.7949 | -7.4069 | 38 KV | 104.4426 | 92.1098 | 239132 | 282962
FINNSTOWN | 0 | 0 | 991000 |  |  |  | 220 kV | 5980.1028 | 393.3669
FISHERSTOWN | 0 | 0 | 480000 | Google Maps | 53.7495 | -7.906 | 38 KV | 75.2497 | 119.0694 | 206248 | 277752
FLAGFORD | 0 | 0 | 788000 | Google Maps | 53.9117 | -8.1237 | 220 KV | 80.4221 | 139.57 | 191918 | 295808
FLAXFORT | 0 | 0 | 477000 | Google Maps | 51.8956 | -8.3647 | 38 KV | 156.6512 | 215.1301 | 174943 | 71495
FOILDARG | 0 | 0 | 764000 | Google Maps | 52.6017 | -8.1656 |  | 85.1698 | 152.6181 | 188826 | 150013
FOREST | 0 | 0 | 579000 | Google Maps | 51.9556 | -8.2962 | 38 kV | 150.908 | 207 | 179688 | 78149
FORTUNESTOWN | 32 | 64 | 892000 | Google Maps | 53.283 | -6.4172 | 110 KV | 154.1229 | 12.7668 | 305616 | 226990
FOSTERSTOWN | 0 | 44 | 893000 | Google Maps | 53.5259 | -6.8219 | 110 KV | 129.6335 | 43.5116 | 278173 | 253507
FOXFORD | 0 | 0 | 044000 | Google Maps | 53.9842 | -9.1029 | 38 KV | 81.2889 | 201.9387 | 127709 | 304422
FOXHOLE | 32 | 64 | 621000 | Google Maps | 51.9712 | -7.8673 | 38 KV | 157.5393 | 187.3904 | 209168 | 79847
FOYNES | 32 | 64 | 314000 | Google Maps | 52.6007 | -9.0963 | 38 KV | 79.9622 | 208.1421 | 125766 | 150462
FRANCIS STREET | 32 | 64 | 733000 | Google Maps | 53.3415 | -6.2758 | 110 KV | 163.5269 | 1.8655 | 314892 | 233720
FREAGH | 0 | 0 | 643000 | Google Maps | 52.7272 | -8.4107 | 110 kV | 65.8577 | 160.1591 | 172300 | 164050
GALMOY | 0 | 0 | 598000 | Google Maps | 52.8082 | -7.5961 | 38 KV | 92.8914 | 107.8219 | 227288 | 173064
GALWAY | 32 | 64 | 679000 | Google Maps | 53.2901 | -9.0128 | 110 KV | 18.422 | 184.3109 | 132505 | 227089
GARDEN CITY | 0 | 0 | 005000 | Google Maps | 52.6786 | -6.2894 | 38 KV | 177.1557 | 73.3783 | 315747 | 159934
GARISTOWN | 0 | 0 | 420000 | Google Maps | 53.6954 | -6.9039 | 38 kV | 129.4394 | 58.9746 | 272450 | 272280
GARRACUMMER | 0 | 0 | 575000 |  |  |  | 38 kV | 5980.1028 | 393.3669
GARRANACANTY | 32 | 64 | 036000 | Google Maps | 52.483 | -8.1465 | 38 KV | 97.6804 | 159.1976 | 190098 | 136802
GARRIGERY | 0 | 0 | 447000 | Google Maps | 51.8917 | -9.3087 |  | 159.8276 | 262.3585 | 109954 | 71802
GARROW | 0 | 64 | 992000 | Google Maps | 52.0025 | -9.1316 | 110 KV | 145.2266 | 245.1411 | 122340 | 83927
GARRYCASTLE | 32 | 64 | 976000 | Google Maps | 53.4211 | -7.895 | 38 KV | 57.7805 | 109.9648 | 207030 | 241201
GARRYOWEN | 32 | 64 | 067000 | Google Maps | 52.6611 | -8.6137 | 38 KV | 69.9938 | 175.7209 | 158524 | 156790
GARRYSPILLANE | 32 | 64 | 292000 | Google Maps | 52.4031 | -8.3876 | 38 KV | 100.9451 | 177.6241 | 173692 | 127969
GARTNANEANE | 0 | 0 | 916000 | Google Maps | 53.945 | -6.9353 | 38 KV | 139.5263 | 81.4748 | 269960 | 300033
GARVAGH | 0 | 64 | 570000 | Google Maps | 54.1505 | -8.1927 | 110 KV | 102.5268 | 156.9818 | 187459 | 322397
GARVILLE AVENUE | 32 | 64 | 230000 | Google Maps | 53.3159 | -6.2782 | 38 KV | 163.333 | 3.0944 | 314799 | 230873
GILLOGUE | 32 | 64 | 458000 | Google Maps | 52.6863 | -8.5836 | 38 KV | 67.483 | 172.6605 | 160574 | 159598
GILRA | 0 | 0 | 935000 | Google Maps | 53.9148 | -7.9853 | 110 KV | 85.6517 | 131.657 | 201016 | 296141
GLANAGOW | 0 | 0 | 740000 | Google Maps | 51.8154 | -8.2494 | 220 KV | 166.826 | 216.9833 | 182849 | 62535
GLANLEE | 0 | 0 | 671000 | Google Maps | 51.9254 | -9.3071 | 110 KV | 156.1659 | 259.9304 | 110128 | 75549
GLANTA COMMONS | 0 | 0 | 739000 | Google Maps | 51.6319 | -9.3796 | 38 KV | 189.0598 | 285.0322 | 104527 | 42987
GLASMORE | 32 | 64 | 322000 | Google Maps | 53.4678 | -6.2382 | 110 KV | 166.8902 | 14.542 | 317050 | 247844
GLASNEVIN | 32 | 64 | 114000 | Google Maps | 53.3689 | -6.2724 | 38 KV | 163.8433 | 3.8492 | 315045 | 236776
GLEBE | 32 | 64 | 416000 | Google Maps | 53.7344 | -7.7851 | 38 KV | 80.2199 | 111.0492 | 214234 | 276089
GLENAMADDY | 32 | 64 | 526000 | Google Maps | 53.6056 | -8.574 | 38 KV | 37.0922 | 157.2795 | 162050 | 261886
GLENGARRIFF | 32 | 64 | 384000 | Google Maps | 51.7582 | -9.5209 | 38 KV | 178.017 | 283.0909 | 95032 | 57241
GLENGOOLE | 64 | 64 | 207000 | Google Maps | 52.6166 | -7.6432 | 38 KV | 104.4169 | 123.3351 | 224219 | 151717
GLENLARA | 32 | 64 | 936000 | Google Maps | 52.2054 | -9.0239 | 110 KV | 121.7428 | 225.718 | 130049 | 106397
GLENMORE | 0 | 0 | 651000 | Google Maps | 52.3853 | -9.1524 | 38 KV | 104.0135 | 222.4216 | 121583 | 126552
GLENREE | 0 | 64 | 894000 | Google Maps | 54.1068 | -8.9893 | 110 KV | 92.7549 | 200.1585 | 135340 | 317970
GLENTIES | 32 | 64 | 216000 | Google Maps | 54.7783 | -8.3171 | 38 KV | 168.1409 | 209.9262 | 179644 | 392308
GLOUCESTER PLACE | 32 | 64 | 115000 | Google Maps | 53.3544 | -6.2548 | 38 KV | 164.9562 | 1.9411 | 316256 | 235193
GNEEVES | 0 | 0 | 379000 | Google Maps | 52.0143 | -9.1203 | 38 KV | 143.7934 | 243.717 | 123134 | 85232
GOLAGH | 0 | 0 | 789000 | Google Maps | 54.6872 | -7.9351 | 110 KV | 164.3377 | 186.5479 | 204232 | 382130
GORESBRIDGE | 32 | 20 | 247000 | Google Maps | 52.6344 | -7.0152 | 38 KV | 136.1347 | 93.6624 | 266722 | 154099
GORMAN | 0 | 0 | 937000 | Google Maps | 53.7011 | -6.646 | 220 KV | 145.7245 | 48.3137 | 289472 | 273209
GORT | 32 | 64 | 038000 | Google Maps | 53.07 | -8.8262 | 38 KV | 24.7962 | 174.7921 | 144667 | 202433
GORTAWEE | 32 | 64 | 815000 | Google Maps | 54.1291 | -7.5813 | 110 KV | 120.647 | 124.5074 | 227421 | 320078
GORTEEN | 0 | 0 | 045000 | Google Maps | 53.9928 | -8.5146 | 38 KV | 79.9071 | 166.6036 | 166299 | 304951
GORTLEE | 32 | 64 | 646000 | Google Maps | 54.9669 | -7.7207 | 38 KV | 198.236 | 205.3156 | 217937 | 413301
GORTNAGROSS | 0 | 0 | 509000 | Google Maps | 52.4521 | -9.3073 | 38 kV | 100.3757 | 228.2034 | 111172 | 134157
GORTYLOUGHLIN | 0 | 0 | 544000 | Google Maps | 53.3207 | -9.2318 | 38 kV | 33.184 | 198.7677 | 117960 | 230726
GRAIGUE | 32 | 64 | 012000 | Google Maps | 52.8369 | -6.9439 | 38 KV | 129.7416 | 72.6129 | 271224 | 176706
GRAIGUENAMANAGH | 32 | 64 | 382000 | Google Maps | 52.5393 | -6.9679 | 38 KV | 144.7376 | 101.142 | 270076 | 143557
GRANAGH | 32 | 64 | 226000 | Google Maps | 52.2793 | -7.1703 | 38 KV | 153.6856 | 133.1531 | 256678 | 114454
GRANBY ROW | 32 | 64 | 102000 | Google Maps | 53.352 | -6.2654 | 38 KV | 164.2435 | 1.9747 | 315555 | 234907
GRANGE (DR) | 32 | 64 | 087000 | Google Maps | 53.3994 | -6.1521 | 110 KV | 171.9709 | 9.4372 | 322962 | 240376
GRANGE (SR) | 32 | 64 | 191000 | Google Maps | 52.2437 | -7.098 | 38 KV | 159.937 | 134.5285 | 261669 | 110553
GRANGE CASTLE | 32 | 64 | 734000 | Google Maps | 53.33 | -6.4453 | 110 KV | 152.2511 | 13.1284 | 303631 | 232180
GREAT CONNELL | 0 | 0 | 938000 |  |  |  | 110 kV | 5980.1028 | 393.3669
GREAT ISLAND | 32 | 16 | 680000 | Google Maps | 52.2796 | -6.9933 | 220 KV | 162.0461 | 127.7433 | 268866 | 114861
GREENHILLS | 32 | 64 | 290000 | Google Maps | 53.3136 | -6.3282 | 38 KV | 160.0129 | 5.9217 | 311475 | 230540
GREYGROVE | 0 | 0 | 339000 | Google Maps | 52.7527 | -9.2744 | 38 KV | 69.4089 | 213.1019 | 114001 | 167571
GREYSTONES | 32 | 64 | 071000 | Google Maps | 53.145 | -6.0857 | 38 KV | 177.1361 | 24.013 | 328134 | 212184
GRIFFINRATH | 32 | 64 | 681000 | Google Maps | 53.3436 | -6.5645 | 110 KV | 144.3732 | 21.0521 | 295660 | 233526
GURRANEBANE | 32 | 64 | 377000 | Google Maps | 51.9353 | -10.2319 | 38 KV | 181.0157 | 311.5172 | 46550 | 78206
NEW GURRANEBANE | 0 | 44 |  |  | 51.9353 | -10.2319 | 38 KV | 181.0162 | 311.5172 | 46550 | 78206
GURTEEN | 32 | 64 |  | Google Maps | 53.9928 | -8.5147 | 38 KV | 79.9029 | 166.6016 | 166297 | 304942
GWEEDORE | 32 | 64 | 192000 | Google Maps | 55.0433 | -8.196 | 38 KV | 198.5096 | 228.508 | 187518 | 421787
HARBOUR | 0 | 0 | 735000 | Google Maps | 53.2957 | -6.1372 | 38 KV | 172.716 | 8.7608 | 324258 | 228857
HAROLDS CROSS | 32 | 64 | 343000 | Google Maps | 53.329 | -6.2753 | 110 KV | 163.535 | 2.0096 | 314956 | 232327
HARTNETTS CROSS | 24 | 64 | 939000 | Google Maps | 51.8935 | -8.9458 | 110 KV | 155.5135 | 243.2744 | 134939 | 71623
HAULBOWLINE | 0 | 0 | 940000 | Google Maps | 51.8401 | -8.3034 | 110 KV | 163.4409 | 217.1456 | 179141 | 65298
HAZELWOOD | 0 | 0 | 409000 | Google Maps | 54.253 | -8.4352 | 38 KV | 109.2976 | 176.4889 | 171682 | 333879
HEADFORD | 0 | 60 | 527000 | Google Maps | 53.4888 | -9.1078 | 38 KV | 33.4082 | 190.5394 | 126844 | 249299
HEADFORD ROAD | 32 | 64 | 262000 | Google Maps | 53.2788 | -9.0485 | 38 KV | 20.8069 | 186.7502 | 130109 | 225868
HERNSBROOK | 0 | 0 | 523000 | Google Maps | 52.3406 | -9.0419 | 38 KV | 107.151 | 218.4795 | 129034 | 121455
HEUSTON SQUARE | 32 | 64 | 504000 | Google Maps | 53.3452 | -6.2999 | 110 KV | 161.9348 | 3.5398 | 313260 | 234094
HOLLY HILL | 0 | 0 | 574000 | Google Maps | 51.9076 | -8.5124 | 38 KV | 154.0438 | 220.9436 | 164784 | 72887
HOLYCROSS ROAD | 32 | 4 | 328000 | Google Maps | 52.6717 | -7.8355 | 38 KV | 91.1216 | 129.7588 | 211180 | 157804
HOLYROOD PARK | 0 | 0 | 555000 | Google Maps | 53.3291 | -6.2224 | 38 KV | 167.048 | 1.974 | 318480 | 232430
HOWTH JUNCTION | 32 | 64 | 334000 | Google Maps | 53.3888 | -6.1513 | 38 KV | 171.9643 | 8.6522 | 323047 | 239198
HUNTSTOWN | 0 | 0 | 919000 | Google Maps | 53.4125 | -6.3263 | 220 KV | 160.5405 | 9.8362 | 311344 | 241549
IIG | 0 | 0 | 968000 | Google Maps | 53.3268 | -6.3502 | 38 KV | 158.5578 | 6.8711 | 309971 | 231970
IKERRIN | 32 | 20 | 682000 | Google Maps | 52.9185 | -7.7712 | 110 KV | 76.2761 | 112.081 | 215437 | 185288
INCH | 32 | 64 | 243000 | Google Maps | 52.1773 | -9.9816 | 38 KV | 149.135 | 283.1416 | 64500 | 104625
INCHERA | 0 | 0 | 533000 | Google Maps | 51.9012 | -8.3705 | 38 KV | 155.9742 | 214.9215 | 174548 | 72120
INCHICORE | 32 | 64 | 964000 | Google Maps | 53.3338 | -6.3387 | 110 KV | 159.337 | 6.0111 | 310724 | 232768
INCHICORE CENTRAL | 0 | 0 | 081000 | Google Maps | 53.3338 | -6.3387 | 110 KV | 159.3376 | 6.0111 | 310724 | 232768
INCHICORE NORTH | 0 | 0 | 083000 | Google Maps | 53.3338 | -6.3387 | 38 KV | 159.3377 | 6.0111 | 310724 | 232768
INCHINASHING | 0 | 0 | 518000 | Google Maps | 51.8797 | -8.9486 | 38 KV | 157.0574 | 244.4554 | 134723 | 70092
INNISCARRA | 0 | 0 | 915000 | Google Maps | 51.9016 | -8.6613 | 110 KV | 154.0538 | 228.525 | 154535 | 72301
IRISHTOWN | 0 | 0 | 941000 | Google Maps | 53.3401 | -6.202 | 220 KV | 168.4239 | 3.1243 | 319812 | 233687
ISLAND | 0 | 0 | 493000 | Google Maps | 52.4369 | -9.4884 | 38 KV | 107.1041 | 239.9827 | 98830 | 132710
JENKINSTOWN | 32 | 64 | 264000 | Google Maps | 54.0173 | -6.2986 | 38 KV | 180.0041 | 75.7677 | 311569 | 308899
JOHNSTOWN | 32 | 64 | 506000 | Google Maps | 53.2313 | -6.6204 | 38 KV | 140.8367 | 27.4626 | 292178 | 220964
JULIANSTOWN | 32 | 64 | 312000 | Google Maps | 53.6451 | -6.3123 | 38 KV | 165.2992 | 34.5167 | 311659 | 267451
KANTURK | 12 | 4 | 119000 | Google Maps | 52.1545 | -8.9045 | 38 KV | 126.3545 | 222.4644 | 138141 | 100629
KEALKILL | 0 | 0 | 079000 | Google Maps | 51.8048 | -9.3218 | 38 KV | 169.4272 | 269.2354 | 108876 | 62156
KEELNAGORE | 0 | 0 | 393000 | Google Maps | 51.936 | -10.0945 | 38 KV | 175.9451 | 303.4636 | 56000 | 78000
KEENAHONE | 0 | 0 | 299000 |  |  |  | 38 KV | 5980.1028 | 393.3669
KELLIS | 0 | 0 | 790000 | Google Maps | 52.7891 | -6.8166 | 220 KV | 139.7104 | 71.9333 | 279885 | 171514
KELLS | 32 | 64 | 180000 | Google Maps | 53.7243 | -6.8641 | 38 KV | 133.0104 | 59.3381 | 275028 | 275538
KENMARE | 32 | 64 | 414000 | Google Maps | 51.8908 | -9.5747 | 38 KV | 165.1951 | 276.8673 | 91641 | 72064
KENTSTOWN | 0 | 0 | 745000 |  |  |  | 110 kV | 5980.1028 | 393.3669
KILBARRY | 64 | 64 | 021000 | Google Maps | 51.9207 | -8.4757 | 110 KV | 152.8532 | 218.0321 | 167287 | 74528
KILCAR | 32 | 64 | 501000 | Google Maps | 54.6478 | -8.5858 | 38 KV | 151.7094 | 211.5837 | 162235 | 377891
KILCARAGH | 32 | 64 | 978000 | Google Maps | 52.2112 | -7.0811 | 38 KV | 163.374 | 137.3573 | 262860 | 106945
KILCLOHER | 32 | 64 | 249000 | Google Maps | 52.1254 | -7.7792 | 38 KV | 144.2678 | 169.9476 | 215169 | 97029
KILCOCK | 32 | 64 | 248000 | Google Maps | 53.4039 | -6.6548 | 38 KV | 138.7561 | 28.032 | 289521 | 240125
KILCOLGAN | 32 | 64 | 084000 | Google Maps | 53.2117 | -8.8701 | 38 KV | 12.1923 | 175.442 | 141917 | 218241
KILCOOLE | 32 | 64 | 498000 | Google Maps | 53.1022 | -6.0698 | 38 KV | 178.7623 | 28.7769 | 329327 | 207442
KILCULLEN | 32 | 64 | 323000 | Google Maps | 53.127 | -6.7623 | 38 KV | 132.6143 | 41.5346 | 282904 | 209177
KILDARE | 32 | 64 | 014000 | Google Maps | 53.1638 | -6.9199 | 38 KV | 121.6447 | 48.7933 | 272294 | 213109
KILDONAN | 0 | 0 | 768000 |  |  |  | 110 KV | 5980.1028 | 393.3669
KILFADDA | 0 | 0 | 457000 | Google Maps | 51.8935 | -9.369 | 38 KV | 160.6608 | 265.4659 | 105806 | 72088
KILFLYNN | 32 | 64 | 137000 | Google Maps | 52.3457 | -9.6225 | 38 KV | 120.3654 | 252.696 | 89478 | 122760
KILGARVAN | 32 | 64 | 110000 | Google Maps | 51.9035 | -9.4356 | 38 KV | 160.8521 | 268.3892 | 101241 | 73289
KILKEE | 32 | 64 | 275000 | Google Maps | 52.6771 | -9.6399 | 38 KV | 90.8388 | 239.1988 | 89134 | 159653
KILKENNY | 32 | 64 | 683000 | Google Maps | 52.6404 | -7.1719 | 110 KV | 126.9985 | 99.3107 | 256112 | 154627
KILLIN HILL | 0 | 64 | 306000 | Google Maps | 54.7102 | -8.7275 | 38 KV | 158.3351 | 223.0054 | 153164 | 384910
KILLACLOYNE | 0 | 44 | 536000 | Google Maps | 51.9117 | -8.2775 | 38 KV | 155.9472 | 209.8725 | 180951 | 73257
KILLAVOY | 0 | 0 | 641000 |  |  |  | 38 kV | 5980.1028 | 393.3669
KILLEAGH | 0 | 0 | 035000 | Google Maps | 52.3771 | -7.9062 | 38 KV | 115.4378 | 154.5439 | 206439 | 125029
KILLESHANDRA | 32 | 64 | 265000 | Google Maps | 54.0161 | -7.5362 | 38 KV | 113.2941 | 113.7928 | 230451 | 307522
NEW KILLINICK | 0 | 44 |  | Google Maps | 52.2629 | -6.4134 | 110 KV | 193.2524 | 120.0877 | 308360 | 113509
KILLINICK | 32 | 64 | 298000 | Google Maps | 52.258 | -6.4318 | 38 KV | 192.5855 | 120.7674 | 307133 | 112919
KILLONAN | 0 | 0 | 791000 | Google Maps | 52.6401 | -8.5458 | 220 KV | 72.9654 | 172.6806 | 163103 | 154419
KILLOTERAN | 32 | 64 | 911000 | Google Maps | 52.2518 | -7.159 | 110 KV | 156.4637 | 135.5306 | 257483 | 111402
KILLYBEGS | 32 | 64 | 255000 | Google Maps | 54.6461 | -8.4347 | 38 KV | 152.4806 | 204.3901 | 171986 | 377632
KILLYGARRY | 0 | 44 |  | Google Maps | 53.9884 | -7.3254 | 38 KV | 121.4043 | 101.5801 | 244291 | 304537
KILMACTHOMAS | 32 | 64 | 296000 | Google Maps | 52.1947 | -7.4205 | 38 KV | 150.2365 | 149.768 | 239676 | 104869
KILMAGIG | 32 | 64 | 301000 | Google Maps | 52.8508 | -6.2036 | 38 KV | 175.9606 | 54.2413 | 321068 | 179240
KILMAHUD | 0 | 0 | 372000 |  |  |  | 110 KV | 5980.1028 | 393.3669
KILMALLOCK | 32 | 64 | 412000 | Google Maps | 52.4072 | -8.5725 | 38 KV | 98.3574 | 187.616 | 161087 | 128516
KILMARTIN | 32 | 64 | 332000 | Google Maps | 53.0498 | -6.0725 | 38 KV | 179.4521 | 34.1103 | 329303 | 201605
KILMEADEN | 32 | 64 | 576000 | Google Maps | 52.2311 | -7.2463 | 38 KV | 154.3069 | 140.3259 | 251547 | 109028
KILMONEY | 96 | 64 | 482000 | Google Maps | 51.811 | -8.4157 | 38 KV | 165.4658 | 224.577 | 171377 | 62096
KILMORE | 32 | 64 | 736000 | Google Maps | 53.403 | -6.2275 | 110 KV | 167.0019 | 7.4376 | 317936 | 240642
KILNAP | 0 | 52 |  | Google Maps | 51.9223 | -8.4776 | 110 KV | 152.6607 | 218.0879 | 167197 | 74536
KILPADDOGE | 0 | 0 | 921000 | Google Maps | 52.5737 | -9.3871 | 220 KV | 90.4627 | 227.3972 | 106005 | 147793
KILROE | 0 | 0 | 512000 | Google Maps | 53.28 | -9.3814 | 38 kV | 42.9278 | 208.921 | 107905 | 226376
KILROSS ROAD | 32 | 64 | 213000 | Google Maps | 52.4671 | -8.1809 | 38 KV | 98.4008 | 162.1243 | 187758 | 135044
KILRUSH | 32 | 64 | 095000 | Google Maps | 52.6485 | -9.4801 | 38 KV | 86.6795 | 230.1257 | 99872 | 156243
KILSARAN | 32 | 64 | 561000 | Google Maps | 53.881 | -6.3721 | 38 KV | 169.4575 | 61.071 | 307106 | 293617
KILSHANNY | 32 | 64 | 125000 | Google Maps | 52.2675 | -8.2427 | 38 KV | 118.031 | 179.6109 | 183483 | 112847
KILTEEL | 32 | 20 | 684000 | Google Maps | 53.2466 | -6.5399 | 110 KV | 146.0976 | 21.8971 | 297518 | 222765
KILTIMAGH | 32 | 64 | 349000 | Google Maps | 53.857 | -8.9966 | 38 KV | 65.7611 | 190.9077 | 134470 | 290174
KILTOY | 0 | 0 | 943000 | Google Maps | 54.9614 | -7.7057 | 38 KV | 197.9902 | 204.3182 | 218902 | 412692
KIMMAGE | 32 | 64 | 145000 | Google Maps | 53.3114 | -6.3025 | 38 KV | 161.7179 | 4.61 | 313192 | 230328
KINGSBRIDGE | 32 | 64 | 107000 | Google Maps | 53.3457 | -6.2938 | 38 KV | 162.3426 | 3.1482 | 313682 | 234164
KINGSCOURT | 32 | 64 | 122000 | Google Maps | 53.8881 | -6.787 | 38 KV | 144.9918 | 70.9119 | 279808 | 293859
KINGSCOURT 400KV | 0 | 0 | 187000 |  |  |  | 400 kV | 5980.1028 | 393.3669
KINNEGAD | 0 | 0 | 777000 | Google Maps | 53.4303 | -7.1426 | 110 KV | 106.9331 | 60.382 | 257043 | 242564
KINSALE | 32 | 64 | 225000 | Google Maps | 51.7266 | -8.5449 | 38 KV | 173.9071 | 237.4999 | 162400 | 52767
KNOCKACUMMER | 0 | 0 | 965000 | Google Maps | 52.2596 | -9.1006 | 110 KV | 116.7697 | 226.6847 | 124897 | 112503
KNOCKAFUTERA | 0 | 0 | 758000 | Google Maps | 52.2882 | -8.6108 | 38 KV | 111.3011 | 197.4855 | 158368 | 115289
KNOCKALOUGH | 0 | 0 | 859000 |  |  |  | 110 KV | 5980.1028 | 393.3669
KNOCKANE | 0 | 0 | 657000 | Google Maps | 52.7384 | -8.2252 | 110 kV | 69.8418 | 148.4013 | 184840 | 165240
KNOCKANURE | 0 | 0 | 982000 |  |  |  | 220 KV | 5980.1028 | 393.3669
KNOCKAPHUNTA | 32 | 64 | 979000 | Google Maps | 53.8383 | -9.3205 | 38 KV | 72.5185 | 210.9223 | 113121 | 288436
KNOCKAWARRIGA | 0 | 0 | 653000 | Google Maps | 52.3453 | -9.2165 | 38 KV | 109.5067 | 228.4245 | 117149 | 122163
KNOCKBROGAN | 0 | 0 | 026000 | Google Maps | 51.7515 | -8.739 | 38 KV | 170.6566 | 244.2979 | 149014 | 55657
KNOCKEARAGH | 32 | 64 | 685000 | Google Maps | 52.0765 | -9.4388 | 110 KV | 142.6245 | 257.2417 | 101406 | 92533
KNOCKMULLEN | 32 | 64 | 957000 | Google Maps | 52.396 | -6.9798 | 38 kV | 153.9746 | 115.7698 | 269500 | 127600
KNOCKNAGASHEL | 0 | 0 | 956000 |  |  |  | 110 kV | 5980.1028 | 393.3669
KNOCKNAGEE | 0 | 44 |  | Google Maps | 52.8559 | -6.8822 | 38 kV | 132.7533 | 68.3609 | 275336 | 178888
KNOCKRAHA | 0 | 0 | 776000 | Google Maps | 51.9541 | -8.3201 | 220 KV | 150.7675 | 208.2129 | 178046 | 77985
KNOCKRANNY | 0 | 0 | 862000 | Google Maps | 53.3632 | -9.2858 | 110 KV | 37.521 | 202.2762 | 114447 | 235525
KNOCKROUR | 0 | 0 | 227000 |  |  |  | 38 KV | 5980.1028 | 393.3669
KNOCKUMBER | 0 | 0 | 816000 | Google Maps | 53.6554 | -6.7138 | 110 KV | 139.9746 | 46.9745 | 285088 | 268042
KYLEERAGH | 96 | 64 | 421000 | Google Maps | 52.872 | -8.1859 | 38 KV | 58.916 | 139.7044 | 187535 | 180100
KYLETAUN | 0 | 0 | 017000 | Google Maps | 52.532 | -8.9505 | 38 KV | 85.0981 | 202.5748 | 135543 | 142671
LABBAN | 0 | 0 | 552000 | Google Maps | 52.177 | -8.1042 | 38 kV | 130.4663 | 179.9141 | 192920 | 102750
LACKA | 0 | 0 | 644000 | Google Maps | 52.1528 | -9.2281 | 38 KV | 130.3201 | 240.5311 | 115992 | 100765
LAKE | 0 | 0 | 027000 | Google Maps | 51.7222 | -9.1052 | 38 KV | 175.708 | 264.3442 | 123674 | 52711
LANESBOROUGH | 32 | 64 | 686000 | Google Maps | 53.6752 | -7.9868 | 110 KV | 65.775 | 121.3113 | 200918 | 269478
LARGAN HILL | 0 | 0 | 959000 | Google Maps | 53.946 | -8.5589 | 38 KV | 74.2785 | 167.1376 | 163352 | 299759
LAUNLUSH | 0 | 0 | 583000 | Google Maps | 52.3246 | -9.5563 | 38 kV | 120.3209 | 249.7918 | 93942 | 120302
LAWLESSTOWN | 32 | 64 | 542000 | Google Maps | 52.3706 | -7.7186 | 38 KV | 122.6225 | 146.2257 | 219218 | 124324
LEE BRIDGE | 24 | 0 | 176000 | Google Maps | 51.8936 | -8.9453 | 38 KV | 155.5002 | 243.2431 | 134972 | 71633
LEESON STREET | 32 | 64 | 342000 | Google Maps | 53.3311 | -6.253 | 38 KV | 165.0174 | 0.75896 | 316435 | 232599
LEIXLIP | 32 | 64 | 289000 | Google Maps | 53.3616 | -6.4844 | 38 KV | 149.7563 | 15.9301 | 300953 | 235641
LEIXLIP GENERATOR | 0 | 0 | 700000 | Google Maps | 53.3613 | -6.4897 | 38 KV | 149.403 | 16.2739 | 300600 | 235603
LETTERAGH | 0 | 0 | 395000 | Google Maps | 52.7804 | -9.1526 | 38 kV | 62.779 | 204.3297 | 122270 | 170510
LETTERKENNY | 32 | 64 | 687000 | Google Maps | 54.9242 | -7.6974 | 110 KV | 194.2979 | 200.4259 | 219448 | 408550
LIBERTY STREET | 32 | 64 | 309000 | Google Maps | 51.898 | -8.4782 | 110 KV | 155.3481 | 220.1284 | 167134 | 71803
LIFFEY VALLEY | 32 | 64 | 633000 | Google Maps | 53.3481 | -6.3943 | 38 KV | 155.6829 | 9.7725 | 306986 | 234268
LIMERICK | 32 | 64 | 688000 | Google Maps | 52.6351 | -8.6413 | 110 KV | 72.6772 | 178.6816 | 156634 | 153918
LISDRUM | 32 | 64 | 624000 | Google Maps | 54.2447 | -6.9102 | 110 KV | 160.4737 | 110.0101 | 271095 | 333413
LISGLENNON | 0 | 0 | 550000 | Google Maps | 54.1911 | -9.2242 | 38 kV | 105.6167 | 218.0156 | 120138 | 327592
LISHEEN | 0 | 64 | 792000 | Google Maps | 52.7511 | -7.6818 | 110 KV | 92.2541 | 116.1804 | 221535 | 166677
LISMORE | 32 | 64 | 374000 | Google Maps | 52.1366 | -7.9211 | 38 KV | 139.113 | 174.9727 | 205463 | 98253
LITTLE BRAY | 32 | 64 | 223000 | Google Maps | 53.2091 | -6.126 | 38 KV | 173.8432 | 16.4564 | 325256 | 219242
LITTLE ISLAND | 0 | 0 | 406000 | Google Maps | 51.9014 | -8.3332 | 38 KV | 156.3694 | 213.2053 | 177118 | 72153
LITTLE MILLS | 32 | 64 | 316000 | Google Maps | 53.9867 | -6.4364 | 38 KV | 170.4201 | 73.3465 | 302614 | 305285
LLOYD | 32 | 64 | 711000 | Google Maps | 53.7383 | -6.9017 | 38 KV | 131.2713 | 62.1894 | 272521 | 277064
LODGEWOOD | 0 | 0 | 601000 | Google Maps | 52.5792 | -6.5373 | 220 KV | 167.0009 | 86.5926 | 299202 | 148502
LONGFORD | 32 | 64 | 049000 | Google Maps | 53.748 | -7.8107 | 38 KV | 79.8543 | 113.1963 | 212539 | 277596
LONGPOINT | 0 | 0 | 821000 | Google Maps | 51.8348 | -8.2375 | 220 KV | 164.8718 | 214.7754 | 183678 | 64692
LOUGH DOO | 0 | 0 | 754000 | Google Maps | 55.1992 | -7.4436 | 38 kV | 228.6664 | 221.3928 | 235482 | 439259
LOUGHAN | 0 | 0 | 530000 | Google Maps | 54.0738 | -8.1366 | 38 kV | 96.0498 | 149.2152 | 191103 | 313853
LOUGHANALLA | 32 | 64 | 613000 | Google Maps | 53.685 | -7.2952 | 38 KV | 105.1193 | 79.4933 | 246616 | 270801
LOUGHBEG | 0 | 0 | 881000 | Google Maps | 51.8302 | -8.3053 | 38 KV | 164.5058 | 218.0975 | 178983 | 64198
LOUGHDALE | 0 | 0 | 548000 | Google Maps | 53.2861 | -9.1961 | 38 KV | 30.6001 | 196.5407 | 120277 | 226832
LOUGHDERRYDUFF | 0 | 0 | 224000 | Google Maps | 54.8153 | -8.3848 | 38 KV | 171.5554 | 215.8464 | 175826 | 396833
LOUGHLINSTOWN | 32 | 64 | 199000 | Google Maps | 53.2552 | -6.1437 | 38 KV | 172.393 | 11.5152 | 323938 | 224341
LOUGHREA | 32 | 64 | 132000 | Google Maps | 53.2076 | -8.6 | 38 KV | 12.5711 | 157.5397 | 159956 | 217602
LOUGHSHINNY | 32 | 64 | 170000 | Google Maps | 53.5474 | -6.1067 | 38 KV | 176.6262 | 25.2183 | 325546 | 256926
LOUGHTAGALLA | 32 | 64 | 127000 | Google Maps | 52.6904 | -7.7765 | 38 KV | 92.2636 | 125.2992 | 215165 | 159901
LOUTH | 0 | 0 | 793000 | Google Maps | 53.9673 | -6.5658 | 220 KV | 161.89 | 73.1912 | 294174 | 302941
LUCAN EAST | 32 | 64 | 359000 | Google Maps | 53.3609 | -6.4388 | 38 KV | 152.7755 | 12.9323 | 303989 | 235629
LUMCLOON | 32 | 64 | 147000 | Google Maps | 53.2224 | -7.8199 | 38 KV | 61.3368 | 105.5941 | 212077 | 219099
MACETOWN | 32 | 64 | 652000 | Google Maps | 53.4142 | -6.4143 | 110 KV | 154.7369 | 13.9514 | 305489 | 241595
MACROOM | 32 | 64 | 630000 | Google Maps | 51.8957 | -8.8922 | 110 KV | 154.9811 | 240.3931 | 138634 | 71821
MALAHIDE | 32 | 64 | 212000 | Google Maps | 53.4419 | -6.1571 | 38 KV | 171.9675 | 13.1349 | 322509 | 245092
MALLOW | 32 | 64 | 689000 | Google Maps | 52.143 | -8.6208 | 110 KV | 127.3601 | 208.1639 | 157550 | 99142
MANGANS | 0 | 64 | 596000 | Google Maps | 52.8336 | -6.4671 | 38 KV | 159.7337 | 57.9415 | 303346 | 176927
MANOR STREET | 32 | 64 | 346000 | Google Maps | 52.2556 | -7.112 | 38 KV | 158.3175 | 133.7458 | 260688 | 111859
MANORHAMILTON | 32 | 64 | 345000 | Google Maps | 54.2931 | -8.1746 | 38 KV | 117.8677 | 165.5587 | 188678 | 338269
MARINA | 32 | 4 | 794000 | Google Maps | 51.9002 | -8.4468 | 110 KV | 155.3519 | 218.4921 | 169294 | 72039
MARROWBONE LANE | 32 | 64 | 128000 | Google Maps | 53.3394 | -6.2861 | 38 KV | 162.8414 | 2.5028 | 314214 | 233476
MARSHES | 32 | 64 | 358000 | Google Maps | 53.9792 | -6.389 | 38 KV | 172.8398 | 72.0471 | 305741 | 304513
MAYFIELD | 32 | 64 | 300000 | Google Maps | 51.9178 | -8.4252 | 38 KV | 153.6032 | 216.041 | 170795 | 73988
MAYNOOTH | 0 | 0 | 901000 | Google Maps | 53.3489 | -6.6024 | 220 KV | 141.878 | 23.5984 | 293125 | 234071
MCDERMOTT | 32 | 64 | 737000 | Google Maps | 53.3543 | -6.2508 | 110 KV | 165.22 | 1.8936 | 316521 | 235190
MCDONAGH | 32 | 64 | 390000 | Google Maps | 52.6547 | -7.2407 | 38 KV | 122.2891 | 101.0477 | 251436 | 156171
MEATH HILL | 32 | 64 | 691000 | Google Maps | 53.8911 | -6.7312 | 110 KV | 148.4137 | 69.423 | 283471 | 294254
MEELICK | 0 | 0 | 522000 | Google Maps | 53.0198 | -7.2962 | 38 KV | 100.4566 | 78.4636 | 247277 | 196762
MEENACHULLALAN | 0 | 0 | 656000 | Google Maps | 54.6738 | -8.4572 | 38 KV | 155.3566 | 207.3284 | 170596 | 380396
MEENACLOY | 0 | 0 | 864000 | Google Maps | 54.7165 | -8.3539 |  | 160.9848 | 206.394 | 177242 | 385447
MEENADREEN[MULREAVY] | 0 | 0 | 569000 | Google Maps | 54.6645 | -7.9695 | 110 kV | 161.2312 | 185.8899 | 202015 | 379593
MEENBOG | 0 | 0 | 703000 | Google Maps | 54.873 | -7.8937 | 110 KV | 184.7884 | 201.983 | 206874 | 402814
MEENTYCAT | 0 | 0 | 732000 | Google Maps | 54.8519 | -7.823 | 110 KV | 183.9987 | 197.5683 | 211419 | 400479
MELBOURNE | 0 | 0 | 194000 |  |  |  | 110 kV | 5980.1028 | 393.3669
MERRION SQUARE | 32 | 64 | 105000 | Google Maps | 53.3388 | -6.246 | 38 KV | 165.5006 | 0.23842 | 316885 | 233469
MERVILLE | 32 | 64 | 200000 | Google Maps | 53.3817 | -6.2918 | 38 KV | 162.6191 | 5.7148 | 313719 | 238175
MERVUE | 0 | 0 | 364000 | Google Maps | 53.2893 | -9.0128 | 38 KV | 18.4205 | 184.3146 | 132504 | 227009
MIDLETON | 32 | 20 | 775000 | Google Maps | 51.938 | -8.1849 | 110 KV | 154.4651 | 203.6745 | 187176 | 76131
MILANE HILL | 0 | 0 | 770000 | Google Maps | 51.6943 | -9.2066 | 38 KV | 179.8698 | 271.5565 | 116616 | 49717
MILESTONE | 0 | 0 | 833000 |  |  |  | 38 KV | 5980.1028 | 393.3669
MILFORD (MWR) | 32 | 64 | 236000 | Google Maps | 52.3391 | -8.8604 | 38 KV | 105.6566 | 208.1268 | 141405 | 121125
MILFORD (NR) | 32 | 20 | 209000 | Google Maps | 55.0822 | -7.6881 | 38 KV | 211.0085 | 215.7445 | 219966 | 426143
MILLTOWN (DR) | 32 | 64 | 069000 | Google Maps | 53.315 | -6.2523 | 110 KV | 165.0546 | 2.4976 | 316529 | 230815
MILLTOWN (SR) | 32 | 64 | 244000 | Google Maps | 52.1379 | -9.7149 | 38 KV | 143.7143 | 269.4788 | 82638 | 99782
MILLTOWN MALBAY | 32 | 64 | 439000 | Google Maps | 52.8356 | -9.4205 | 38 KV | 67.8578 | 219.7344 | 104319 | 176978
MISERY HILL | 32 | 64 | 980000 | Google Maps | 53.3452 | -6.2394 | 110 KV | 165.9489 | 1.0664 | 317303 | 234193
MOANMORE | 0 | 0 | 648000 | Google Maps | 52.6733 | -9.4807 | 38 KV | 84.4562 | 229.1999 | 99891 | 158998
MOATE | 32 | 64 | 073000 | Google Maps | 53.3921 | -7.7062 | 38 KV | 69.3622 | 97.228 | 219597 | 238012
MOHILL | 32 | 64 | 048000 | Google Maps | 53.9153 | -7.8554 | 38 KV | 90.9229 | 124.2573 | 209553 | 296211
MONAVEA | 0 | 0 | 955000 | Google Maps | 52.8235 | -7.0588 | 38 KV | 123.3246 | 78.8628 | 263500 | 175100
MONEENAGHIESHA | 32 | 64 | 039000 | Google Maps | 53.2826 | -9.0366 | 38 KV | 19.9999 | 185.9329 | 130911 | 226276
MONETEEN | 0 | 0 | 923000 | Google Maps | 52.6369 | -8.6881 | 110 KV | 72.274 | 181.4278 | 153464 | 154145
MONEYCOOLEY | 32 | 64 | 549000 | Google Maps | 53.3648 | -6.5793 | 38 KV | 143.476 | 22.2368 | 294623 | 235874
MONEYPOINT | 0 | 0 | 795000 | Google Maps | 52.6105 | -9.4225 | 400 KV | 88.1049 | 228.0333 | 103690 | 151935
MONFIN | 96 | 64 | 297000 | Google Maps | 52.4809 | -6.58 | 38 KV | 170.1147 | 97.8956 | 296526 | 137514
MONKSLAND | 0 | 0 | 626000 | Google Maps | 53.4171 | -7.9867 | 38 KV | 51.8005 | 116.0179 | 200932 | 240748
MONKSTOWN | 32 | 64 | 222000 | Google Maps | 53.295 | -6.1702 | 38 KV | 170.5199 | 7.0402 | 322056 | 228724
MONREAD | 32 | 64 | 902000 | Google Maps | 53.2415 | -6.6454 | 110 KV | 139.1145 | 28.5613 | 290469 | 222032
MORNINGTON ROAD | 32 | 64 | 168000 | Google Maps | 53.7146 | -6.3361 | 38 KV | 165.701 | 42.3936 | 309907 | 275150
MORRISTOWN | 32 | 20 | 121000 | Google Maps | 53.1825 | -6.8196 | 38 KV | 128.0443 | 41.8252 | 278962 | 215296
MOUNT CRONALAGHT | 0 | 0 | 272000 | Google Maps | 55.0584 | -8.2174 | 38 KV | 199.9189 | 230.6686 | 186152 | 423470
MOUNT LUCAS | 0 | 0 | 872000 |  |  |  | 110 KV | 5980.1028 | 393.3669
MOUNT MERRION | 32 | 64 | 101000 | Google Maps | 53.2969 | -6.2054 | 38 KV | 168.1822 | 5.3502 | 319708 | 228874
MOUNT MISERY | 32 | 64 | 009000 | Google Maps | 52.2709 | -7.1249 | 38 KV | 156.4731 | 132.5916 | 259788 | 113555
MOUNTGORRY | 32 | 64 | 524000 | Google Maps | 53.455 | -6.2072 | 38 KV | 168.7888 | 13.3864 | 319141 | 246470
MOUNTMELLICK | 32 | 64 | 387000 | Google Maps | 53.1071 | -7.308 | 38 KV | 97.17 | 75.2655 | 246393 | 206468
MOUNTRATH | 32 | 64 | 388000 | Google Maps | 52.9906 | -7.4646 | 38 KV | 90.9388 | 90.0255 | 236003 | 193421
MOVILLE | 32 | 64 | 405000 | Google Maps | 55.1949 | -7.0471 | 38 KV | 238.9062 | 213.2342 | 260735 | 439062
MOY | 32 | 64 | 774000 | Google Maps | 54.1232 | -9.1882 | 110 KV | 97.7114 | 212.8068 | 122361 | 319994
MOYLISH | 32 | 64 | 402000 | Google Maps | 52.6782 | -8.6543 | 38 KV | 67.8334 | 177.3617 | 155796 | 158717
MUINGNAMINNANE | 0 | 0 | 738000 | Google Maps | 52.2924 | -9.5351 | 38 KV | 122.8878 | 250.2316 | 95312 | 116694
MUINGS | 0 | 0 | 5840000 |  |  |  | 38 kV | 5980.1028 | 393.3669
MULGANNON | 32 | 64 | 174000 | Google Maps | 52.3244 | -6.4646 | 38 KV | 186.3895 | 113.6838 | 304733 | 120255
MULLAGH | 32 | 64 | 428000 | Google Maps | 53.8128 | -6.9273 | 38 KV | 133.0451 | 69.4433 | 270709 | 285327
MULLAGHARLIN | 32 | 64 | 817000 | Google Maps | 53.9756 | -6.4089 | 110 KV | 171.5015 | 71.8381 | 304450 | 304090
MULLASAWNY | 0 | 0 | 537000 | Google Maps | 54.9079 | -7.528 | 38 kV | 196.7571 | 193.8056 | 230325 | 406794
MULLINANALT | 0 | 0 | 655000 | Google Maps | 54.0767 | -6.9119 | 38 KV | 148.8285 | 93.2299 | 271270 | 314712
MULLINGAR | 32 | 20 | 693000 | Google Maps | 53.5384 | -7.3714 | 110 KV | 94.6726 | 77.907 | 241725 | 254439
MULMOSOG | 0 | 0 | 531000 | Google Maps | 54.7201 | -8.3853 | 38 kV | 161.0678 | 208.061 | 175220 | 385850
MULREAVY | 0 | 0 | 890000 |  |  |  | 110 KV | 5980.1028 | 393.3669
MULTEEN | 0 | 0 | 752000 | Google Maps | 52.6438 | -8.1482 | 38 KV | 81.5613 | 149.0981 | 190019 | 154697
MUNGRET | 0 | 0 | 944000 | Google Maps | 52.6412 | -8.6917 | 110 KV | 71.7838 | 181.4311 | 153227 | 154628
NAAS | 32 | 64 | 015000 | Google Maps | 53.2053 | -6.6662 | 38 KV | 137.9947 | 31.4972 | 289175 | 218014
NAVAN | 32 | 64 | 694000 | Google Maps | 53.6998 | -6.7066 | 110 KV | 141.8893 | 50.5038 | 285478 | 272994
NENAGH | 32 | 64 | 946000 | Google Maps | 52.8613 | -8.1814 | 110 KV | 60.0377 | 139.8916 | 187830 | 178906
NEW GURRANEBANE | 0 | 44 |  |  |  |  | 38 KV | 5980.1028 | 393.3669
NEW KILMONEY-CARRIGALINE STATION | 0 | 52 |  |  |  |  | 38 KV | 5980.1028 | 393.3669
NEW MAYFIELD-RIVERSTOWN STATION | 0 | 44 |  |  |  |  | 110 KV | 5980.1028 | 393.3669
NEW MONAGHAN | 0 | 44 |  | Google Maps | 54.234 | -7.0317 | 110 KV | 153.7923 | 112.365 | 263183 | 332102
NEW ROSS | 0 | 0 | 008000 | Google Maps | 52.4005 | -6.9284 | 38 KV | 156.3101 | 113.8799 | 272993 | 128152
NEW TINAHASK | 0 | 44 |  |  |  |  | 38 KV | 5980.1028 | 393.3669
NEWBRIDGE | 32 | 64 | 695000 | Google Maps | 53.1956 | -6.8355 | 110 KV | 126.8511 | 42.2215 | 277879 | 216731
NEWBRIDGE EAST | 0 | 44 |  |  |  |  | 110 KV | 5980.1028 | 393.3669
NEWBROOK | 32 | 64 | 465000 | Google Maps | 53.5127 | -7.3705 | 38 KV | 93.9474 | 77.0956 | 241810 | 251570
NEWBURY | 0 | 0 | 883000 | Google Maps | 53.4013 | -6.2207 | 110 KV | 167.4445 | 7.3529 | 318380 | 240467
NEWCASTLEWEST | 32 | 64 | 185000 | Google Maps | 52.4444 | -9.0383 | 38 KV | 95.7869 | 212.4328 | 129447 | 133007
NEWMARKET (DR) | 32 | 64 | 217000 | Google Maps | 53.3377 | -6.2763 | 38 KV | 163.485 | 1.843 | 314868 | 233297
NEWMARKET (SR) | 32 | 64 | 481000 | Google Maps | 52.2126 | -9.0066 | 38 KV | 120.7702 | 224.2889 | 131244 | 107181
NEWPORT | 32 | 64 | 260000 | Google Maps | 53.8757 | -9.5169 | 38 KV | 83.3938 | 224.4743 | 100280 | 292857
NEWTOWNCUNNINGHAM | 32 | 64 | 503000 | Google Maps | 55.0007 | -7.4777 | 38 KV | 207.4935 | 201.8119 | 233470 | 417151
NEWTOWNSTALABAN | 0 | 0 | 091000 | Google Maps | 53.726 | -6.319 | 38 KV | 167.1325 | 43.5184 | 311007 | 276449
NORTH CITY JUNCTION | 0 | 44 |  |  |  |  | 110 KV | 5980.1028 | 393.3669
NORTH EAST CASHEL | 0 | 44 |  |  |  |  | 110 KV | 5980.1028 | 393.3669
NORTH KERRY | 0 | 0 |  |  |  |  | 220 kV | 5980.1028 | 393.3669
NORTH QUAYS | 32 | 64 | 981000 | Google Maps | 53.3504 | -6.2354 | 110 KV | 166.2288 | 1.7008 | 317556 | 234782
NORTH WALL | 0 | 0 | 999000 | Google Maps | 53.3496 | -6.212 | 220 KV | 167.7811 | 2.7946 | 319118 | 234726
NOVARTIS | 0 | 0 | 880000 | Google Maps | 51.8271 | -8.3437 | 38 KV | 164.4045 | 220.0252 | 176355 | 63862
NOWLAN PARK | 0 | 0 | 011000 | Google Maps | 52.6549 | -7.2404 | 38 KV | 122.2925 | 101.0126 | 251449 | 156206
NUTLEY LANE | 0 | 44 | 835000 | Google Maps | 53.3177 | -6.215 | 110 KV | 167.5293 | 3.1206 | 318987 | 231171
OAKFIELD | 32 | 64 | 240000 | Google Maps | 54.2624 | -8.4977 | 38 KV | 109.6665 | 180.4484 | 167616 | 334954
OLDBAWN | 32 | 64 | 365000 | Google Maps | 53.2781 | -6.3571 | 38 KV | 158.1287 | 9.7888 | 309637 | 226540
OLDCASTLE | 32 | 64 | 538000 | Google Maps | 53.7723 | -7.1523 | 38 KV | 117.7923 | 77.0156 | 255945 | 280623
OLDCOURT | 0 | 0 | 947000 | Google Maps | 51.8788 | -8.324 | 110 KV | 158.9574 | 214.7348 | 177735 | 69609
OLDSTREET | 0 | 0 | 948000 | Google Maps | 53.1347 | -8.2695 | 400 KV | 35.3256 | 136.8148 | 182009 | 209355
OLDTOWN | 0 | 0 | 560000 | Google Maps | 53.0187 | -7.3003 | 38 KV | 100.2349 | 78.763 | 247005 | 196636
ORANMORE | 32 | 64 | 487000 | Google Maps | 53.2789 | -8.9346 | 38 KV | 13.247 | 179.1664 | 137703 | 225773
OUGHTERARD | 32 | 64 | 444000 | Google Maps | 53.4159 | -9.3012 | 38 KV | 40.2038 | 203.3415 | 113531 | 241408
OUGHTRAGH | 32 | 64 | 696000 | Google Maps | 52.1366 | -9.6929 | 110 KV | 143.1738 | 268.2668 | 84140 | 99598
PALLAS | 32 | 64 | 559000 | Google Maps | 53.0402 | -7.3147 | 38 KV | 98.6074 | 78.5682 | 246018 | 199021
PALMERSTOWN | 32 | 64 | 302000 | Google Maps | 53.3526 | -6.3789 | 38 KV | 156.7148 | 8.8428 | 307995 | 234798
PARKMORE | 32 | 64 | 551000 | Google Maps | 53.3049 | -8.9913 | 38 KV | 17.1092 | 182.8057 | 133963 | 228715
PARKROE | 0 | 0 | 750000 | Google Maps | 52.6017 | -8.1656 | 38 kV | 85.1698 | 152.6181 | 188826 | 150013
PARKVIEW | 0 | 0 | 554000 | Google Maps | 53.3632 | -6.2277 | 38 KV | 166.7823 | 3.1975 | 318034 | 236217
PATRICKSWELL | 32 | 64 | 077000 | Google Maps | 52.5984 | -8.7442 | 38 KV | 76.4919 | 186.7524 | 149622 | 149893
PEARSE STREET | 0 | 0 | 661000 | Google Maps | 53.3427 | -6.2469 | 38 KV | 165.4446 | 0.61009 | 316810 | 233908
PELLETSTOWN | 32 | 64 | 092000 | Google Maps | 53.3815 | -6.3276 | 110 KV | 160.2443 | 7.1997 | 311335 | 238095
PEMBROKE | 32 | 20 | 094000 | Google Maps | 53.3392 | -6.2307 | 38 KV | 166.5156 | 1.2128 | 317902 | 233535
PHIBSBORO | 32 | 64 | 307000 | Google Maps | 53.3586 | -6.2724 | 38 KV | 163.8001 | 2.8425 | 315070 | 235627
PIPERHILL | 0 | 0 | 757000 | Google Maps | 52.6227 | -8.1026 | 38 KV | 85.1018 | 147.7618 | 193100 | 152350
PLATIN | 0 | 0 | 797000 | Google Maps | 53.6808 | -6.3861 | 110 KV | 161.5307 | 39.3047 | 306687 | 271311
POLLAPHUCA | 0 | 0 | 798000 | Google Maps | 53.1209 | -6.5906 | 110 KV | 144.0462 | 33.2022 | 294408 | 208710
POLLERTON | 32 | 64 | 242000 | Google Maps | 52.8389 | -6.9115 | 38 KV | 131.6536 | 71.0664 | 273402 | 176961
POOLBEG | 0 | 0 | 799000 | Google Maps | 53.3395 | -6.1897 | 220 KV | 169.2373 | 3.9345 | 320631 | 233644
POPPINTREE | 32 | 64 | 983000 | Google Maps | 53.406 | -6.272 | 110 KV | 164.0805 | 7.7969 | 314970 | 240906
PORTAN | 0 | 0 | 873000 |  |  |  | 400 KV | 5980.1028 | 393.3669
PORTARLINGTON | 32 | 64 | 160000 | Google Maps | 53.1615 | -7.2096 | 38 KV | 102.5372 | 67.0715 | 252916 | 212599
PORTLAOISE | 32 | 64 | 054000 | Google Maps | 53.0288 | -7.3004 | 110 KV | 99.8901 | 78.2806 | 247068 | 197561
PORTLAW | 96 | 64 | 471000 | Google Maps | 52.2958 | -7.3145 | 38 KV | 145.8078 | 136.3875 | 246817 | 116189
PORTMARNOCK | 0 | 0 | 663000 | Google Maps | 53.4175 | -6.151 | 38 KV | 172.1697 | 11.0431 | 322986 | 242393
POTTERY ROAD | 32 | 64 | 317000 | Google Maps | 53.2734 | -6.152 | 110 KV | 171.7773 | 9.6018 | 323333 | 226353
PROSPECT | 0 | 0 | 800000 | Google Maps | 52.6396 | -9.2538 | 220 KV | 79.8375 | 216.2294 | 115175 | 154958
PURCELLS INCH | 96 | 64 | 485000 | Google Maps | 52.6441 | -7.2095 | 38 KV | 124.6852 | 100.583 | 253561 | 155018
RAFFEEN | 0 | 0 | 778000 | Google Maps | 51.8268 | -8.3696 | 220 KV | 164.1655 | 221.19 | 174567 | 63836
RAHANS | 32 | 64 | 461000 | Google Maps | 54.0995 | -9.1572 | 38 KV | 94.5904 | 209.9145 | 124344 | 317324
RAHEEN | 32 | 64 | 401000 | Google Maps | 52.6265 | -8.6563 | 38 KV | 73.5594 | 180.0196 | 155622 | 152948
RAHEEN (Lineschool) | 0 | 0 | - | Google Maps | 53.0187 | -7.3003 | 38 KV | 100.235 | 78.7664 | 246998 | 196642
RAHEEN BARR | 0 | 0 | 378000 | Google Maps | 53.9059 | -9.341 | 38 KV | 79.6345 | 214.1724 | 111915 | 295983
RAHENY | 0 | 0 | 662000 | Google Maps | 53.3813 | -6.1765 | 38 KV | 170.2576 | 6.8609 | 321393 | 238321
RAMPARTS | 32 | 64 | 175000 | Google Maps | 54.0031 | -6.3977 | 38 KV | 173.495 | 74.7622 | 305112 | 307163
RAMSTOWN | 0 | 0 | 287000 | Google Maps | 52.6688 | -6.3046 | 38 KV | 176.6477 | 74.5101 | 314740 | 158822
RANDALSTOWN | 32 | 64 | 463000 | Google Maps | 53.6797 | -6.7123 | 38 KV | 140.8477 | 48.9793 | 285137 | 270750
RATHCAHILL | 0 | 0 | 431000 | Google Maps | 52.3973 | -9.1288 | 38 KV | 102.3152 | 220.3696 | 123210 | 127854
RATHDOWN | 0 | 0 | 660000 | Google Maps | 53.1592 | -6.077 | 38 KV | 177.5539 | 22.9003 | 328676 | 213780
RATHDOWNEY | 32 | 64 | 391000 | Google Maps | 52.857 | -7.6024 | 38 KV | 89.5008 | 105.2756 | 226830 | 178494
RATHDRUM | 32 | 64 | 602000 | Google Maps | 52.9473 | -6.2443 | 38 KV | 170.4822 | 43.4141 | 318065 | 189913
RATHGOGGIN | 0 | 0 | 025000 | Google Maps | 52.3484 | -8.6811 | 38 KV | 104.3514 | 197.4229 | 153634 | 122033
RATHKEALE | 32 | 64 | 712000 | Google Maps | 52.5435 | -8.9684 | 110 KV | 84.049 | 203.0672 | 134351 | 143969
RATHMORE | 32 | 64 | 221000 | Google Maps | 52.0848 | -9.184 | 38 KV | 136.9714 | 242.4459 | 118887 | 93143
RATHMULLAN | 32 | 64 | 422000 | Google Maps | 53.7077 | -6.3747 | 38 KV | 163.0468 | 42.0598 | 307377 | 274317
RATHRUSSAN | 0 | 0 | 987000 | Google Maps | 54.0008 | -7.1059 | 110 KV | 133.6224 | 93.0877 | 258682 | 306093
REAMORE | 0 | 64 | 197000 | Google Maps | 52.302 | -9.5435 | 110 KV | 122.1766 | 250.2192 | 94760 | 117775
REANAGOWAN | 0 | 0 | 354000 |  |  |  | 38 kV | 5980.1028 | 393.3669
RECESS | 32 | 64 | 581000 | Google Maps | 53.4588 | -9.7711 | 38 KV | 71.3092 | 234.6911 | 82411 | 246849
REDMONDSTOWN | 0 | 0 | 219000 | Google Maps | 52.3627 | -7.6551 | 38 KV | 125.7636 | 144.0287 | 223544 | 123469
RICHFIELD | 0 | 0 | 997000 | Google Maps | 52.2187 | -6.5944 | 38 KV | 186.7021 | 126.6782 | 296117 | 108313
RICHMOND | 32 | 64 | 713000 | Google Maps | 53.7432 | -7.8571 | 110 KV | 77.1777 | 115.8116 | 209479 | 277051
RINAWADE | 0 | 44 | 802000 | Google Maps | 53.3553 | -6.5212 | 110 KV | 147.2866 | 18.2652 | 298515 | 234894
RINEANNA | 32 | 64 | 109000 | Google Maps | 52.715 | -8.8806 | 38 KV | 64.2598 | 189.694 | 140538 | 162972
RINGASKIDDY 110KV | 32 | 64 | 603000 | Google Maps | 51.8333 | -8.3448 | 110 KV | 163.7131 | 219.5417 | 176282 | 64551
RINGASKIDDY 38KV | 0 | 0 | 898000 | Google Maps | 51.8333 | -8.3443 | 38 KV | 163.7191 | 219.5417 | 176282 | 64551
RINGSEND | 32 | 64 | 998000 | Google Maps | 53.3407 | -6.2065 | 110 KV | 168.1257 | 2.8328 | 319510 | 233742
RIVERS | 0 | 0 | 610000 | Google Maps | 52.6736 | -8.5375 | 38 KV | 69.4084 | 170.4897 | 163687 | 158137
RIVERSTOWN | 32 | 64 | 129000 | Google Maps | 51.9397 | -8.3791 | 38 KV | 151.6585 | 212.1115 | 173979 | 76402
ROCHES STREET | 32 | 64 | 356000 | Google Maps | 52.6615 | -8.6249 | 38 KV | 69.8608 | 176.3811 | 157764 | 156846
ROCK HILL | 0 | 0 | 665000 | Google Maps | 53.3052 | -6.1852 | 38 KV | 169.5151 | 5.5382 | 321029 | 229838
ROCKBORO ROAD | 0 | 0 | 989000 |  |  |  | 110 kV | 5980.1028 | 393.3669
ROOSKY | 32 | 64 | 434000 | Google Maps | 53.8345 | -7.9105 | 38 KV | 81.7748 | 123.1939 | 205938 | 287214
ROSBERCON | 32 | 64 | 179000 | Google Maps | 52.4012 | -6.9549 | 38 KV | 154.8826 | 114.5301 | 271199 | 128207
ROSCOMMON | 32 | 64 | 136000 | Google Maps | 53.6384 | -8.1658 | 38 KV | 54.3776 | 131.6021 | 189081 | 265395
ROSCREA | 32 | 64 | 055000 | Google Maps | 52.9499 | -7.7949 | 38 KV | 73.0842 | 112.0985 | 213837 | 188775
ROSEHILL | 32 | 64 | 193000 | Google Maps | 52.643 | -7.2636 | 38 KV | 121.8023 | 103.0482 | 249895 | 154855
ROSS CARBERY | 32 | 64 | 352000 | Google Maps | 51.6016 | -9.0222 | 38 KV | 188.3302 | 269.859 | 129224 | 39212
ROSSGEIR | 32 | 64 | 489000 | Google Maps | 54.8561 | -7.5036 | 38 KV | 192.1792 | 187.9478 | 231929 | 401045
RUSHEEN | 0 | 0 | 614000 | Google Maps | 52.7793 | -9.2154 |  | 64.853 | 208.3806 | 118032 | 170464
RUSHFIELD | 0 | 0 | 863000 | Google Maps | 55.1986 | -7.4414 | 38 KV | 228.6623 | 221.2873 | 235620 | 439200
RYEBROOK | 0 | 0 | 903000 | Google Maps | 53.3777 | -6.5236 | 110 KV | 147.2424 | 18.8503 | 298306 | 237379
SAGGART | 32 | 64 | 172000 | Google Maps | 53.2753 | -6.4499 | 38 KV | 151.9708 | 15.0929 | 303457 | 226086
SAINT JOSEPHS ROAD | 0 | 0 | 022000 | Google Maps | 52.1425 | -8.6273 | 38 KV | 127.3897 | 208.5409 | 157101 | 99090
SALLINS | 32 | 64 | 268000 | Google Maps | 53.2596 | -6.6677 | 38 KV | 137.5437 | 29.2558 | 288960 | 224044
SALLYNOGGIN ROAD | 32 | 64 | 133000 | Google Maps | 53.2784 | -6.1376 | 38 KV | 172.722 | 9.894 | 324280 | 226934
SALTHILL | 32 | 64 | 161000 | Google Maps | 53.2741 | -9.0794 | 110 KV | 22.8875 | 188.8394 | 128038 | 225381
SANDYFORD | 32 | 64 | 288000 | Google Maps | 53.2681 | -6.2299 | 38 KV | 166.6155 | 7.807 | 318151 | 225633
SANTRY | 32 | 64 | 315000 | Google Maps | 53.3963 | -6.2433 | 38 KV | 165.9154 | 6.5679 | 316906 | 239871
SCARIFF | 32 | 64 | 229000 | Google Maps | 52.9071 | -8.5368 | 38 KV | 44.2024 | 160.5024 | 163929 | 184126
SCARTEEN | 32 | 64 | 211000 | Google Maps | 52.1425 | -8.6756 | 38 KV | 127.2434 | 211.0688 | 153802 | 99102
SCREEB | 32 | 64 | 366000 | Google Maps | 53.3803 | -9.5846 | 110 KV | 57.3264 | 222.1588 | 94598 | 237819
SCREGGAN | 0 | 0 | 654000 | Google Maps | 52.7274 | -8.1354 | 110 kV | 73.9937 | 143.6375 | 190900 | 164000
SEAFIELD | 0 | 0 | 190000 | Google Maps | 51.9427 | -7.8559 | 38 KV | 160.7738 | 189.5443 | 209962 | 76680
SEALROCK | 0 | 0 | 741000 | Google Maps | 52.6329 | -9.0579 | 110 KV | 75.788 | 204.3085 | 128423 | 153999
SEECON | 0 | 0 |  |  |  |  | 110 kV | 5980.1028 | 393.3669
SEMPERIT | 32 | 64 | 360000 | Google Maps | 53.3327 | -6.3565 | 38 KV | 158.1533 | 7.2026 | 309541 | 232622
SERPENTINE AVENUE | 0 | 0 | 723000 | Google Maps | 53.3306 | -6.2259 | 38 KV | 166.8202 | 1.6903 | 318245 | 232596
SHALLOW | 0 | 0 | 567000 |  |  |  | 110 kV | 5980.1028 | 393.3669
SHANDON | 0 | 0 | 031000 | Google Maps | 52.097 | -7.6307 | 38 KV | 151.7681 | 166.669 | 225358 | 93903
SHANKILL | 32 | 64 | 714000 | Google Maps | 53.9988 | -7.2988 | 110 KV | 123.4827 | 101.1895 | 246031 | 305719
SHANKILL (DART) | 0 | 0 | 557000 | Google Maps | 53.2357 | -6.1176 | 38 KV | 174.2234 | 14.2967 | 325736 | 222218
SHANNON | 32 | 64 | 325000 | Google Maps | 52.7007 | -8.9005 | 38 KV | 66.0372 | 191.5471 | 139172 | 161402
SHANNONBRIDGE | 0 | 0 | 803000 | Google Maps | 53.2725 | -8.039 | 220 KV | 46.3493 | 119.5775 | 197447 | 224653
SHELLYBANKS | 0 | 0 | 804000 | Google Maps | 53.3385 | -6.1883 | 220 KV | 169.3283 | 4.0225 | 320727 | 233534
SHELTON ABBEY | 0 | 0 | 950000 | Google Maps | 52.8129 | -6.1797 | 110 KV | 178.764 | 58.5618 | 322785 | 175060
SHERCOCK | 32 | 64 | 539000 | Google Maps | 53.9867 | -6.9121 | 38 KV | 143.2478 | 84.5479 | 271414 | 304696
SHERIFF STREET | 32 | 64 | 588000 | Google Maps | 53.3507 | -6.2451 | 38 KV | 165.5878 | 1.5004 | 316911 | 234793
SHILLELAGH | 32 | 64 | 708000 | Google Maps | 52.7524 | -6.5329 | 38 KV | 158.8453 | 67.883 | 299112 | 167744
SINGLAND | 32 | 64 | 521000 | Google Maps | 52.6635 | -8.5873 | 110 KV | 69.9564 | 174.0007 | 160313 | 157044
SKIBBEREEN | 16 | 8 | 164000 | Google Maps | 51.5595 | -9.2445 | 38 KV | 195.082 | 283.9277 | 113740 | 34767
SLANE | 32 | 64 | 208000 | Google Maps | 53.7478 | -6.5521 | 38 KV | 153.2163 | 49.921 | 295571 | 278530
SLIABH BAWN | 0 | 0 | 202000 | Google Maps | 53.7479 | -8.0499 | 110 kV | 68.4934 | 127.8581 | 196759 | 277569
SLIEVECALLAN | 0 | 0 | 148000 |  |  |  | 110 KV | 5980.1028 | 393.3669
SLIGO | 32 | 64 | 715000 | Google Maps | 54.2412 | -8.4671 | 110 KV | 107.6393 | 177.4763 | 169593 | 332574
SMEARLA | 32 | 64 | 140000 | Google Maps | 52.4348 | -9.4384 | 38 KV | 105.7781 | 237.0388 | 102221 | 132403
SNOWHILL | 0 | 0 | 611000 | Google Maps | 52.2714 | -7.0329 | 38 KV | 160.7827 | 129.8964 | 266069 | 113688
SNUGSBOROUGH | 0 | 0 | 357000 |  |  |  | 110 KV | 5980.1028 | 393.3669
SOMERSET | 32 | 64 | 716000 | Google Maps | 53.2666 | -8.2307 | 110 KV | 33.6565 | 132.3781 | 184659 | 224020
SONNAGH | 0 | 0 | 088000 | Google Maps | 53.1327 | -8.6373 | 38 KV | 18.2925 | 161.1166 | 157395 | 209286
SORNE HILL | 0 | 64 | 743000 | Google Maps | 55.1314 | -7.3682 | 110 KV | 223.6009 | 212.6337 | 240347 | 431754
SOUTH EAST CARLOW | 0 | 44 |  |  |  |  | 110 KV | 5980.1028 | 393.3669
SOUTH HILL | 0 | 0 | 347000 | Google Maps | 52.6497 | -8.6038 | 38 KV | 71.3357 | 175.6922 | 159187 | 155499
SOUTH KING STREET | 32 | 64 | 241000 | Google Maps | 53.3401 | -6.263 | 38 KV | 164.3715 | 1.0048 | 315746 | 233586
SOUTH NAVAN | 28 | 44 |  | Google Maps | 53.6408 | -6.6613 | 110 kV | 142.8632 | 43.4929 | 288576 | 266473
SOUTHGREEN | 0 | 0 | 135000 |  |  |  | 110 kV | 5980.1028 | 393.3669
SPA ROAD | 32 | 64 | 205000 | Google Maps | 52.3497 | -7.6845 | 38 KV | 125.8416 | 146.434 | 221552 | 122006
SPADDEN | 0 | 0 | 541000 | Google Maps | 54.526 | -8.1911 | 38 KV | 142.3909 | 183.798 | 187675 | 364193
SPIDDAL | 32 | 64 | 443000 | Google Maps | 53.2497 | -9.3034 | 38 KV | 37.9649 | 203.9263 | 113050 | 222907
SPRINGS | 32 | 64 | 585000 | Google Maps | 52.0893 | -7.6415 | 38 KV | 152.1614 | 167.7882 | 224624 | 93046
SRAH | 32 | 64 | 484000 | Google Maps | 53.2871 | -7.5124 | 38 KV | 81.3182 | 84.4284 | 232566 | 226394
SRANANAGH | 0 | 0 | 951000 | Google Maps | 54.1774 | -8.3848 | 220 KV | 101.7445 | 169.0962 | 174922 | 325444
STEPHENSTOWN | 32 | 64 | 730000 | Google Maps | 53.6013 | -6.1896 | 110 KV | 172.2197 | 29.6456 | 319896 | 262780
STEEVENS LANE | 0 | 48 |  | Google Maps | 53.3442 | -6.2909 | 110 KV | 162.5297 | 2.9325 | 313862 | 234001
STICKILLEN | 32 | 64 | 063000 | Google Maps | 53.8541 | -6.5213 | 38 KV | 159.2675 | 60.2937 | 297354 | 290408
STRABANE | 0 | 0 | XXXXXXXX | Google Maps | 54.8565 | -7.4555 |  | 193.5538 | 186.635 | 235020 | 401113
STRADBALLY ROAD | 0 | 0 | 282000 | Google Maps | 52.9998 | -7.0026 | 38 KV | 119.9009 | 62.8895 | 267012 | 194769
STRANORLAR | 32 | 64 | 150000 | Google Maps | 54.8047 | -7.7554 | 38 KV | 180.5645 | 190.8073 | 215780 | 395233
STRATFORD | 32 | 64 | 913000 | Google Maps | 52.9942 | -6.6499 | 110 KV | 142.8619 | 46.686 | 290702 | 194536
STREAMHILL | 0 | 0 | 756000 | Google Maps | 52.2868 | -8.5429 | 38 KV | 111.8887 | 193.9065 | 163000 | 115100
SUTTON | 32 | 64 | 333000 | Google Maps | 53.3914 | -6.1192 | 38 KV | 174.1062 | 10.5124 | 325177 | 239538
SWINFORD | 32 | 64 | 043000 | Google Maps | 53.9448 | -8.9415 | 38 KV | 74.4684 | 190.4993 | 138227 | 299890
SWORDS | 32 | 64 | 066000 | Google Maps | 53.4639 | -6.2198 | 38 KV | 168.0553 | 14.217 | 318281 | 247436
TALBOTS INCH | 32 | 64 | 508000 | Google Maps | 52.6732 | -7.2701 | 38 KV | 119.475 | 100.8318 | 249421 | 158212
TALBOTS INCH/ROSEHILL | 0 | 52 |  |  |  |  | 38 KV | 5980.1028 | 393.3669
TANDRAGEE | 0 | 0 | 963000 | Google Maps | 54.0575 | -6.5884 | 275 KV | 165.4103 | 83.2531 | 292487 | 312957
TANEY | 32 | 64 | 953000 | Google Maps | 53.2886 | -6.2451 | 110 KV | 165.5501 | 5.4334 | 317078 | 227885
TARBERT | 0 | 0 | 805000 | Google Maps | 52.5891 | -9.364 | 220 KV | 88.2147 | 225.2847 | 107604 | 149476
TAURBEG | 0 | 0 | 532000 | Google Maps | 52.255 | -9.135 | 38 KV | 117.7776 | 228.9321 | 122544 | 112025
TAWNAGHMORE | 0 | 64 | 952000 | Google Maps | 54.1931 | -9.2195 | 110 KV | 105.7295 | 217.8262 | 120450 | 327804
TELAYDON | 32 | 64 | 415000 | Google Maps | 54.2583 | -6.9807 | 38 KV | 158.0554 | 113.295 | 266478 | 334856
TEMPLEMORE | 32 | 64 | 057000 | Google Maps | 52.7984 | -7.8264 | 38 KV | 81.4775 | 121.5926 | 211759 | 171907
TEMPLEOGUE | 32 | 64 | 146000 | Google Maps | 53.2963 | -6.3115 | 38 KV | 161.1274 | 6.1997 | 312631 | 228638
TERMONFECKIN ROAD | 32 | 64 | 263000 | Google Maps | 53.7264 | -6.3268 | 38 KV | 166.6479 | 43.612 | 310490 | 276472
THORNSBERRY | 32 | 64 | 717000 | Google Maps | 53.2948 | -7.4696 | 110 KV | 84.1609 | 81.5204 | 235414 | 227275
THURLES | 32 | 64 | 718000 | Google Maps | 52.692 | -7.7645 | 110 KV | 92.6992 | 124.5387 | 215976 | 160078
TIEVEBRACK | 0 | 0 | 818000 |  |  |  | 110 KV | 5980.1028 | 393.3669
TIMOLEAGUE | 32 | 64 | 163000 | Google Maps | 51.672 | -8.7582 | 38 KV | 179.5078 | 251.7831 | 147550 | 46814
TINAHASK | 32 | 64 | 362000 | Google Maps | 52.7863 | -6.1625 | 38 KV | 180.8041 | 61.6106 | 324024 | 172131
TIPPERARY | 32 | 64 | 806000 | Google Maps | 52.4723 | -8.067 | 110 KV | 101.0239 | 155.6836 | 195500 | 135606
TOGHER | 32 | 64 | 336000 | Google Maps | 51.8768 | -8.4953 | 38 KV | 157.5675 | 222.6684 | 165936 | 69452
TONROE | 32 | 20 | 904000 | Google Maps | 53.9098 | -8.5725 | 110 KV | 70.1668 | 166.4378 | 162427 | 295740
TOOMEVARA | 32 | 64 | 385000 | Google Maps | 52.8674 | -8.0308 | 38 KV | 66.2294 | 130.3306 | 197972 | 179574
TOSSY | 0 | 0 | 320000 |  |  |  | 38 KV | 5980.1028 | 393.3669
TOURNAFULLA | 0 | 0 | 086000 | Google Maps | 52.3838 | -9.1814 | 38 KV | 104.7174 | 224.2212 | 119610 | 126412
TRABEG | 16 | 20 | 701000 | Google Maps | 51.8827 | -8.4597 | 110 KV | 157.1837 | 220.5375 | 168395 | 70091
TRALEE | 32 | 64 | 719000 | Google Maps | 52.2892 | -9.6742 | 110 KV | 127.5681 | 258.7403 | 85813 | 116547
TRAMORE | 32 | 64 | 032000 | Google Maps | 52.1639 | -7.1599 | 38 KV | 163.8153 | 144.3557 | 257548 | 101631
TRIEN | 32 | 20 | 720000 | Google Maps | 52.4248 | -9.4264 | 110 KV | 106.4247 | 236.8034 | 103018 | 131271
TRILLICK | 32 | 64 | 721000 | Google Maps | 55.1128 | -7.4188 | 110 KV | 220.4201 | 211.8638 | 237141 | 429660
TRIM | 32 | 64 | 196000 | Google Maps | 53.5466 | -6.7953 | 38 KV | 131.8119 | 43.1544 | 279906 | 255838
TRIMMS LANE | 32 | 64 | 427000 | Google Maps | 53.2669 | -9.0676 | 38 KV | 22.171 | 188.1024 | 128812 | 224560
TRINITY | 32 | 64 | 494000 | Google Maps | 53.3425 | -6.2492 | 110 KV | 165.2945 | 0.58187 | 316644 | 233884
TUAM NORTH | 32 | 20 | 253000 | Google Maps | 53.5298 | -8.872 | 38 KV | 28.5488 | 175.6709 | 142222 | 253649
TUAM SOUTH | 32 | 64 | 040000 | Google Maps | 53.5194 | -8.858 | 38 KV | 27.1574 | 174.6302 | 143136 | 252474
TUBBERCURRY | 32 | 64 | 355000 | Google Maps | 54.0476 | -8.7273 | 38 KV | 84.6607 | 181.8197 | 152409 | 311173
TULLA | 32 | 64 | 182000 | Google Maps | 52.861 | -8.7483 | 38 KV | 47.2991 | 175.6317 | 149648 | 179117
TULLABRACK | 32 | 64 | 722000 | Google Maps | 52.6731 | -9.4791 | 110 KV | 84.413 | 229.1093 | 99995 | 158974
TULLAMORE | 0 | 0 | 053000 | Google Maps | 53.2776 | -7.4847 | 38 KV | 83.1781 | 82.6695 | 234425 | 225352
TULLOW | 32 | 64 | 293000 | Google Maps | 52.8099 | -6.7275 | 38 KV | 144.3074 | 66.9064 | 285860 | 173937
TULLYLEASE | 0 | 0 | 435000 |  |  |  | 38 kV | 5980.1028 | 393.3669
TULLYNAMALRA | 32 | 64 | 466000 | Google Maps | 54.058 | -6.8158 | 38 KV | 152.8312 | 88.5347 | 277599 | 312733
TURLOUGH HILL | 0 | 0 | 807000 | Google Maps | 53.033 | -6.3965 | 220 KV | 158.4784 | 35.2888 | 307625 | 199207
TURLOUGH ROAD | 32 | 64 | 042000 | Google Maps | 53.8692 | -9.2837 | 38 KV | 74.2293 | 209.4491 | 115605 | 291832
TURSILLAGH | 0 | 0 | 698000 | Google Maps | 52.3147 | -9.6029 | 38 KV | 122.7571 | 253.1161 | 90736 | 119275
TYCOR | 32 | 20 | 286000 | Google Maps | 52.257 | -7.1403 | 38 KV | 156.8904 | 134.4411 | 258754 | 111999
TYMON | 32 | 64 | 424000 | Google Maps | 53.3002 | -6.3429 | 38 KV | 159.0384 | 7.5219 | 310529 | 229021
TYNAGH | 0 | 0 | 985000 | Google Maps | 53.1668 | -8.3821 | 220 KV | 27.0283 | 143.6653 | 174493 | 212965
TYONE | 0 | 0 | 058000 | Google Maps | 52.8568 | -8.1926 | 38 KV | 59.98 | 140.7773 | 187079 | 178408
UGGOOL | 0 | 0 | 861000 |  |  |  | 110 KV | 5980.1028 | 393.3669
UNIDARE | 32 | 64 | 245000 | Google Maps | 53.3975 | -6.2969 | 38 KV | 162.3727 | 7.4249 | 313335 | 239919
URLINGFORD | 0 | 60 | 910000 | Google Maps | 52.715 | -7.5885 | 38 kV | 99.6433 | 114.3788 | 227600 | 161600
VACORNEEN | 0 | 0 | 525000 | Google Maps | 51.823 | -9.2469 | 38 kV | 166.333 | 263.995 | 114080 | 64090
VIRGINIA | 32 | 64 | 452000 | Google Maps | 53.8181 | -7.0474 | 38 KV | 126.2354 | 75.2685 | 262771 | 285802
WALLINGSTOWN | 0 | 0 | 448000 |  |  |  | 38 KV | 5980.1028 | 393.3669
WALTERSTOWN | 0 | 44 |  | Google Maps | 53.3933 | -6.4914 | 110 KV | 149.4743 | 17.3362 | 300396 | 239168
WATERFORD | 32 | 64 | 808000 | Google Maps | 52.2633 | -7.1246 | 110 KV | 157.1096 | 133.3484 | 259819 | 112703
WATERFORD IND EST | 32 | 64 | 348000 | Google Maps | 52.2475 | -7.1509 | 38 KV | 157.1909 | 135.7136 | 258044 | 110928
WATLING STREET | 32 | 64 | 361000 | Google Maps | 53.3449 | -6.2853 | 38 KV | 162.9066 | 2.5807 | 314252 | 234089
WEST PORTLAOISE | 0 | 44 |  |  |  |  | 110 KV | 5980.1028 | 393.3669
WESTPORT | 32 | 64 | 116000 | Google Maps | 53.804 | -9.4998 | 38 KV | 76.5638 | 221.5537 | 101237 | 284852
WEXFORD | 32 | 64 | 742000 | Google Maps | 52.3403 | -6.539 | 110 KV | 181.2667 | 112.6905 | 299627 | 121918
WHITEBANK | 0 | 0 | 472000 | Google Maps | 53.3391 | -6.2009 | 110 KV | 168.4929 | 3.1862 | 319886 | 233573
WHITECHURCH | 32 | 64 | 167000 | Google Maps | 51.9833 | -8.5107 | 38 KV | 145.678 | 214.771 | 164964 | 81321
WHITEGATE | 0 | 0 | 914000 | Google Maps | 51.8187 | -8.2389 | 110 KV | 166.6046 | 216.2461 | 183575 | 62903
WHITEHALL | 32 | 64 | 183000 | Google Maps | 53.3766 | -6.2511 | 38 KV | 165.2924 | 4.3712 | 316444 | 237669
WHITESTOWN | 32 | 64 | 423000 | Google Maps | 53.2827 | -6.3841 | 38 KV | 156.3249 | 10.8907 | 307826 | 227008
WICKLOW | 0 | 0 | 003000 |  |  |  | 38 KV | 5980.1028 | 393.3669
WILTON | 0 | 44 |  | Google Maps | 51.8782 | -8.5085 | 110 KV | 157.3167 | 223.1373 | 165037 | 69644
WINDSOR | 32 | 64 | 608000 | Google Maps | 53.8664 | -9.2691 | 38 KV | 73.4904 | 208.4432 | 116556 | 291500
WOLFE TONE STREET | 32 | 64 | 769000 | Google Maps | 53.3497 | -6.268 | 110 KV | 164.0662 | 1.8831 | 315390 | 234648
WOODFORD | 32 | 64 | 276000 | Google Maps | 52.0557 | -9.458 | 38 KV | 145.2414 | 259.6408 | 100038 | 90246
WOODHOUSE | 0 | 0 | 876000 |  |  |  | 110 KV | 5980.1028 | 393.3669
WOODLAND | 0 | 0 | 810000 | Google Maps | 53.4749 | -6.5696 | 400 KV | 145.1921 | 26.2744 | 295024 | 248139
YELLOWMEADOWS | 0 | 44 | 853000 | Google Maps | 53.3308 | -6.3822 | 110 KV | 156.4432 | 8.9414 | 307819 | 232367
Note on F15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on rough area for site selection
Note on F85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on rough area for site selection
Note on A112: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Future Customer Station - BAXTER
Note on A268: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AKA Loughteeog
Note on F282: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on rough area for site selection
Note on F328: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on rough area for site selection
Note on F337: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on rough area for site selection
Note on A346: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Barrysparks
Note on F362: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on rough area for site selection
Note on F363: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on rough area for site selection
Note on F365: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on rough area for site selection
Note on F380: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on rough area for site selection
Note on F514: Midway between Killinick/Rosslare, no site selected as of yet.
Note on A621: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AKA Meenbog
Note on A675: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No site data available at this time
Note on A676: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No site data available at this time
Note on A677: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No site data available at this time
Note on F678: Approximate site search location according to I_CL0280
Note on A680: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No site data available at this time
Note on A682: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No site data available at this time
Note on A691: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No further site detail available
Note on A692: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No further site detail available
Note on A735: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: (Lineschool)
Note on A815: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No site data available
Note on F827: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rough Site Search location
Note on A838: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New future station - no further data
Note on A893: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: FUTURE STATION

## Connection methods (hidden)
Station Name | Connection Method Identifier | Substation Voltage Level | Transformer Type | ConnectionMethodID | Node Name | Element Name | Element_ID | Vn1 [kV] | Vn2 [kV] | Present in demand results? | Present in generation results? | Comment | Gen Result Sheet | Connection Configuration | Consumer type
ABBEYFEALE | ABBEYFEALE-T42_5_MVA | 38 KV | 38 kV - MV | 1 | ABBEYFEALE | T42_5_MVA | 3809 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
ABBEYFEALE | ABBEYFEALE_T421-T421_10_MVA | 38 KV | 38 kV - MV | 1 | ABBEYFEALE_T421 | T421_10_MVA | 3810 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
ABBEYLAND | ABBEYLANDS-T42_10_MVA_ABBEYLANDS | 38 KV | 38 kV - MV | 1 | ABBEYLANDS | T42_10_MVA_ABBEYLANDS | 3449 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
ABBEYLEIX | ABBEYLEIX-T422_5_MVA | 38 KV | 38 kV - MV | 1 | ABBEYLEIX | T422_5_MVA | 4846 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
ACADEMY STREET | ACADEMY_STREET-T422_5_MVA_ACADEMY | 38 KV | 38 kV - MV | 1 | ACADEMY_STREET | T422_5_MVA_ACADEMY | 4082 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
ACADEMY STREET | ACADEMY_STREET_T44-T44_10_MVA_ACADEMY | 38 KV | 38 kV - MV | 1 | ACADEMY_STREET_T44 | T44_10_MVA_ACADEMY | 4080 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
ACHILL | ACHILL-T422_5_MVA | 38 KV | 38 kV - MV | 1 | ACHILL | T422_5_MVA | 3925 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
ADAMSTOWN | ADAMSTOWN-T122_20MVA | 110 KV | 110 kV - MV | 1 | ADAMSTOWN | T122_20MVA | 7960 | 110 | 21.4 | 32 | 64 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 20 MVA | Mixed Gen/Demand
AGANNYGAL | AGANNYGAL | 110 KV |  |  | AGANNYGAL |  |  |  |  | 0 | 0 | 110 kV switching station only
AGHADA | AGHADA | 220 KV |  |  | AGHADA |  |  |  |  | 0 | 0 | 220/110 + gen only
AGHADA 110KV | AGHADA 110KV | 110 KV |  |  | AGHADA 110KV |  |  |  |  | 0 | 0 | 220/110 + gen only
AGHAGAD | AGHAGAD-T42_5_MVA AGHAGAD | 38 KV | 38 kV - MV | 1 | AGHAGAD | T42_5_MVA AGHAGAD | 4095 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
AGHAMORE | AGHAMORE-T42_5_MVA | 38 KV | 38 kV - MV | 1 | AGHAMORE | T42_5_MVA | 2943 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
AHANE | AHANE_1A_110-T102_15MVA | 110 KV | 110 kV - MV | 1 | AHANE_1A_110 | T102_15MVA | 10206 | 110 | 10.7 | 0 | 64 | DSO Station - should be included in Model. Kilonan to Nenagh 110 kV feeder and Kilonan to Ahane 110 kV Feeder are DSO controlled | Mixed-Standalone-110-MV | 110/10 kV - 1 x 15 MVA | Mixed Gen/Demand
AIRTON | AIRTON | 110 KV | 110 kV - MV |  | AIRTON |  |  |  |  | 0 | 0 | Customer Station - Amazon
ALLENWOOD | Allenwood_38-T422_15_MVA | 38 KV | 38 kV - MV | 1 | Allenwood_38-T422_15_MVA | T422_15_MVA | 12898 | 41.6 | 21.4 |  | 0 |  |  | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
ANALOG | ANALOG | 38 KV |  |  | ANALOG |  |  |  |  | 0 | 0 | Customer Station - Analog Devices
ANNABELLA | ANNABELLA | 38 KV |  |  | ANNABELLA |  |  |  |  | 0 | 0 | Unsure - No SCADA but Fairly sure this is dairygold
ANNER | ANNER | 110 KV |  |  | ANNER |  |  |  |  | 0 | 0 | TSO-Customer station
ARDFINNAN | ARDFINNAN-T42_5_MVA | 38 KV | 38 kV - MV | 1 | ARDFINNAN | T42_5_MVA | 3716 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
ARDFINNAN | ARDFINNAN_T421-T421_5_MVA | 38 KV | 38 kV - MV | 1 | ARDFINNAN_T421 | T421_5_MVA | 3717 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
ARDGEEHA | ARDGEEHA-T42_10MVA | 38 KV | 38 kV - MV | 1 | ARDGEEHA | T42_10MVA | 3577 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
ARDMORE | ARDMORE | 0 |  |  | ARDMORE |  |  |  |  | 0 | 0 | Unsure
ARDNACRUSHA | ARDNACRUSHA_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | ARDNACRUSHA_110 | T142_63MVA | 2773 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
ARDNAGAPPARY | ARDNAGAPPARY_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | ARDNAGAPPARY_110 | T141_31_5MVA | 3127 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
ARDNAREE | ARDNAREE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | ARDNAREE | T42_10_MVA | 4240 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
ARDNAREE | ARDNAREE_T421-T421_10_MVA | 38 KV | 38 kV - MV | 1 | ARDNAREE_T421 | T421_10_MVA | 4241 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
ARIGNA | Arigna_110-T121_15MVA | 110 KV | 110 kV - MV | 1 | Arigna_110 | T121_15MVA | 10188 | 110 | 21.4 | 0 | 64 | DSO Station - should be included in Model | Mixed-Standalone-110-MV | 110/20 kV - 1 x 15 MVA | Mixed Gen/Demand
ARKLOW | ARKLOW 110-T142_63MVA | 220 KV | 110 - 38 kV | 1 | ARKLOW 110 | T142_63MVA | 2593 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
ARKLOW | ARKLOW_T143-T143_63_MVA | 220 KV | 110 - 38 kV | 2 | ARKLOW_T143 | T143_63_MVA | 13318 | 110 | 41.6 |  | 56 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
ARKLOW | ARKLOW 110-T102_20MVA | 220 KV | 110 kV - MV | 1 | ARKLOW 110 | T102_20MVA | 5209 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
ARKLOW BANKS | ARKLOW BANKS | 38 KV |  |  | ARKLOW BANKS |  |  |  |  | 0 | 0 | Unsure - gen only
ARTANE | ARTANE-T102_20MVA | 110 KV | 110 kV - MV | 1 | ARTANE | T102_20MVA | 8247 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
ARTHURSTOWN | ARTHURSTOWN | 38 KV |  |  | ARTHURSTOWN |  |  |  |  | 0 | 0 | Unsure - gen only
ARVA | ARVA | 110 KV |  |  | ARVA |  |  |  |  | 0 | 0 | 110 kV switching station only
ASHBOURNE | ASHBOURNE | 38 KV | 38 kV - MV | 1 | ASHBOURNE | T422_10_MVA | 3551 | 41.6 | 21.4 | 96 | 64 |  | Mixed-Uneven-38-MV | 38/20 kV (1x15MVA) + (1x10MVA) | Mixed Gen/Demand
ASHE ROAD | ASHE ROAD | 38 KV |  |  | ASHE ROAD |  |  |  |  | 0 | 0 | Retired per central mapping FL list
ASKEATON | ASKEATON | 38 KV |  |  | ASKEATON |  |  |  |  | 0 | 0 | Customer Station - Pfizer
ATHBOY | ATHBOY-T42_5_MVA_ATHBOY | 38 KV | 38 kV - MV | 1 | ATHBOY | T42_5_MVA_ATHBOY | 3112 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
ATHBOY | ATHBOY_T423-T423_5_MVA_ATHBOY | 38 KV | 38 kV - MV | 1 | ATHBOY_T423 | T423_5_MVA_ATHBOY | 3113 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
ATHEA | ATHEA | 110 KV |  |  | ATHEA |  |  |  |  | 0 | 0 | TSO-Customer station
ATHENRY | ATHENRY-T42_5_MVA_ATHENRY | 38 KV | 38 kV - MV | 1 | ATHENRY | T42_5_MVA_ATHENRY | 2983 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
ATHENRY | ATHENRY_T423-T423_10_MVA | 38 KV | 38 kV - MV | 1 | ATHENRY_T423 | T423_10_MVA | 4192 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
ATHGARVAN | ATHGARVAN-T44_15_MVA | 38 KV | 38 kV - MV | 1 | ATHGARVAN | T44_15_MVA | 3749 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
ATHLONE | ATHLONE_38-T42_10_MVA | 110 KV | 38 kV - MV | 1 | ATHLONE_38 | T42_10_MVA | 3691 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
ATHLONE | ATHLONE_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | ATHLONE_110 | T142_63MVA | 2814 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
ATHY | ATHY_110-T101_20MVA | 110 KV | 110 kV - MV | 1 | ATHY_110 | T101_20MVA | 9078 | 110 | 10.7 | 32 | 12 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
ATHY | ATHY_110-T121_31.5_MVA | 110 KV | 110 kV - MV | 1 | ATHY_110 | T121_31.5_MVA | 13346 | 110 | 21.4 |  | 52 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
AUGHINISH | AUGHINISH | 110 KV |  |  | AUGHINISH |  |  |  |  | 0 | 0 | 110 kV switching station only
AVOCA | AVOCA | 38 KV |  |  | AVOCA |  |  |  |  | 0 | 0 | Retired per central mapping FL list
AVONCORE | AVONCORE | 38 KV |  |  | AVONCORE |  |  |  |  | 0 | 0 | Retired per central mapping FL list
BAGENALSTOWN | BAGENALSTOWN-T422_10_MVA | 38 KV | 38 kV - MV | 1 | BAGENALSTOWN | T422_10_MVA | 3741 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
BAILIEBORO | BAILIEBORO-T42_5_MVA_BAILIEBORO | 38 KV | 38 kV - MV | 1 | BAILIEBORO | T42_5_MVA_BAILIEBORO | 2978 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BAILIEBORO | BAILIEBORO-T423_15_MVA_BAILIEBORO | 38 KV | 38 kV - MV | 1 | BAILIEBORO | T423_15_MVA_BAILIEBORO | 2979 | 41.6 | 21.4 | 0 | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 15 MVA (Gen only) | Gen Only
BALBRIGGAN | BALBRIGGAN-T42_10_MVA_BALBRIGGAN | 38 KV | 38 kV - MV | 1 | BALBRIGGAN | T42_10_MVA_BALBRIGGAN | 4106 | 41.6 | 10.7 | 32 | 12 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BALGADDY | BALGADDY-T42_10MVA | 38 KV | 38 kV - MV | 1 | BALGADDY | T42_10MVA | 4075 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BALGRIFFIN | BALGRIFFIN | 220 kV |  |  | BALGRIFFIN |  |  |  |  | 0 | 0 | Unsure
BALLAGHADERREEN | Ballaghaderreen-T42_5_MVA BALLAGHADERE | 38 KV | 38 kV - MV | 1 | Ballaghaderreen | T42_5_MVA BALLAGHADERE | 3821 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BALLAGHADERREEN | Ballaghaderreen-T42_15_MVA | 38 KV | 38 kV - MV | 1 | Ballaghaderreen | T42_15_MVA | 12901 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
BALLINACURRA | BALLINACURRA | 38 KV | 38 kV - MV | 1 | BALLINACURRA | T41_5_MVA | 2947 | 41.6 | 10.7 | 96 | 64 |  | Mixed-Uneven-38-MV | 38/10 kV (1x10MVA) + (1x5MVA) | Mixed Gen/Demand
BALLINASLOE | BALLINASLOE-T42_5_MVA BALLINASLOE | 38 KV | 38 kV - MV | 1 | BALLINASLOE | T42_5_MVA BALLINASLOE | 2903 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BALLINCLEA | BALLINCLEA-T41_10_MVA | 38 KV | 38 kV - MV | 1 | BALLINCLEA | T41_10_MVA | 3751 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
BALLINCOLLIG | BALLINCOLLIG-T42_10_MVA | 38 KV | 38 kV - MV | 1 | BALLINCOLLIG | T42_10_MVA | 8674 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BALLINCOLLIG HILL | BALLINCOLLIG HILL | 38 KV |  |  | BALLINCOLLIG HILL |  |  |  |  | 0 | 0 | Unsure - I think this is Generation
BALLINDERRY | BALLINDERRY-T41_10_MVA | 38 KV | 38 kV - MV | 1 | BALLINDERRY | T41_10_MVA | 3705 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
BALLINDERRY | BALLINDERRY_T422-T422_10_MVA | 38 KV | 38 kV - MV | 1 | BALLINDERRY_T422 | T422_10_MVA | 3706 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
BALLINEEN | BALLINEEN | 38 KV |  |  | BALLINEEN |  |  |  |  | 0 | 0 | Customer Station - Carbury Group
BALLINROBE | BALLINROBE-T422_10_MVA BALLINROBE | 38 KV | 38 kV - MV | 1 | BALLINROBE | T422_10_MVA BALLINROBE | 3378 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
BALLINVALLY | BALLINVALLY-T421_45MVA | 38 KV | 38 kV - MV | 1 | BALLINVALLY | T421_45MVA | 3774 | 41.6 | 21.4 | 0 | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 45 MVA (Gen only) | Gen Only
BALLYARD | BALLYARD-T42_5_MVA BALLYARD | 38 KV | 38 kV - MV | 1 | BALLYARD | T42_5_MVA BALLYARD | 3461 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BALLYARD | BALLYARD-T42_15_MVA | 38 KV | 38 kV - MV | 1 | BALLYARD | T42_15_MVA | 12885 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
BALLYBAILIE | BALLYBAILIE-T41_5_MVA-BALLYBAILIE | 38 KV | 38 kV - MV | 1 | BALLYBAILIE | T41_5_MVA-BALLYBAILIE | 3445 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
BALLYBAY | BALLYBAY-T42_10_MVA_BALLYBAY | 38 KV | 38 kV - MV | 1 | BALLYBAY | T42_10_MVA_BALLYBAY | 4070 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BALLYBAY | BALLYBAY-T41_15_MVA | 38 KV | 38 kV - MV | 1 | BALLYBAY | T41_15_MVA | 12869 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
BALLYBEG | BALLYBEG_110-T101_20MVA | 110 KV | 110 kV - MV | 1 | BALLYBEG_110 | T101_20MVA | 9100 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
BALLYBEGGAN | BALLYBEGGAN-T44_10_MVA | 38 KV | 38 kV - MV | 1 | BALLYBEGGAN | T44_10_MVA | 3867 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BALLYBODEN | BALLYBODEN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | BALLYBODEN | T42_10_MVA | 3178 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BALLYBRIT | BALLYBRIT | 38 KV |  |  | BALLYBRIT |  |  |  |  | 0 | 0 | Customer Station - Boston Scientific
BALLYBUNION | BALLYBUNION-T422_5_MVA BALLYBUNION | 38 KV | 38 kV - MV | 1 | BALLYBUNION | T422_5_MVA BALLYBUNION | 3604 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
BALLYBUNION | BALLYBUNION-T424_10_MVA | 38 KV | 38 kV - MV | 2 | BALLYBUNION | T424_10_MVA | 3605 | 41.6 | 21.4 | 0 | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 10 MVA (Gen only) | Gen Only
BALLYCADDEN | BALLYCADDEN | 110 kV |  |  | BALLYCADDEN |  |  |  |  | 0 | 0 | Unsure
BALLYCONNELL | BALLYCONNELL-T422_5MVA | 38 KV | 38 kV - MV | 1 | BALLYCONNELL | T422_5MVA | 4022 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
BALLYCONRA | BALLYCONRA-T423_10_MVA | 38 KV | 38 kV - MV | 1 | BALLYCONRA | T423_10_MVA | 3892 | 41.6 | 21.4 | 0 | 64 | Warning - Ballyconra has an ESB owned T423 10 MVA which feeds lisdoney Windfarm. Customer station for T41 and T42 to Glanbia | Generation-Standalone-38-MV | 38/20 kV - 1 x 10 MVA (Gen only) | Gen Only
BALLYCOOLIN | BALLYCOOLIN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | BALLYCOOLIN | T42_10_MVA | 3950 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Three-38-MV | 38/10 kV - 3 x 10 MVA | Mixed Gen/Demand
BALLYCROSSAUN | Ballycrossaun-T422_5_MVA | 38 KV | 38 kV - MV | 1 | Ballycrossaun | T422_5_MVA | 3406 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
BALLYCUMMIN | Ballycummin_110-T142_63_MVA | 110 kV | 110 - 38 kV | 1 | Ballycummin_110 | T142_63_MVA | 13101 | 110 | 41.6 | 0 | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
BALLYCUMMIN | Ballycummin_38-T422_15_MVA | 110 kV | 38 kV - MV | 1 | Ballycummin_38 | T422_15_MVA | 13099 | 41.6 | 21.4 |  | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
BALLYDEHOB | BALLYDEHOB-T421_5_MVA | 38 KV | 38 kV - MV | 1 | BALLYDEHOB | T421_5_MVA | 3976 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
BALLYDINE | BALLYDINE_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | BALLYDINE_110 | T141_31_5MVA | 3100 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
BALLYDOORLIS | BALLYDOORLIS | 38 KV |  |  | BALLYDOORLIS |  |  |  |  | 0 | 0 | Generation station - but customer owned T421. OK - keep as removed from Capacity workbooks
BALLYGAR | BALLYGAR-T42_5_MVA | 38 KV | 38 kV - MV | 1 | BALLYGAR | T42_5_MVA | 3531 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BALLYGAR | BALLYGAR-T41_10_MVA | 38 KV | 38 kV - MV | 1 | BALLYGAR | T41_10_MVA | 12056 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BALLYHALE | BALLYHALE-T42_5_MVA | 38 KV | 38 kV - MV | 1 | BALLYHALE | T42_5_MVA | 2758 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BALLYHALE | BALLYHALE-T422_10_MVA | 38 KV | 38 kV - MV | 1 | BALLYHALE | T422_10_MVA | 13314 | 41.6 | 21.4 | 0 | 52 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 10 MVA (Gen only) | Gen Only
BALLYHAUNIS | BALLYHAUNIS-T42_5_MVA | 38 KV | 38 kV - MV | 1 | BALLYHAUNIS | T42_5_MVA | 3611 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BALLYHAUNIS | BALLYHAUNIS-T42_15_MVA | 38 KV | 38 kV - MV | 1 | BALLYHAUNIS | T42_15_MVA | 12067 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
BALLYJAMESDUFF | Ballyjamesduff-T42_10_MVA | 38 KV | 38 kV - MV | 1 | Ballyjamesduff | T42_10_MVA | 2981 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BALLYKEERAN | BALLYKEERAN | 38 KV |  |  | BALLYKEERAN |  |  |  |  | 0 | 0 | 38 kV Ballykeernan switching station. OK - leave as removed
BALLYKETT | BALLYKETT | 38 KV |  |  | BALLYKETT |  |  |  |  | 0 | 0 | Generation station - but customer owned T421. OK - keep as removed from Capacity workbooks
BALLYLICKEY | BALLYLICKEY_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | BALLYLICKEY_110 | T142_63MVA | 2661 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 63 MVA | Mixed Gen/Demand
BALLYLICKEY | BALLYLICKEY-T421_10_MVA | 110 KV | 38 kV - MV | 1 | BALLYLICKEY | T421_10_MVA | 3659 | 41.6 | 21.4 | 0 | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 10 MVA (Gen only) | Gen Only
BALLYLINAN ROAD | BALLYLINAN ROAD | 38 KV |  |  | BALLYLINAN ROAD |  |  |  |  | 0 | 0 | Retired per central mapping FL list
BALLYMACARRY | BALLYMACARRY-T421_5_MVA | 38 KV | 38 kV - MV | 1 | BALLYMACARRY | T421_5_MVA | 4056 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
BALLYMAHON | BALLYMAHON-T42_5_MVA | 38 KV | 38 kV - MV | 1 | BALLYMAHON | T42_5_MVA | 4169 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BALLYMAKENNY | Ballymakenny_38-T422_15_MVA | 38 KV | 38 kV - MV | 1 | Ballymakenny_38 | T422_15_MVA | 12926 | 41.6 | 21.4 |  | 52 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
BALLYMOTE | BALLYMOTE-T41_5_MVA | 38 KV | 38 kV - MV | 1 | BALLYMOTE | T41_5_MVA | 3926 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
BALLYMOUNT | BALLYMOUNT-T42_10_MVA | 38 KV | 38 kV - MV | 1 | BALLYMOUNT | T42_10_MVA | 3825 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BALLYMUN | BALLYMUN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | BALLYMUN | T42_10_MVA | 4259 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BALLYNAHULLA | BALLYNAHULLA | 110 KV |  |  | BALLYNAHULLA |  |  |  |  | 0 | 0 | OK - fully TSO station
BALLYRAGGET | BALLYRAGGET-T422_5_MVA | 38 KV | 38 kV - MV | 1 | BALLYRAGGET | T422_5_MVA | 8868 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
BALLYRAGGET | BALLYRAGGET_110-T141_31.5 MVA | 38 KV | 110 - 38 kV | 1 | BALLYRAGGET_110 | T141_31.5 MVA | 5819 | 110 | 41.6 | 32 | 8 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
BALLYRAGGET | BALLYRAGGET_110-T142_63_MVA | 38 KV | 110 - 38 kV | 1 | BALLYRAGGET_110 | T142_63_MVA | 13305 | 110 | 41.6 |  | 56 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
BALLYRAINE | BALLYRAINE-T42_5_MVA | 38 KV | 38 kV - MV | 1 | BALLYRAINE | T42_5_MVA | 3839 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BALLYRICKARD | BALLYRICKARD-T42_10_MVA | 38 KV | 38 kV - MV | 1 | BALLYRICKARD | T42_10_MVA | 3103 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BALLYSHANNON | BALLYSHANNON-T42_5_MVA | 38 KV | 38 kV - MV | 1 | BALLYSHANNON | T42_5_MVA | 2739 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BALLYTIVNAN | BALLYTIVNAN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | BALLYTIVNAN | T42_10_MVA | 3847 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BALLYVOUSKILL | BALLYVOUSKILL | 220 KV |  |  | BALLYVOUSKILL |  |  |  |  | 0 | 0 | OK - fully TSO station
BALLYWATER | BALLYWATER | 110 KV |  |  | BALLYWATER |  |  |  |  | 0 | 0 | OK - Fully customer 110 kV station fed from Crane
BALTINGLASS | BALTINGLASS-T422_5MVA BALTINGLASS | 38 KV | 38 kV - MV | 1 | BALTINGLASS | T422_5MVA BALTINGLASS | 3487 | 41.6 | 21.4 | 4 | 4 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
BALTINGLASS | BALTINGLASS-T422_10MVA BALTINGLASS | 38 KV | 38 kV - MV | 1 | BALTINGLASS | T422_10MVA BALTINGLASS | 13343 | 41.6 | 21.4 | 44 | 60 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
BALTRASNA | BALTRASNA-T122_20MVA | 110 KV | 110 kV - MV | 1 | BALTRASNA | T122_20MVA | 8224 | 110 | 21.4 | 32 | 64 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 20 MVA | Mixed Gen/Demand
BANAGHER | BANAGHER-T42_5_MVA | 38 KV | 38 kV - MV | 1 | BANAGHER | T42_5_MVA | 3505 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BANCROFT | BANCROFT | 110 KV |  |  | BANCROFT |  |  |  |  | 0 | 0 | Customer station - Amazon
BANDON | BANDON_38 | 110 KV | 38 kV - MV | 1 | BANDON_38 | T42_10_MVA | 3692 | 41.6 | 10.7 | 64 | 64 |  | Mixed-Uneven-110-MV-38 | 38/10 kV (1x10MVA) + 110/10 kV (1x20MVA) | Mixed Gen/Demand
BANDON | BANDON_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | BANDON_110 | T142_31_5MVA | 4835 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
BANDON | BANDON_110-T101_20MVA | 110 KV | 110 kV - MV | 1 | BANDON_110-T101_20MVA | T101_20MVA | 5030 | 110 | 10.7 | 32 | 0
BANGOR ERRIS | BANGOR ERRIS-T421_5_MVA | 38 KV | 38 kV - MV | 1 | BANGOR ERRIS | T421_5_MVA | 3286 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
BANOGE | BANOGE_110-T122_20MVA | 110 KV | 110 kV - MV | 1 | BANOGE_110 | T122_20MVA | 9048 | 110 | 21.4 | 32 | 64 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 20 MVA | Mixed Gen/Demand
BANTRY | BANTRY-T42_5_MVA BANTRY | 38 KV | 38 kV - MV | 1 | BANTRY | T42_5_MVA BANTRY | 2799 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BARNAHELY_A | BARNHELY_A_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | BARNHELY_A_110 | T142_31_5MVA | 2831 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
BARNAHELY_A | BARNHELY_A_110-T122_20MVA | 110 KV | 110 kV - MV | 1 | BARNHELY_A_110 | T122_20MVA | 4830 | 110 | 21.4 | 32 | 64 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 20 MVA | Mixed Gen/Demand
BARNAHELY_B | BARNHELY_B_110-T124_20MVA | 110 KV | 110 kV - MV | 1 | BARNHELY_B_110 | T124_20MVA | 4832 | 110 | 21.4 | 32 | 64 |  | Mixed-Standalone-110-MV | 110/20 kV - 1 x 20 MVA | Mixed Gen/Demand
BARNAKYLE | BARNAKYLE | 110 KV |  |  | BARNAKYLE |  |  |  |  | 0 | 0 | Customer Station - TSO - Google
BARNTOWN | BARNTOWN | 38 KV |  |  | BARNTOWN |  |  |  |  | 0 | 0 | OK - BARNtown is assumed retired and affixed to Banoge.
BARODA | BARODA_110-T103_20MVA | 110 KV | 110 kV - MV | 1 | BARODA_110 | T103_20MVA | 9344 | 110 | 10.7 | 20 | 44 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
BARRYMORE | BARYMORE_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | BARYMORE_110 | T141_31_5MVA | 2821 | 110 | 41.6 | 32 | 12 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
BARRYMORE | BARYMORE_110-T141_63_MVA | 110 KV | 110 - 38 kV | 1 | BARYMORE_110 | T141_63_MVA | 13336 | 110 | 41.6 |  | 52 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 63 MVA | Mixed Gen/Demand
BATTER LANE | Batter Lane_110-T101_31.5_MVA | 110 KV | 110 kV - MV | 1 | Batter Lane_110 | T101_31.5_MVA | 9362 | 110 | 21.4 | 16 | 56 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
NEW CASTLEBAR | Baxter Station_38-T422_15_MVA | 38 KV | 38 kV - MV | 1 | Baxter Station_38 | T422_15_MVA | 12176 | 41.6 | 21.4 |  | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
BAYSIDE | BAYSIDE | 38 KV |  |  | BAYSIDE |  |  |  |  | 0 | 0 | Customer station - Bayside CIE Dart
BEALISTOWN | BEALISTOWN-T422_5_MVA | 38 KV | 38 kV - MV | 1 | BEALISTOWN | T422_5_MVA | 3620 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
BEALNABLATH | BEAL NA Blath-T421_10_MVA | 38 KV | 38 kV - MV | 2 | BEAL NA Blath-T421_10_MVA | T421_10_MVA | 8876 | 41.6 | 21.4 | 64 | 0
BEALNABLATH | BEAL NA Blath | 38 KV | 38 kV - MV | 1 | BEAL NA Blath | T422_5_MVA | 3372 | 41.6 | 21.4 | 96 | 64 |  | Mixed-Uneven-38-MV | 38/20 kV (1x5MVA) + (1x10MVA) | Mixed Gen/Demand
BEAM HILL | BEAM HILL | 38 KV |  |  | BEAM HILL |  |  |  |  | 0 | 0 | OK - Beam Hil WF transformer is IPP owned per SCADA.
BEDFORD ROW | BEDFORD ROWA-T44_15_MVA | 38 KV | 38 kV - MV | 1 | BEDFORD ROWA | T44_15_MVA | 4175 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
BEDFORD ROW | BEDFORD ROWB-T42_15_MVA BEDFORD ROWB | 38 KV | 38 kV - MV | 2 | BEDFORD ROWB | T42_15_MVA BEDFORD ROWB | 4123 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
BEENAGEEHA | BEENAGEEHA | 38 kV |  |  | BEENAGEEHA |  |  |  |  | 0 | 0 | Unsure, appears to connect at 38 kV to KilFlynn per SLD. Note Kilflynn SCADA sows MV feeder to Beenageehha
BELFIELD | BELFIELD-T42_10_MVA | 38 KV | 38 kV - MV | 1 | BELFIELD | T42_10_MVA | 3512 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BELGARD | BELGARD-T42_10_MVA | 38 KV | 38 kV - MV | 1 | BELGARD | T42_10_MVA | 3544 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BELLACORRICK | BELLACORRICK_110-T122_10MVA | 110 KV | 110 kV - MV | 1 | BELLACORRICK_110 | T122_10MVA | 4798 | 110 | 21.4 |  | 20 |  | Mixed-Standalone-110-MV | 110/20 kV - 1 x 10 MVA | Mixed Gen/Demand
BELLACORRICK | BELLACORRICK_110-T122_10_MVA | 110 KV | 110 kV - MV | 1 | BELLACORRICK_110 | T122_10_MVA | 13324 | 110 | 21.4 | 32 | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 10 MVA | Mixed Gen/Demand
BELLACORRICK | BELLACORRICK_110-T141_63_MVA | 110 KV | 110 - 38 kV | 1 | BELLACORRICK_110 | T141_63_MVA | 3162 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 63 MVA | Mixed Gen/Demand
BELLACORRICK | BELLACORRICK_110-T143_63_MVA | 110 KV | 110 - 38 kV | 2 | BELLACORRICK_110 | T143_63_MVA | 13290 | 110 | 41.6 |  | 48 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
BELLFIELD | Bellfield-T42_10_MVA | 38 KV | 38 kV - MV | 1 | Bellfield | T42_10_MVA | 4129 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BELMAYNE | BELMAYNE_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | BELMAYNE_110 | T142_63_MVA | 13145 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
BELMAYNE | BELMAYNE_38-T422_15_MVA | 110 KV | 38 kV - MV | 1 | BELMAYNE_38 | T422_15_MVA | 13147 | 41.6 | 21.4 |  | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
BELMULLET | BELMULLET-T421_5_MVA | 38 KV | 38 kV - MV | 1 | BELMULLET | T421_5_MVA | 3935 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
BELVIEW | BELVIEW-T422_15_MVA | 38 KV | 38 kV - MV | 1 | BELVIEW | T422_15_MVA | 4055 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
BETTYSTOWN | Bettystown_38-T422_15_MVA | 38 KV | 38 kV - MV | 1 | Bettystown_38 | T422_15_MVA | 12958 | 41.6 | 21.4 |  | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
BINBANE | BINBANE_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | BINBANE_110 | T142_63MVA | 2864 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
BINBANE | BINBANE_T143-T143_63MVA | 110 KV | 110 - 38 kV | 2 | BINBANE_T143 | T143_63MVA | 2862 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
BIRDHILL | BIRDHILL-T422_10_MVA | 38 KV | 38 kV - MV | 1 | BIRDHILL | T422_10_MVA | 3031 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
BIRDHILL | New 110/MV station at Birdhill_110-T122_31.5_MVA | 38 KV | 110 kV - MV | 2 | New 110/MV station at Birdhill_110 | T122_31.5_MVA | 12943 | 110 | 21.4 |  | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
BIRR | BIRR-T41_10_MVA | 38 KV | 38 kV - MV | 1 | BIRR | T41_10_MVA | 4019 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
BIRR | BIRR_T422-T422_10_MVA | 38 KV | 38 kV - MV | 1 | BIRR_T422 | T422_10_MVA | 4020 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
BISHOPSTOWN | BISHOPSTOWN-T42_10_MVA BISHOPSTOWN | 38 KV | 38 kV - MV | 1 | BISHOPSTOWN | T42_10_MVA BISHOPSTOWN | 3414 | 41.6 | 10.7 | 20 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BISHOPSTOWN | BISHOPSTOWN-T42_15_MVA BISHOPSTOWN | 38 KV | 38 kV - MV | 1 | BISHOPSTOWN | T42_15_MVA BISHOPSTOWN | 13351 | 41.6 | 10.7 | 28 | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
BLACKPOOL | BLACKPOOL | 110 kV |  |  | BLACKPOOL |  |  |  |  | 0 | 0 | Unsure
BLACKROCK | BLACKROCK_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | BLACKROCK_110 | T142_63MVA | 2606 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
BLACKWATER BRIDGE | BLACKWATER BRIDGE | 38 KV |  |  | BLACKWATER BRIDGE |  |  |  |  | 0 | 0 | Retired per central mapping FL list
BLAKE | BLAKE_38-T42_5_MVA | 110 KV | 38 kV - MV | 1 | BLAKE_38 | T42_5_MVA | 3658 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BLAKE | BLAKE_38-T42_15_MVA | 110 KV | 38 kV - MV | 1 | BLAKE_38 | T42_15_MVA | 13349 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
BLAKE | BLAKE_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | BLAKE_110 | T142_31_5MVA | 2655 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
BLANCHFIELD | BLANCHFIELD-T421_15_MVA | 38 KV | 38 kV - MV | 1 | BLANCHFIELD | T421_15_MVA | 3820 | 41.6 | 21.4 | 0 | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 15 MVA (Gen only) | Gen Only
BLANCHFIELD | BLANCHFIELD-T422_31_5MVA | 38 KV | 38 kV - MV | 2 | BLANCHFIELD | T422_31_5MVA | 3819 | 41.6 | 21.4 |  | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 31.5 MVA (Gen only) | Gen Only
BLANE | BLANE | 38 kV |  |  | BLANE |  |  |  |  | 0 | 0 | Unsure
BLESSINGTON | BLESSINGTON-T422_10MVA | 38 KV | 38 kV - MV | 1 | BLESSINGTON | T422_10MVA | 3817 | 41.6 | 21.4 | 32 | 8 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
BLESSINGTON | BLESSINGTON-T422_15_MVA | 38 KV | 38 kV - MV | 1 | BLESSINGTON | T422_15_MVA | 13302 | 41.6 | 21.4 |  | 56 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
BLUNDELSTOWN | BLUNDELSTOWN-T142_63_MVA | 38 KV | 110 - 38 kV | 1 | BLUNDELSTOWN | T142_63_MVA | 12982 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
BOGGERAGH | BOGGERAGH_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | BOGGERAGH_110 | T142_63MVA | 2703 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
BOGHALL ROAD | BOGHALL RD-T42_10_MVA | 38 KV | 38 kV - MV | 1 | BOGHALL RD | T42_10_MVA | 3341 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BOOLTIAGH | BOOLTIAGH_T143-T143_63_MVA | 110 KV | 110 - 38 kV | 1 | BOOLTIAGH_T143 | T143_63_MVA | 2854 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
BOOLTIAGH | BOOLTGH_38_2-T421_15_MVA | 110 KV | 38 kV - MV | 1 | BOOLTGH_38_2 | T421_15_MVA | 3688 | 41.6 | 21.4 | 0 | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 15 MVA (Gen only) | Gen Only
BOOLTIAGH | BOOLTIAGH_T141-T141_63MVA | 110 KV | 110 - 38 kV | 2 | BOOLTIAGH_T141 | T141_63MVA | 2853 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
BORRISOLEIGH | BORRISOLEIGH-T422_5_MVA | 38 KV | 38 kV - MV | 1 | BORRISOLEIGH | T422_5_MVA | 13181 | 41.6 | 21.4 | 0 | 60 | No loads in SCADA | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
BOTHAR | BOTHAR | 38 kV |  |  | BOTHAR |  |  |  |  | 0 | 0 | Unsure
BOYLE | BOYLE-T42_5_MVA BOYLE | 38 KV | 38 kV - MV | 1 | BOYLE | T42_5_MVA BOYLE | 3894 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BRACKLONE | Bracklone_110-T123_20MVA | 110 kV | 110 kV - MV | 1 | Bracklone_110 | T123_20MVA | 9314 | 110 | 21.4 | 20 | 56 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 20 MVA | Mixed Gen/Demand
BRAY | BRAY-T42_10_MVA | 38 KV | 38 kV - MV | 1 | BRAY | T42_10_MVA | 3497 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BREWERY ROAD | BREWERY ROAD-T42_10_MVA | 38 KV | 38 kV - MV | 1 | BREWERY ROAD | T42_10_MVA | 3924 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BRINNY | BRINNY | 38 KV |  |  | BRINNY |  |  |  |  | 0 | 0 | TSO-Customer station
BROCK | BROCK | 38 kV |  |  | BROCK |  |  |  |  | 0 | 0 | Unsure
BRUFF | BRUFF-T42_5_MVA | 38 KV | 38 kV - MV | 1 | BRUFF | T42_5_MVA | 3021 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
BRUFF | BRUFF_T421-T421_5_MVA | 38 KV | 38 kV - MV | 1 | BRUFF_T421 | T421_5_MVA | 3022 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
BUCKLEYS CROSS | BUCKLEYS CROSS | 38 KV |  |  | BUCKLEYS CROSS |  |  |  |  | 0 | 0 | OK - 38 kV switching station
BUNCLODY | BUNCLODY-T422_5_MVA BUNCLODY | 38 KV | 38 kV - MV | 1 | BUNCLODY | T422_5_MVA BUNCLODY | 3880 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
BUNCRANA | BUNCRANA-T422_5_MVA | 38 KV | 38 kV - MV | 1 | BUNCRANA | T422_5_MVA | 3257 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
BUNDORAN | BUNDORAN-T42_5_MVA | 38 KV | 38 kV - MV | 1 | BUNDORAN | T42_5_MVA | 3578 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
BURNWOOD | BURNWOOD | 38 KV |  |  | BURNWOOD |  |  |  |  | 0 | 0 | No loads in SCADA. I think this may be the Training School
BUSH | BUSH-T422_5_MVA_BUSH | 38 KV | 38 kV - MV | 1 | BUSH | T422_5_MVA_BUSH | 3913 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
BUSHFIELD | BUSHFIELD-T42_10_MVA | 38 KV | 38 kV - MV | 1 | BUSHFIELD | T42_10_MVA | 3888 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
BUTLERSTOWN | BUTLERSTOWN_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | BUTLERSTOWN_110 | T142_31_5MVA | 2609 | 110 | 41.6 | 32 | 12 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
BUTLERSTOWN | BUTLERSTOWN_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | BUTLERSTOWN_110 | T142_63_MVA | 12100 | 110 | 41.6 |  | 52 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
BUTTEVANT | BUTTEVANT-T42_5_MVA BUTTEVANT | 38 KV | 38 kV - MV | 1 | BUTTEVANT | T42_5_MVA BUTTEVANT | 3404 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CABRA | CABRA_110-T102_20MVA | 110 KV | 110 kV - MV | 1 | CABRA_110 | T102_20MVA | 8204 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
CAHERDAVIN | CAHERDAVIN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | CAHERDAVIN | T42_10_MVA | 4276 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
CAHIR | CAHIR_38-T42_10_MVA | 110 KV | 38 kV - MV | 1 | CAHIR_38 | T42_10_MVA | 3630 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
CAHIR | CAHIR_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | CAHIR_110 | T142_31_5MVA | 3632 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
CAHIRCALLA | Cahercalla-T42_5_MVA CAHIRCALLA | 38 KV | 38 kV - MV | 1 | Cahercalla | T42_5_MVA CAHIRCALLA | 3149 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CAHIRCIVEEN | CAHIRCIVEEN | 38 KV |  |  | CAHIRCIVEEN |  |  |  |  | 0 | 0 | Retired per central mapping FL list
CALLAN | CALLAN-T42_5_MVA | 38 KV | 38 kV - MV | 1 | CALLAN | T42_5_MVA | 3862 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CALLEE | CALLEE | 38 KV |  |  | CALLEE |  |  |  |  | 0 | 0 | Customer windfarm Trafo - Barranafaddock WF
CAMDEN ROW | CAMDEN ROW-T41_15_MVA | 38 KV | 38 kV - MV | 1 | CAMDEN ROW | T41_15_MVA | 2656 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 15 MVA | Mixed Gen/Demand
CAPPAMORE | CAPPAMORE-T42_5_MVA CAPPAMORE | 38 KV | 38 kV - MV | 1 | CAPPAMORE | T42_5_MVA CAPPAMORE | 3023 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CARK | CARK | 38 KV |  |  | CARK |  |  |  |  | 0 | 0 | Unsure - WF connecting to Letterkenny
CARLISLE | CARLISLE | 38 KV |  |  | CARLISLE |  |  |  |  | 0 | 0 | Customer trafos
CARLOW | CARLOW_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | CARLOW_110 | T142_63MVA | 2611 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
CARNA | CARNA | 110 kV |  |  | CARNA |  |  |  |  | 0 | 0 | Unsure
CARNDONAGH | CARNDONAGH-T422_5_MVA | 38 KV | 38 kV - MV | 1 | CARNDONAGH | T422_5_MVA | 3436 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
CARNSORE | CARNSORE | 38 KV |  |  | CARNSORE |  |  |  |  | 0 | 0 | OK IPP owned trafo
CAROLINE STREET | Caroline Street_38-T422_15_MVA | 10 KV | 38 kV - MV | 1 | Caroline Street_38 | T422_15_MVA | 12125 | 41.6 | 21.4 | 0 | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
CARRANSTOWN | CARRANSTOWN | 38 KV |  |  | CARRANSTOWN |  |  |  |  | 0 | 0
CARRAROE | CARRAROE-T42_5_MVA | 38 KV | 38 kV - MV | 1 | CARRAROE | T42_5_MVA | 3884 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
CARRICK ON SHANNON | CARRICK ON SHANNON_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | CARRICK ON SHANNON_110 | T142_31_5MVA | 2626 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
CARRICK ON SHANNON | CARICKONS_38-T42_5_MVA CARICKON2_10 | 110 KV | 38 kV - MV | 1 | CARICKONS_38 | T42_5_MVA CARICKON2_10 | 3641 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CARRICKMACROSS | Carrickmacross-T42_10_MVA_CARICKMACROS | 38 KV | 38 kV - MV | 1 | Carrickmacross | T42_10_MVA_CARICKMACROS | 3299 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
CARRICKMINES | CARRICKMINS_GIS_B_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | CARRICKMINS_GIS_B_110 | T142_63MVA | 2618 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
CARRICKMINES | Carrickmines_38-T42_15_MVA | 110 KV | 38 kV - MV | 1 | Carrickmines_38 | T42_15_MVA | 3635 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
CARRIGADROHID | CARRIGADROHID | 110 KV |  |  | CARRIGADROHID |  |  |  |  | 0 | 0
CARRIGALINE | CARRIGALINE-T42_5_MVA CARRIGALINE | 38 KV | 38 kV - MV | 1 | CARRIGALINE | T42_5_MVA CARRIGALINE | 3080 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CARRIGALLEN | CARRIGALLEN-T421_5_MVA | 38 KV | 38 kV - MV | 1 | CARRIGALLEN | T421_5_MVA | 3061 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
CARRIGCANNON | CARRIGCANNON | 38 KV |  |  | CARRIGCANNON |  |  |  |  | 0 | 0
CARRIGLAWN | CARRIGLAWN-T42_5_MVA CARRIGLAWN | 38 KV | 38 kV - MV | 1 | CARRIGLAWN | T42_5_MVA CARRIGLAWN | 3156 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CARRIGSHANE | CARRIGSHANE-T422_10_MVA | 38 KV | 38 kV - MV | 1 | CARRIGSHANE | T422_10_MVA | 3860 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
CARRIGTHOMAS | CARRIGTHOMAS | 38 KV |  |  | CARRIGTHOMAS |  |  |  |  | 0 | 0
CARRIGTWOHILL | Carrigtowhill-T42_5_MVA | 38 KV | 38 kV - MV | 1 | Carrigtowhill-T42_5_MVA |  |  |  |  | 32 | 0
CARRIGTWOHILL | Carrigtwohill-T42_15_MVA | 38 KV | 38 kV - MV | 1 | Carrigtwohill | T42_15_MVA | 12070 | 41.6 | 10.7 |  | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 15 MVA | Mixed Gen/Demand
CARROWBEG | CARROWBEG-T42_10_MVA CARROWBEG | 110 KV | 38 kV - MV | 1 | CARROWBEG | T42_10_MVA CARROWBEG | 3701 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
CARROWBEG | CARROWBEG_T423-T421_10_MVA | 110 KV | 38 kV - MV | 1 | CARROWBEG_T423 | T421_10_MVA | 3702 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
CARROWBEG | CARROWBEG_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | CARROWBEG_110 | T142_31_5MVA | 2924 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
CARTRONTROY | CARTRONTROY | 38 KV |  |  | CARTRONTROY |  |  |  |  | 0 | 0
CASHEL | CASHEL-T42_10_MVA | 38 KV | 38 kV - MV | 1 | CASHEL | T42_10_MVA | 3089 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
CASHLA | CASHLA | 220 KV |  |  | CASHLA |  |  |  |  | 0 | 0
CASTLEBAR | CASTLEBAR_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | CASTLEBAR_110 | T142_31_5MVA | 3633 | 110 | 41.6 |  | 20 |  | Mixed-Uneven-110-38 | 110/38 kV (1x31.5MVA) + (1x63MVA) | Mixed Gen/Demand
CASTLEBAR | CASTLEBAR_110-T141_63_MVA | 110 KV | 110 - 38 kV | 1 | CASTLEBAR_110 | T141_63_MVA | 2615 | 110 | 41.6 | 64 | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
CASTLEBLAYNEY | Castleblayney-T42_10MVA_CASTLEBLAYENY | 38 KV | 38 kV - MV | 1 | Castleblayney | T42_10MVA_CASTLEBLAYENY | 3134 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
CASTLECOMER | CASTLECOMER-T42_5_MVA | 38 KV | 38 kV - MV | 1 | CASTLECOMER | T42_5_MVA | 2984 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CASTLECOMER | CASTLECOMER-T41_15_MVA | 38 KV | 38 kV - MV | 1 | CASTLECOMER | T41_15_MVA | 12873 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
CASTLEDOCKRILL | CASTLEDOCKRILL | 110 kV |  |  | CASTLEDOCKRILL |  |  |  |  | 0 | 0
CASTLEFARM | CASTLEFARM | 38 KV |  |  | CASTLEFARM |  |  |  |  | 0 | 0
CASTLEFARM 110KV | CASTLEFARM 110KV | 110 KV |  |  | CASTLEFARM 110KV |  |  |  |  | 0 | 0
CASTLEISLAND | CASTLEISLAND-T42_5_MVA | 38 KV | 38 kV - MV | 1 | CASTLEISLAND | T42_5_MVA | 3367 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CASTLEISLAND | CASTLEISLAND-T42_15_MVA | 38 KV | 38 kV - MV | 1 | CASTLEISLAND | T42_15_MVA | 12082 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
CASTLEKNOCK | CASTLEKNOCK-T42_5_MVA | 38 KV | 38 kV - MV | 1 | CASTLEKNOCK | T42_5_MVA | 3044 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CASTLELYONS | CASTLELYONS-T422_5_MVA CASTLELYONS | 38 KV | 38 kV - MV | 1 | CASTLELYONS | T422_5_MVA CASTLELYONS | 3856 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
CASTLEREA | CASTLEREA-T42_5_MVA CASTLEREA | 38 KV | 38 kV - MV | 1 | CASTLEREA | T42_5_MVA CASTLEREA | 3418 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CASTLETOWNBERE | CASTLETOWNBERE-T42_5_MVA | 38 KV | 38 kV - MV | 1 | CASTLETOWNBERE | T42_5_MVA | 3948 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
CASTLETOWNBERE | CASTLETOWNBERE_T421-T421_5_MVA | 38 KV | 38 kV - MV | 1 | CASTLETOWNBERE_T421 | T421_5_MVA | 3949 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
CASTLETOWNROCHE | Castletownroche-T41_5_MVA | 38 KV | 38 kV - MV | 1 | Castletownroche | T41_5_MVA | 4184 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
CASTLETROY | CASTLETROY-T42_5_MVA CASTLETROY | 38 KV | 38 kV - MV | 1 | CASTLETROY | T42_5_MVA CASTLETROY | 4010 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CASTLEVIEW | Castleview_110-T101_31.5_MVA | 110 KV | 110 kV - MV | 1 | Castleview_110 | T101_31.5_MVA | 9125 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 31.5 MVA | Mixed Gen/Demand
CASTLEVIEW | Castleview_T103-T103_31.5_MVA | 110 KV | 110 kV - MV | 2 | Castleview_T103 | T103_31.5_MVA | 13334 | 110 | 10.7 |  | 52 |  | Generation-Standalone-110-MV | 110/10 kV - 1 x 31.5 MVA (Gen only) | Gen Only
CATHALEENS FALL | CATHALEENS FALL_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | CATHALEENS FALL_110 | T141_31_5MVA | 3687 | 110 | 41.6 | 32 | 12 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
CATHALEENS FALL | CATHALEENS FALL_110-T141_63_MVA | 110 KV | 110 - 38 kV | 1 | CATHALEENS FALL_110 | T141_63_MVA | 13293 | 110 | 41.6 | 0 | 52 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 63 MVA | Mixed Gen/Demand
CATHALEENS FALL 38 |  | 38 KV |  |  | 0 | [5 empty] | 0
CAUSEWAY | CAUSEWAY-T42_5_MVA | 38 KV | 38 kV - MV | 1 | CAUSEWAY | T42_5_MVA | 3902 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CAUTEEN | CAUTEEN_T141-T141_63MVA | 110 KV | 110 - 38 kV | 1 | CAUTEEN_T141 | T141_63MVA | 4836 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
CAUTEEN | CAUTEEN_T142-T142_63MVA | 110 KV | 110 - 38 kV | 2 | CAUTEEN_T142 | T142_63MVA | 2920 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
CAUTEEN | CAUTEEN_T144-T144_63_MVA | 110 KV | 110 - 38 kV | 3 | CAUTEEN_T144 | T144_63_MVA | 2921 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
CAUTEEN | CAUTEEN_T143-T143_63_MVA | 110 KV | 110 - 38 kV | 4 | CAUTEEN_T143 | T143_63_MVA | 13330 | 110 | 41.6 |  | 48 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
CAVAN | CAVAN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | CAVAN | T42_10_MVA | 4046 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
CAVAN | CAVAN_T421-T421_10_MVA | 38 KV | 38 kV - MV | 1 | CAVAN_T421 | T421_10_MVA | 4047 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
CELBRIDGE | CELBRIDGE-T42_10_MVA_CELBRIDGE | 38 KV | 38 kV - MV | 1 | CELBRIDGE | T42_10_MVA_CELBRIDGE | 3092 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
CENTRAL PARK | Central Park-T102_20MVA | 110 KV | 110 kV - MV | 1 | Central Park | T102_20MVA | 8220 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
CENTRE PARK ROAD | CENTRE PARK ROAD | 38 KV |  |  | CENTRE PARK ROAD |  |  |  |  | 0 | 0
CHARLESLAND | CHARLESLAND | 110 kV |  |  | CHARLESLAND |  |  |  |  | 0 | 0
CHARLESTOWN | CHARLESTOWN-T41_5_MVA | 38 KV | 38 kV - MV | 1 | CHARLESTOWN | T41_5_MVA | 4172 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
CHARLEVILLE | CHARLEVILLE_38-T421_10_MVA | 110 KV | 38 kV - MV | 1 | CHARLEVILLE_38 | T421_10_MVA | 3643 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
CHARLEVILLE | CHARLEVILLE__110-T142_30MVA | 110 KV | 110 - 38 kV | 1 | CHARLEVILLE__110-T142_30MVA |  |  |  |  | 8 | 0
CHARLEVILLE | CHARLEVILLE__110-T142_31.5_MVA | 110 KV | 110 - 38 kV | 1 | CHARLEVILLE__110 | T142_31.5_MVA | 4801 | 110 | 41.6 | 24 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
CHARLEVILLE | CHARLEVILLE_T141-T141_63_MVA | 110 KV | 110 - 38 kV | 2 | CHARLEVILLE_T141 | T141_63_MVA | 2631 | 110 | 41.6 |  | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
CHEEVERSTOWN | CHEEVERSTOWN | 38 KV |  |  | CHEEVERSTOWN |  |  |  |  | 0 | 0
CHERRYWOOD | CHERRYWOOD_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | CHERRYWOOD_110 | T142_63MVA | 3932 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
CHERRYWOOD | CHERRYWOOD_110-T102_20MVA | 110 KV | 110 kV - MV | 1 | CHERRYWOOD_110 | T102_20MVA | 8159 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
CHURCHTOWN | CHURCHTOWN-T41_10_MVA | 38 KV | 38 kV - MV | 1 | CHURCHTOWN | T41_10_MVA | 4267 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
CHURCHTOWN | CHURCHTOWN_T422-T422_10_MVA | 38 KV | 38 kV - MV | 1 | CHURCHTOWN_T422 | T422_10_MVA | 4268 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
CITYWEST | CITYWEST_110-T102_20MVA | 110 KV | 110 kV - MV | 1 | CITYWEST_110 | T102_20MVA | 8198 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
CLADY | CLADY-T42_5MVA | 38 KV | 38 kV - MV | 1 | CLADY | T42_5MVA | 3829 | 41.6 | 10.7 | 0 | 64 |  | Generation-Standalone-38-MV | 38/10 kV - 1 x 5 MVA (Gen only) | Gen Only
CLAHANE | CLAHANE | 110 KV |  |  | CLAHANE |  |  |  |  | 0 | 0
CLARA | CLARA-T422_10_MVA | 38 KV | 38 kV - MV | 1 | CLARA | T422_10_MVA | 3964 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
CLARECASTLE | CLARECASTLE | 38 KV |  |  | CLARECASTLE |  |  |  |  | 0 | 0
CLAREGALWAY | CLAREGALWAY-T42_5_MVA | 38 KV | 38 kV - MV | 1 | CLAREGALWAY | T42_5_MVA | 3407 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
CLAREGALWAY | CLAREGALWAY_T421-T421_5_MVA | 38 KV | 38 kV - MV | 1 | CLAREGALWAY_T421 | T421_5_MVA | 3408 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
CLAREMORRIS | CLAREMORRIS | 38 KV |  |  | CLAREMORRIS |  |  |  |  | 0 | 0 | Retired per central mapping FL list
CLARKSTOWN | Clarkstown-T41_5_MVA_CLARKESTN | 38 KV | 38 kV - MV | 1 | Clarkstown | T41_5_MVA_CLARKESTN | 4083 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
CLASH (Created to allow 019 series Subs) | CLASH (Created to allow 019 series Subs) | 38 KV |  |  | CLASH (Created to allow 019 series Subs) |  |  |  |  | 0 | 0 | Retired per central mapping FL list
CLASHAVOON | CLASHAVOON | 220 KV |  |  | CLASHAVOON |  |  |  |  | 0 | 0
CLASHMORE | CLASHMORE | 38 KV |  |  | CLASHMORE |  |  |  |  | 0 | 0 | Retired per central mapping FL list
CLIFDEN | CLIFDEN-T42_5_MVA CLIFDEN | 38 KV | 38 kV - MV | 1 | CLIFDEN | T42_5_MVA CLIFDEN | 3410 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CLIFF | CLIFF | 110 KV |  |  | CLIFF |  |  |  |  | 0 | 0
CLOGHBAN | CLOGHBAN | 110 KV |  |  | CLOGHBAN |  |  |  |  | 0 | 0
CLOGHBOOLA | Cloghboola_110-T122_63MVA | 110 KV | 110 kV - MV | 1 | Cloghboola_110 | T122_63MVA | 9408 | 110 | 21.4 | 0 | 64 |  | Generation-Standalone-110-MV | 110/20 kV - 1 x 63 MVA (Gen only) | Gen Only
CLOGHER | CLOGHER | 110 KV |  |  | CLOGHER |  |  |  |  | 0 | 0
CLONAKILTY | CLONAKILTY-T42_5_MVA CLONAKILTY | 38 KV | 38 kV - MV | 1 | CLONAKILTY | T42_5_MVA CLONAKILTY | 3078 | 41.6 | 10.7 | 16 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CLONAKILTY | CLONAKILTY-T42_15_MVA | 38 KV | 38 kV - MV | 1 | CLONAKILTY | T42_15_MVA | 9273 | 41.6 | 10.7 | 16 | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
CLONARD | CLONARD-T42_5_MVA CLONARD | 38 KV | 38 kV - MV | 1 | CLONARD | T42_5_MVA CLONARD | 3992 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CLONDALKIN | CLONDALKIN-T41_10_MVA | 38 KV | 38 kV - MV | 1 | CLONDALKIN | T41_10_MVA | 4147 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Three-38-MV | 38/10 kV - 3 x 10 MVA | Mixed Gen/Demand
CLONEE | CLONEE | 220 KV |  |  | CLONEE |  |  |  |  | 0 | 0
CLONES | CLONES-T42_5_MVA CLONES | 38 KV | 38 kV - MV | 1 | CLONES | T42_5_MVA CLONES | 3395 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CLONKEEN | CLONKEEN | 110 KV |  |  | CLONKEEN |  |  |  |  | 0 | 0
CLONMINCH | CLONMINCH-T41_10_MVA | 38 KV | 38 kV - MV | 1 | CLONMINCH | T41_10_MVA | 4097 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
CLONMINCH | CLONMINCH_T422-T422_10_MVA | 38 KV | 38 kV - MV | 1 | CLONMINCH_T422 | T422_10_MVA | 4098 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
CLONROCHE | CLONROCHE-T422_5_MVA CLONROCHE | 38 KV | 38 kV - MV | 1 | CLONROCHE | T422_5_MVA CLONROCHE | 3954 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
CLONSHAUGH | CLONSHAUGH-T42_10_MVA | 38 KV | 38 kV - MV | 1 | CLONSHAUGH | T42_10_MVA | 3779 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
CLONTARF | CLONTARF-T42_10_MVA | 38 KV | 38 kV - MV | 1 | CLONTARF | T42_10_MVA | 3466 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
CLOON | CLOON_T421-T421_10_MVA | 110 KV | 38 kV - MV | 1 | CLOON_T421 | T421_10_MVA | 3637 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
CLOON | CLOON_38-T42_10_MVA | 110 KV | 38 kV - MV | 1 | CLOON_38 | T42_10_MVA | 3636 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
CLOON | CLOON_110-T142_31.5_MVA | 110 KV | 110 - 38 kV | 1 | CLOON_110 | T142_31.5_MVA | 3638 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
CLOONBANNIN | CLOONBANNIN-T42_5_MVA | 38 KV | 38 kV - MV | 1 | CLOONBANNIN | T42_5_MVA | 4137 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
CLOONBANNIN | CLOONBANNIN_T421-T421_5_MVA | 38 KV | 38 kV - MV | 1 | CLOONBANNIN_T421 | T421_5_MVA | 4138 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
CLOONFAUGHNA | CLOONFAUGHNA | 38 kV |  |  | CLOONFAUGHNA |  |  |  |  | 0 | 0
CLOONLOUGH | CLOONLOUGH-T42_5_MVA CLOONLOUGH | 38 KV | 38 kV - MV | 1 | CLOONLOUGH | T42_5_MVA CLOONLOUGH | 3613 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CLOUGHKEATING | CLOUGHKEATING | 38 KV |  |  | CLOUGHKEATING |  |  |  |  | 0 | 0
CLOYNE | CLOYNE-T41_5_MVA | 38 KV | 38 kV - MV | 1 | CLOYNE | T41_5_MVA | 3361 | 41.6 | 10.7 | 32 | 16 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
CLOYNE | CLOYNE-T42_15_MVA | 38 KV | 38 kV - MV | 1 | CLOYNE | T42_15_MVA | 12167 | 41.6 | 10.7 |  | 48 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
COBH | COBH-T42_5_MVA | 38 KV | 38 kV - MV | 1 | COBH-T42_5_MVA |  |  |  |  | 32 | 0
COES ROAD | Coe's Road-T42_5_MVA_COES | 38 KV | 38 kV - MV | 1 | Coe's Road | T42_5_MVA_COES | 3608 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
COLLEGE PARK | College Park-T122_20MVA | 110 KV | 110 kV - MV | 1 | College Park | T122_20MVA | 8256 | 110 | 21.4 | 32 | 64 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 20 MVA | Mixed Gen/Demand
COLLEGE PARK | College Park-T103_20MVA | 110 KV | 110 kV - MV | 1 | College Park | T103_20MVA | 8255 | 110 | 10.7 | 32 | 64 |  | Mixed-Standalone-110-MV | 110/10 kV - 1 x 20 MVA | Mixed Gen/Demand
COLLIGAN | COLLIGAN-T42_10_MVA COLLIGAN | 38 KV | 38 kV - MV | 1 | COLLIGAN | T42_10_MVA COLLIGAN | 3955 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
COLLINSTOWN | COLLINSTOWN-T42_5_MVA COLLINSTOWN | 38 KV | 38 kV - MV | 1 | COLLINSTOWN | T42_5_MVA COLLINSTOWN | 3438 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
COLLINSTOWN | COLLINSTOWN-T41_15_MVA | 38 KV | 38 kV - MV | 1 | COLLINSTOWN | T41_15_MVA | 12867 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
COLLOONEY | COLLOONEY-T422_5_MVA Collooney | 38 KV | 38 kV - MV | 1 | COLLOONEY | T422_5_MVA Collooney | 2891 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
COLLOPS | COLLOPS | 38 kV |  |  | COLLOPS |  |  |  |  | 0 | 0
CONG | CONG-T422_5MVA | 38 KV | 38 kV - MV | 1 | CONG | T422_5MVA | 4038 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
CONVOY | CONVOY-T42_10_MVA CONVOY | 38 KV | 38 kV - MV | 1 | CONVOY | T42_10_MVA CONVOY | 3071 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
COOKSTOWN | COOKSTOWN_GIS-T102_20MVA | 110 KV | 110 kV - MV | 1 | COOKSTOWN_GIS | T102_20MVA | 8207 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
COOKSTOWN | COOKSTOWN_GIS_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | COOKSTOWN_GIS_110 | T142_63MVA | 2910 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
COOLCARRON | COOLCARRON-T41_5_MVA | 38 KV | 38 kV - MV | 1 | COOLCARRON | T41_5_MVA | 3369 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
COOLCORCORAN | COOLCORCORAN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | COOLCORCORAN | T42_10_MVA | 3295 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
COOLEA | COOLEA | 38 KV |  |  | COOLEA |  |  |  |  | 0 | 0
COOLGREANEY ROAD | COOLGREANEY ROAD | 38 KV |  |  | COOLGREANEY ROAD |  |  |  |  | 0 | 0 | Retired per central mapping FL list
COOLMINE | COOLMINE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | COOLMINE | T42_10_MVA | 3772 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
COOLNABACKY | COOLNABACKY | 400 KV |  |  | COOLNABACKY |  |  |  |  | 0 | 0
COOLOCK | COOLOCK-T42_10_MVA | 38 KV | 38 kV - MV | 1 | COOLOCK | T42_10_MVA | 3459 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
COOLROE | COOLROE_110-T121_20_MVA | 110 KV | 110 kV - MV | 1 | COOLROE_110 | T121_20_MVA | 9129 | 110 | 21.4 | 32 | 64 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 20 MVA | Mixed Gen/Demand
COOMAGEARLAGHY | COOMAGEARLAGHY | 110 KV |  |  | COOMAGEARLAGHY |  |  |  |  | 0 | 0
COOMATAGGERT | COOMATAGGART_110-T141_63_MVA | 110 KV | 110 - 38 kV | 1 | COOMATAGGART_110 | T141_63_MVA | 3153 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
COOTEHILL | COOTEHILL | 38 KV |  |  | COOTEHILL |  |  |  |  | 0 | 0 | Retired per central mapping FL list
CORBALLY | CORBALLY-T42_5_MVA | 38 KV | 38 kV - MV | 1 | CORBALLY | T42_5_MVA | 3171 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CORDAL | CORDAL_110-T141_63_MVA | 110 KV | 110 - 38 kV | 1 | CORDAL_110 | T141_63_MVA | 3142 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
CORDERRY | Corderry_T121-T121_20 MVA | 110 KV | 110 kV - MV | 1 | Corderry_T121 | T121_20 MVA | 9415 | 110 | 21.4 | 0 | 64 |  | Generation-Standalone-110-MV | 110/20 kV - 1 x 20 MVA (Gen only) | Gen Only
CORDERRY | Corderry_T122-T122_63MVA | 110 KV | 110 kV - MV | 2 | Corderry_T122 | T122_63MVA | 9461 | 110 | 21.4 |  | 64 |  | Generation-Standalone-110-MV | 110/20 kV - 1 x 63 MVA (Gen only) | Gen Only
CORDUFF | CORDUFF1_110-T121_31.5_MVA | 220 KV | 110 kV - MV | 1 | CORDUFF1_110 | T121_31.5_MVA | 9142 | 110 | 21.4 | 32 | 64 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
CORKAGH | CORKAGH | 110 KV |  |  | CORKAGH |  |  |  |  | 0 | 0
CORKERMORE | CORKERMORE-T421_12MVA | 38 kV | 38 kV - MV | 1 | CORKERMORE | T421_12MVA | 3940 | 41.6 | 21.4 | 0 | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 12 MVA (Gen only) | Gen Only
CORRACLASSY | CORRACLASSY | 110 KV |  |  | CORRACLASSY |  |  |  |  | 0 | 0
CORRAWARRIN | CORRAWARRIN | 38 KV |  |  | CORRAWARRIN |  |  |  |  | 0 | 0 | Retired per central mapping FL list
COURTLOUGH | COURTLOUGH_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | COURTLOUGH_110 | T142_63_MVA | 13219 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
COURTLOUGH | COURTLOUGH_38-T422_15_MVA | 110 KV | 38 kV - MV | 1 | COURTLOUGH_38 | T422_15_MVA | 13221 | 41.6 | 21.4 |  | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
COW CROSS | COWCROSS_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | COWCROSS_110 | T141_31_5MVA | 2628 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
COW CROSS | COWCROSS_38 | 110 KV | 38 kV - MV | 1 | COWCROSS_38 | T41_15_MVA | 5833 | 41.6 | 10.7 |  | 64 |  | Mixed-Uneven-110-MV-38 | 38/10 kV (1x15MVA) + 110/10 kV (1x20MVA) | Mixed Gen/Demand
CRANE | CRANE_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | CRANE_110 | T141_31_5MVA | 2630 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
CRANE | CRANE_110-T122_20MVA | 110 KV | 110 kV - MV | 1 | CRANE_110 | T122_20MVA | 4811 | 110 | 21.4 | 32 | 64 |  | Mixed-Standalone-110-MV | 110/20 kV - 1 x 20 MVA | Mixed Gen/Demand
CRANE | CRANE_38-T421_15_MVA | 110 KV | 38 kV - MV | 2 | CRANE_38 | T421_15_MVA | 13391 | 41.6 | 21.4 |  | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 15 MVA | Mixed Gen/Demand
CRANMORE | CRANMORE-T42_5_MVA CRANMORE | 38 KV | 38 kV - MV | 1 | CRANMORE | T42_5_MVA CRANMORE | 3878 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CRANNY | CRANNY-T41_2_MVA | 38 KV | 38 kV - MV | 1 | CRANNY | T41_2_MVA | 4029 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 2 MVA | Mixed Gen/Demand
CRATLOE | CRATLOE-T422_5_MVA CRATLOE | 38 KV | 38 kV - MV | 1 | CRATLOE | T422_5_MVA CRATLOE | 3453 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
CREAGH | CREAGH-T422_5MVA | 38 KV | 38 kV - MV | 1 | CREAGH | T422_5MVA | 3962 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
CREESLOUGH | CREESLOUGH-T421_5MVA | 38 KV | 38 kV - MV | 1 | CREESLOUGH | T421_5MVA | 3420 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
CREGG ROAD | CREGG ROAD-T42_2_MVA_CREGG ROAD | 38 KV | 38 kV - MV | 1 | CREGG ROAD | T42_2_MVA_CREGG ROAD | 3128 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 2 MVA | Mixed Gen/Demand
CROCKAHENNY | CROCKAHENNY | 38 KV |  |  | CROCKAHENNY |  |  |  |  | 0 | 0
CROMCASTLE | CROMCASTLE | 110 KV |  |  | CROMCASTLE |  |  |  |  | 0 | 0
CRORY | Crory_110-T121_63MVA | 110 KV | 110 kV - MV | 1 | Crory_110 | T121_63MVA | 9423 | 110 | 21.4 | 0 | 64 |  | Generation-Standalone-110-MV | 110/20 kV - 1 x 63 MVA (Gen only) | Gen Only
CRORY | Crory_T122-T122_31,5_MVA | 110 KV | 110 kV - MV | 2 | Crory_T122 | T122_31,5_MVA | 13341 | 110 | 21.4 |  | 60 |  | Generation-Standalone-110-MV | 110/20 kV - 1 x 31.5 MVA (Gen only) | Gen Only
CROSSANA | CROSSANA | 38 KV |  |  | CROSSANA |  |  |  |  | 0 | 0
CROSSLEA | CROSSLEA | 0 |  |  | CROSSLEA |  |  |  |  | 0 | 0
CROSSMOLINA | CROSSMOLINA-T42_5_MVA | 38 KV | 38 kV - MV | 1 | CROSSMOLINA | T42_5_MVA | 3342 | 41.6 | 10.7 | 96 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
CROUGHMARKE | CROUGHMARKE | 38 KV |  |  | CROUGHMARKE |  |  |  |  | 0 | 0
CRUMLIN | CRUMLIN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | CRUMLIN | T42_10_MVA | 3422 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
CULLENAGH | CULLENAGH | 220 KV |  |  | CULLENAGH |  |  |  |  | 0 | 0
CULLION | CULLION-T42_5_MVA | 38 KV | 38 kV - MV | 1 | CULLION | T42_5_MVA | 4278 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
CUNGHILL | CUNGHILL | 110 KV |  |  | CUNGHILL |  |  |  |  | 0 | 0
CURRA | CURRA-T41_5_MVA | 38 KV | 38 kV - MV | 1 | CURRA | T41_5_MVA | 3973 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
CURRABWEE | CURRABWEE | 38 KV |  |  | CURRABWEE |  |  |  |  | 0 | 0
CURRAGLASS | CURRAGLASS-T41_5_MVA | 38 KV | 38 kV - MV | 1 | CURRAGLASS | T41_5_MVA | 4032 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
CURRALEIGH | CURRALEIGH-T422_5_MVA CURRALEIGH | 38 KV | 38 kV - MV | 1 | CURRALEIGH | T422_5_MVA CURRALEIGH | 3849 | 41.6 | 21.4 | 32 | 20 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
CURRALEIGH | CURRALEIGH-T422_10_MVA | 38 KV | 38 kV - MV | 1 | CURRALEIGH | T422_10_MVA | 12065 | 41.6 | 21.4 |  | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
CUSHALING | CUSHALING | 110 KV |  |  | CUSHALING |  |  |  |  | 0 | 0
DALKEY | DALKEY | 38 KV |  |  | DALKEY |  |  |  |  | 0 | 0
DALLIGAN | DALLIGAN | 38 kV |  |  | DALLIGAN |  |  |  |  | 0 | 0
DALLOW | DALLOW_110-T141_31_5_MV | 110 KV | 110 - 38 kV | 1 | DALLOW_110 | T141_31_5_MV | 3020 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
DALLOW | DALLOW_38-T421_10_MVA | 110 KV | 38 kV - MV | 1 | DALLOW_38 | T421_10_MVA | 3695 | 41.6 | 21.4 | 0 | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 10 MVA (Gen only) | Gen Only
DALTON | DALTON_38-T422_10_MVA DALTON_38 | 110 KV | 38 kV - MV | 1 | DALTON_38 | T422_10_MVA DALTON_38 | 3640 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
DALTON | DALTON_110-T142_31_5_MV | 110 KV | 110 - 38 kV | 1 | DALTON_110 | T142_31_5_MV | 2624 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
DALTON | DALTON_T141-T141_63_MVA | 110 KV | 110 - 38 kV | 2 | DALTON_T141 | T141_63_MVA | 2623 | 110 | 41.6 |  | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
DARDISTOWN | DARDISTOWN | 110 KV |  |  | DARDISTOWN |  |  |  |  | 0 | 0
DEANSGRANGE | DEANSGRANGE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | DEANSGRANGE | T42_10_MVA | 2783 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
DEERPARK | DEERPARK-T42_5_MVA DEERPARK | 38 KV | 38 kV - MV | 1 | DEERPARK | T42_5_MVA DEERPARK | 3556 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
DEERPARK | DEERPARK-T42_15_MVA | 38 KV | 38 kV - MV | 1 | DEERPARK | T42_15_MVA | 12081 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
DELVIN | DELVIN | 38 KV | 38 kV - MV | 1 | DELVIN | T42_3.2_MVA_DELVIN | 2941 | 41.6 | 10.7 | 96 | 12 |  | Mixed-Uneven-38-MV | 38/10 kV (1x5MVA) + (1x3.2MVA) | Mixed Gen/Demand
DELVIN | DELVIN-T41_15_MVA | 38 KV | 38 kV - MV | 1 | DELVIN | T41_15_MVA | 12216 | 41.6 | 10.7 |  | 52 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
DENNEHYS CROSS | Dennehy's Cross-T42_15_MVA DENNEHYS X | 38 KV | 38 kV - MV | 1 | Dennehy's Cross | T42_15_MVA DENNEHYS X | 3514 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
DEREEN | DEREEN | 38 KV |  |  | DEREEN |  |  |  |  | 0 | 0
DERRYBEG | DERRYBEG-T42_5_MVA | 38 KV | 38 kV - MV | 1 | DERRYBEG | T42_5_MVA | 3753 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
DERRYBRIEN | DERRYBRIEN | 110 KV |  |  | DERRYBRIEN |  |  |  |  | 0 | 0
DERRYCRAMPH | DERRYCRAMPH-T42_5MVA DERRYCRAMPH | 38 KV | 38 kV - MV | 1 | DERRYCRAMPH | T42_5MVA DERRYCRAMPH | 3989 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
DERRYFRENCH | DERRYFRENCH | 110 KV |  |  | DERRYFRENCH |  |  |  |  | 0 | 0
DERRYIRON | DERRYIRON-T141_63_MVA | 110 KV | 110 - 38 kV | 1 | DERRYIRON | T141_63_MVA | 13299 | 110 | 41.6 | 0 | 52 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
DERRYULK | DERRYULK | 38 kV |  |  | DERRYULK |  |  |  |  | 0 | 0
DINGLE | DINGLE-T422_5_MVA | 38 KV | 38 kV - MV | 1 | DINGLE | T422_5_MVA | 3803 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
DOCK ROAD | DOCK ROAD-T42_5_MVA DOCK ROAD | 38 KV | 38 kV - MV | 1 | DOCK ROAD | T42_5_MVA DOCK ROAD | 4087 | 41.6 | 10.7 | 32 | 8 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
DOCK ROAD | DOCK ROAD-T42_15_MVA | 38 KV | 38 kV - MV | 1 | DOCK ROAD | T42_15_MVA | 12882 | 41.6 | 10.7 |  | 56 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
DODDER ROAD | DODDER Road-T42_10_MVA | 38 KV | 38 kV - MV | 1 | DODDER Road | T42_10_MVA | 3542 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
DONEGAL | DONEGAL-T42_10_MVA | 38 KV | 38 kV - MV | 1 | DONEGAL | T42_10_MVA | 3011 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
DONNYBROOK | DONNYBROOK-T42_10_MVA | 38 KV | 38 kV - MV | 1 | DONNYBROOK | T42_10_MVA | 3510 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
DONORE ROAD | Donore Road_110-T141_63_MVA | 110 KV | 110 - 38 kV | 1 | Donore Road_110 | T141_63_MVA | 9325 | 110 | 41.6 | 12 | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
DONORE ROAD | Donore Road_38-T41_15_MVA | 110 KV | 38 kV - MV | 1 | Donore Road_38 | T41_15_MVA | 9370 | 41.6 | 10.7 | 12 | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
DOOCHARN | DOOCHARN | 38 kV |  |  | DOOCHARN |  |  |  |  | 0 | 0
DOON | DOON_110-T142_31_5_MV | 110 KV | 110 - 38 kV | 1 | DOON_110 | T142_31_5_MV | 2810 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
DORNEY | DORNEY | 38 kV |  |  | DORNEY |  |  |  |  | 0 | 0
DOUGLAS | DOUGLAS-T42_10_MVA DOUGLAS | 38 KV | 38 kV - MV | 1 | DOUGLAS | T42_10_MVA DOUGLAS | 3465 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
DOWNES | DOWNES | 110 KV |  |  | DOWNES |  |  |  |  | 0 | 0
DROMADA | DROMADA | 110 KV |  |  | DROMADA |  |  |  |  | 0 | 0
DROMBEG | DROMBEG_110-T142_31.5_MVA | 110 KV | 110 - 38 kV | 1 | DROMBEG_110 | T142_31.5_MVA | 13260 | 110 | 41.6 |  | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA (Gen only) | Gen Only
DROMDEEVEEN | DROMDEEVEEN | 38 KV |  |  | DROMDEEVEEN |  |  |  |  | 0 | 0
DROMTHACKER | Dromthacker-T422_10_MVA | 38 KV | 38 kV - MV | 1 | Dromthacker | T422_10_MVA | 12888 | 41.6 | 21.4 |  | 56 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
DRUMBEAR | DRUMBEAR-T42_5_MVA_DRUMBEAR | 38 KV | 38 kV - MV | 1 | DRUMBEAR | T42_5_MVA_DRUMBEAR | 3059 | 41.6 | 10.7 | 32 | 16 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
DRUMBEAR | DRUMBEAR-T42_10_MVA | 38 KV | 38 kV - MV | 1 | DRUMBEAR | T42_10_MVA | 12053 | 41.6 | 10.7 |  | 48 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
DRUMCONDRA | DRUMCONDRA-T42_10_MVA | 38 KV | 38 kV - MV | 1 | DRUMCONDRA | T42_10_MVA | 3567 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
DRUMDOWNEY | DRUMDOWNEY | 38 KV |  |  | DRUMDOWNEY |  |  |  |  | 0 | 0
DRUMKEEN | DRUMKEEN | 110 KV |  |  | DRUMKEEN |  |  |  |  | 0 | 0
DRUMLINE | DRUMLINE_38-T422_5_MVA DRUMLINE_38 | 110 KV | 38 kV - MV | 1 | DRUMLINE_38 | T422_5_MVA DRUMLINE_38 | 3648 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
DRUMLINE | DRUMLINE_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | DRUMLINE_110 | T142_31_5MVA | 3650 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
DRUMLOUGH HILL | DRUMLOUGH HILL | 38 KV |  |  | DRUMLOUGH HILL |  |  |  |  | 0 | 0
DRUMQUIN | DRUMQUIN-T42_5_MVA | 38 KV | 38 kV - MV | 1 | DRUMQUIN | T42_5_MVA | 3319 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
DRYBRIDGE | DRYBRIDGE_38-T42_15_MVA_DRYBRIDGE | 110 KV | 38 kV - MV | 1 | DRYBRIDGE_38 | T42_15_MVA_DRYBRIDGE | 3654 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
DRYBRIDGE | DRYBRDGE_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | DRYBRDGE_110 | T142_63MVA | 2644 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
DRYNAM | DRYNAM | 110 KV |  |  | DRYNAM |  |  |  |  | 0 | 0
DUBLIN AIRPORT | DUBLIN AIRPORT | 38 KV |  |  | DUBLIN AIRPORT |  |  |  |  | 0 | 0 | Retired per central mapping FL list
DULEEK | DULEEK-T422_5_MVA_DULEEK | 38 KV | 38 kV - MV | 1 | DULEEK | T422_5_MVA_DULEEK | 3991 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
DUN LAOGHAIRE | Dun Laoghaire-T42_10_MVA | 38 KV | 38 kV - MV | 1 | Dun Laoghaire | T42_10_MVA | 3468 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
DUNDALK | DUNDALK2_38-T42_10_MVA_DUNDALK | 110 KV | 38 kV - MV | 1 | DUNDALK2_38 | T42_10_MVA_DUNDALK | 3647 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
DUNDALK | DUNDALK_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | DUNDALK_110 | T142_63MVA | 2633 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
DUNDERROW | DUNDERROW | 38 KV |  |  | DUNDERROW |  |  |  |  | 0 | 0
DUNDRUM | DUNDRUM-T42_10_MVA | 38 KV | 38 kV - MV | 1 | DUNDRUM | T42_10_MVA | 2970 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
DUNFIRTH | DUNFIRTH_110-T122_20MVA | 38 KV | 110 kV - MV | 1 | DUNFIRTH_110 | T122_20MVA | 9153 | 110 | 21.4 | 32 | 8 |  | Mixed-Standalone-110-MV | 110/20 kV - 1 x 20 MVA | Mixed Gen/Demand
DUNFIRTH | DUNFIRTH_110-T122_31.5_MVA | 38 KV | 110 kV - MV | 1 | DUNFIRTH_110 | T122_31.5_MVA | 12087 | 110 | 21.4 |  | 56 |  | Mixed-Standalone-110-MV | 110/20 kV - 1 x 31.5 MVA | Mixed Gen/Demand
DUNGARVAN | DUNGARVAN_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | DUNGARVAN_110 | T142_31_5MVA | 2635 | 110 | 41.6 | 32 | 16 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
DUNGARVAN | DUNGARVAN_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | DUNGARVAN_110 | T142_63_MVA | 13339 | 110 | 41.6 |  | 48 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
DUNGLOE | DUNGLOE-T42_5_MVA | 38 KV | 38 kV - MV | 1 | DUNGLOE | T42_5_MVA | 3557 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
DUNLAVIN | DUNLAVIN | 38 KV |  |  | DUNLAVIN |  |  |  |  | 0 | 0
DUNLEER | DUNLEER-T42_5_MVA_DUNLEER | 38 KV | 38 kV - MV | 1 | DUNLEER | T42_5_MVA_DUNLEER | 3376 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
DUNMANWAY | DUNMANWAY_T422-T422_10_MVA | 110 KV | 38 kV - MV | 1 | DUNMANWAY_T422 | T422_10_MVA | 3652 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
DUNMANWAY | DUNMANWAY_38-T43_10MVA | 110 KV | 38 kV - MV | 1 | DUNMANWAY_38 | T43_10MVA | 3651 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
DUNMANWAY | DUNMANWAY_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | DUNMANWAY_110 | T142_63_MVA | 2641 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
DUNMOYLAN | DUNMOYLAN | 38 KV |  |  | DUNMOYLAN |  |  |  |  | 0 | 0
DUNSINK | DUNSINK_110-T122_31.5_MVA | 110 KV | 110 kV - MV | 1 | DUNSINK_110 | T122_31.5_MVA | 13065 | 110 | 21.4 | 0 | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
DUNSTOWN | DUNSTOWN | 400 KV |  |  | DUNSTOWN |  |  |  |  | 0 | 0
EAST ATHLONE | East Athlone_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | East Athlone_110 | T142_63_MVA | 13113 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
EAST ATHLONE | East Athlone_38-T422_15_MVA | 110 KV | 38 kV - MV | 1 | East Athlone_38 | T422_15_MVA | 13111 | 41.6 | 21.4 |  | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
EAST GALWAY | East Galway_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | East Galway_110 | T142_63_MVA | 13116 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
EAST GALWAY | East Galway_38-T422_15_MVA | 110 KV | 38 kV - MV | 1 | East Galway_38 | T422_15_MVA | 13118 | 41.6 | 21.4 |  | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
EAST WALL ROAD | East Wall Road-T42_10_MVA | 38 KV | 38 kV - MV | 1 | East Wall Road | T42_10_MVA | 2816 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
EASTMONT | EASTMONT_110-T102_31.5_MVA | 110 KV | 110 kV - MV | 1 | EASTMONT_110 | T102_31.5_MVA | 12105 | 110 | 10.7 |  | 44 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 31.5 MVA | Mixed Gen/Demand
EDENDERRY | EDENDERRY-T422_10_MVA | 38 KV | 38 kV - MV | 1 | EDENDERRY | T422_10_MVA | 3248 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
EDGEWORTHSTOWN | Edgeworthstown-T422_10_MVA EDGEWORT2_20 | 38 KV | 38 kV - MV | 1 | Edgeworthstown | T422_10_MVA EDGEWORT2_20 | 2958 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
EMYVALE | EMYVALE-T422_5_MVA_EMYVALE | 38 KV | 38 kV - MV | 1 | EMYVALE | T422_5_MVA_EMYVALE | 3937 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
ENNIS | ENNIS_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | ENNIS_110 | T142_31_5MVA | 2648 | 110 | 41.6 | 32 | 8 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
ENNIS | ENNIS_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | ENNIS_110 | T142_63_MVA | 12079 | 110 | 41.6 |  | 56 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
ENNIS | ENNIS_110-T102_20MVA | 110 KV | 110 kV - MV | 1 | ENNIS_110 | T102_20MVA | 5306 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
ENNIS NORTH | ENNIS NORTH-T42_5_MVA ENNIS NORTH | 38 KV | 38 kV - MV | 1 | ENNIS NORTH | T42_5_MVA ENNIS NORTH | 3783 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
ENNISCRONE | ENNISCRONE-T422_5_MVA ENNISCRONE | 38 KV | 38 kV - MV | 1 | ENNISCRONE | T422_5_MVA ENNISCRONE | 3920 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
ENNISKEANE | ENNISKEANE-T42_5_MVA ENNISKEANE | 38 KV | 38 kV - MV | 1 | ENNISKEANE | T42_5_MVA ENNISKEANE | 4251 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
ENNISTYMON | ENNISTYMON-T42_5_MVA ENNISTYMON | 38 KV | 38 kV - MV | 1 | ENNISTYMON | T42_5_MVA ENNISTYMON | 3064 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
ENNISTYMON | ENNISTYMON-T42_15_MVA | 38 KV | 38 kV - MV | 1 | ENNISTYMON | T42_15_MVA | 12077 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
ERRIGAL | ERRIGAL-T41_10_MVA | 38 KV | 38 kV - MV | 1 | ERRIGAL | T41_10_MVA | 3957 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
ERRIGAL | ERRIGAL_T422-T422_10_MVA | 38 KV | 38 kV - MV | 1 | ERRIGAL_T422 | T422_10_MVA | 3958 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
ERRIGAL | ERRIGAL-T423_10_MVA | 38 KV | 38 kV - MV | 2 | ERRIGAL | T423_10_MVA | 13295 | 41.6 | 21.4 |  | 52 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 10 MVA (Gen only) | Gen Only
ESK | ESK | 38 kV |  |  | ESK |  |  |  |  | 0 | 0
FACTORY CROSS | FACTORY CROSS-T42_10_MVA FACTORY CROS | 38 KV | 38 kV - MV | 1 | FACTORY CROSS | T42_10_MVA FACTORY CROS | 3617 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
FAIRHILL | FAIRHILL-T42_10_MVA | 38 KV | 38 kV - MV | 1 | FAIRHILL | T42_10_MVA | 3909 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
FAIRVIEW | FAIRVIEW-T41_15_MVA | 38 KV | 38 kV - MV | 1 | FAIRVIEW | T41_15_MVA | 2827 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 15 MVA | Mixed Gen/Demand
FASSAROE | FASSAROE_E_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | FASSAROE_E_110 | T142_63MVA | 3656 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
FERMOY | FERMOY_110-T122_31.5_MVA | 110 KV | 110 kV - MV | 1 | FERMOY_110 | T122_31.5_MVA | 12113 | 110 | 21.4 |  | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
FERMOY NORTH | FERMOY NORTH-T42_5_MVA FERMOY NORTH | 38 KV | 38 kV - MV | 1 | FERMOY NORTH | T42_5_MVA FERMOY NORTH | 4017 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
FERNS | FERNS-T421_5_MVA | 38 KV | 38 kV - MV | 1 | FERNS | T421_5_MVA | 4167 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
FIDDANDARRY | FIDDANDARRY | 38 KV |  |  | FIDDANDARRY |  |  |  |  | 0 | 0
FINAWN | FINAWN | 38 KV |  |  | FINAWN |  |  |  |  | 0 | 0
FINGLAS | Finglas_T142_110-T142_63MVA_Finglas Orange | 110 KV | 110 - 38 kV | 1 | Finglas_T142_110 | T142_63MVA_Finglas Orange | 2653 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA (Mesh) | Mixed Gen/Demand
FINGLAS | Finglas_T143_110-T143_63MVA_Finglas Blue | 110 KV | 110 - 38 kV | 2 | Finglas_T143_110 | T143_63MVA_Finglas Blue | 2650 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA (Mesh) | Mixed Gen/Demand
FINISKLIN | Finisklin-T42_5_MVA FINISKLIN | 38 KV | 38 kV - MV | 1 | Finisklin | T42_5_MVA FINISKLIN | 3947 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
FINNEA | FINNEA-T422_5_MVA FINNEA | 38 KV | 38 kV - MV | 1 | FINNEA | T422_5_MVA FINNEA | 4034 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
FINNSTOWN | FINNSTOWN | 220 kV |  |  | FINNSTOWN |  |  |  |  | 0 | 0
FISHERSTOWN | FISHERSTOWN | 38 KV |  |  | FISHERSTOWN |  |  |  |  | 0 | 0
FLAGFORD | FLAGFORD | 220 KV |  |  | FLAGFORD |  |  |  |  | 0 | 0
FLAXFORT | FLAXFORT | 38 KV |  |  | FLAXFORT |  |  |  |  | 0 | 0
FOILDARG | FOILDARG | 0 |  |  | FOILDARG |  |  |  |  | 0 | 0
FOREST | FOREST | 38 kV |  |  | FOREST |  |  |  |  | 0 | 0
FORTUNESTOWN | FORTUNESTOWN-T102_20MVA | 110 KV | 110 kV - MV | 1 | FORTUNESTOWN | T102_20MVA | 8178 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
FOSTERSTOWN | Fosterstown_110-T123_31.5_MVA | 110 KV | 110 kV - MV | 1 | Fosterstown_110 | T123_31.5_MVA | 12152 | 110 | 21.4 |  | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
FOXFORD | FOXFORD | 38 KV |  |  | FOXFORD |  |  |  |  | 0 | 0 | Retired per central mapping FL list
FOXHOLE | FOXHOLE-T422_10_MVA | 38 KV | 38 kV - MV | 1 | FOXHOLE | T422_10_MVA | 4073 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
FOYNES | FOYNES-T42_5_MVA | 38 KV | 38 kV - MV | 1 | FOYNES | T42_5_MVA | 3521 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
FRANCIS STREET | FRANCIS ST_A 110-T142_63MVA_Francis Street_Red | 110 KV | 110 - 38 kV | 1 | FRANCIS ST_A 110 | T142_63MVA_Francis Street_Red | 2654 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA (Mesh) | Mixed Gen/Demand
FREAGH | FREAGH | 110 kV |  |  | FREAGH |  |  |  |  | 0 | 0
GALMOY | GALMOY | 38 KV |  |  | GALMOY |  |  |  |  | 0 | 0
GALWAY | GALWAY_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | GALWAY_110 | T142_63MVA | 2660 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
GALWAY | GALWAY_110-T102_20MVA | 110 KV | 110 kV - MV | 1 | GALWAY_110 | T102_20MVA | 4889 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
GARDEN CITY | GARDEN CITY | 38 KV |  |  | GARDEN CITY |  |  |  |  | 0 | 0
GARISTOWN | GARISTOWN | 38 kV |  |  | GARISTOWN |  |  |  |  | 0 | 0
GARRACUMMER | GARRACUMMER | 38 kV |  |  | GARRACUMMER |  |  |  |  | 0 | 0
GARRANACANTY | GARRANACANTY-T422_10_MVA | 38 KV | 38 kV - MV | 1 | GARRANACANTY | T422_10_MVA | 3615 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
GARRIGERY | GARRIGERY | 0 |  |  | GARRIGERY |  |  |  |  | 0 | 0
GARROW | Garrow_T121-T121_20MVA | 110 KV | 110 kV - MV | 1 | Garrow_T121 | T121_20MVA | 9431 | 110 | 21.4 | 0 | 64 |  | Generation-Standalone-110-MV | 110/20 kV - 1 x 20 MVA (Gen only) | Gen Only
GARRYCASTLE | GARRYCASTLE-T42_15MVA | 38 KV | 38 kV - MV | 1 | GARRYCASTLE | T42_15MVA | 4270 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
GARRYOWEN | GARRYOWEN-T42_15_MVA | 38 KV | 38 kV - MV | 1 | GARRYOWEN | T42_15_MVA | 4122 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
GARRYSPILLANE | Garryspillane-T41_5_MVA | 38 KV | 38 kV - MV | 1 | Garryspillane | T41_5_MVA | 3483 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
GARTNANEANE | GARTNANEANE | 38 KV |  |  | GARTNANEANE |  |  |  |  | 0 | 0
GARVAGH | GARVAGH_110-T141_63_MVA | 110 KV | 110 - 38 kV | 1 | GARVAGH_110 | T141_63_MVA | 3029 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
GARVILLE AVENUE | Garville Avenue-T42_10_MVA | 38 KV | 38 kV - MV | 1 | Garville Avenue | T42_10_MVA | 3359 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
GILLOGUE | GILLOGUE-T42_5_MVA GILLOGUE | 38 KV | 38 kV - MV | 1 | GILLOGUE | T42_5_MVA GILLOGUE | 3858 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
GILRA | GILRA | 110 KV |  |  | GILRA |  |  |  |  | 0 | 0
GLANAGOW | GLANAGOW | 220 KV |  |  | GLANAGOW |  |  |  |  | 0 | 0
GLANLEE | GLANLEE | 110 KV |  |  | GLANLEE |  |  |  |  | 0 | 0
GLANTA COMMONS | GLANTA COMMONS | 38 KV |  |  | GLANTA COMMONS |  |  |  |  | 0 | 0
GLASMORE | GLASMORE_38-T422_10MVA_GLASMORE | 110 KV | 38 kV - MV | 1 | GLASMORE_38 | T422_10MVA_GLASMORE | 3671 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
GLASMORE | GLASMORE T142_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | GLASMORE T142_110 | T142_63_MVA | 2701 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
GLASNEVIN | GLASNEVIN-T41_10_MVA | 38 KV | 38 kV - MV | 1 | GLASNEVIN | T41_10_MVA | 2849 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
GLEBE | GLEBE-T42_10_MVA GLEBE | 38 KV | 38 kV - MV | 1 | GLEBE | T42_10_MVA GLEBE | 3789 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
GLENAMADDY | GLENAMADDY-T422_5_MVA | 38 KV | 38 kV - MV | 1 | GLENAMADDY | T422_5_MVA | 3970 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
GLENGARRIFF | GLENGARRIFF-T421_5_MVA | 38 KV | 38 kV - MV | 1 | GLENGARRIFF | T421_5_MVA | 3707 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
GLENGOOLE | GLENGOOLE | 38 KV | 38 kV - MV | 1 | GLENGOOLE | T42_5_MVA | 3287 | 41.6 | 10.7 | 64 | 64 |  | Mixed-Uneven-38-MV | 38/10 kV (1x5MVA) + (1x10MVA) | Mixed Gen/Demand
GLENLARA | GLENLARA_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | GLENLARA_110 | T142_63_MVA | 2734 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 63 MVA | Mixed Gen/Demand
GLENLARA | GLENLARA_T141-T141_63MVA | 110 KV | 110 - 38 kV | 2 | GLENLARA_T141 | T141_63MVA | 2735 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
GLENMORE | GLENMORE | 38 KV |  |  | GLENMORE |  |  |  |  | 0 | 0
GLENREE | GLENREE_110-T121_20MVA | 110 KV | 110 kV - MV | 1 | GLENREE_110 | T121_20MVA | 4797 | 110 | 21.4 | 0 | 64 |  | Generation-Standalone-110-MV | 110/20 kV - 1 x 20 MVA (Gen only) | Gen Only
GLENREE | GLENREE_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | GLENREE_110 | T142_63MVA | 3160 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
GLENTIES | GLENTIES-T41_5_MVA | 38 KV | 38 kV - MV | 1 | GLENTIES | T41_5_MVA | 3334 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
GLOUCESTER PLACE | Gloucester Place-T42_10_MVA | 38 KV | 38 kV - MV | 1 | Gloucester Place | T42_10_MVA | 2865 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
GNEEVES | GNEEVES | 38 KV |  |  | GNEEVES |  |  |  |  | 0 | 0
GOLAGH | GOLAGH | 110 KV |  |  | GOLAGH |  |  |  |  | 0 | 0
GORESBRIDGE | GORESBRIDGE-T42_5_MVA GORESBRIDGE | 38 KV | 38 kV - MV | 1 | GORESBRIDGE | T42_5_MVA GORESBRIDGE | 3398 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
GORESBRIDGE | GORESBRIDGE-T42_15_MVA | 38 KV | 38 kV - MV | 1 | GORESBRIDGE | T42_15_MVA | 12063 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
GORMAN | GORMAN | 220 KV |  |  | GORMAN |  |  |  |  | 0 | 0
GORT | GORT-T42_5_MVA GORT | 38 KV | 38 kV - MV | 1 | GORT | T42_5_MVA GORT | 3743 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
GORTAWEE | GORTAWEE_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | GORTAWEE_110 | T142_63MVA | 3724 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 63 MVA | Mixed Gen/Demand
GORTEEN | GORTEEN | 38 KV |  |  | GORTEEN |  |  |  |  | 0 | 0
GORTLEE | GORTLEE-T42_10_MVA GORTLEE | 38 KV | 38 kV - MV | 1 | GORTLEE | T42_10_MVA GORTLEE | 4222 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
GORTNAGROSS | GORTNAGROSS | 38 kV |  |  | GORTNAGROSS |  |  |  |  | 0 | 0
GORTYLOUGHLIN | GORTYLOUGHLIN | 38 kV |  |  | GORTYLOUGHLIN |  |  |  |  | 0 | 0
GRAIGUE | GRAIGUE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | GRAIGUE | T42_10_MVA | 2953 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
GRAIGUENAMANAGH | Graiguenamanagh-T42_2_MVA GRAIGUENAMAN | 38 KV | 38 kV - MV | 1 | Graiguenamanagh | T42_2_MVA GRAIGUENAMAN | 3704 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 2 MVA | Mixed Gen/Demand
GRANAGH | Granagh-T42_5_MVA | 38 KV | 38 kV - MV | 1 | Granagh | T42_5_MVA | 3355 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
GRANBY ROW | GRANBY ROW-T41_15_MVA | 38 KV | 38 kV - MV | 1 | GRANBY ROW | T41_15_MVA | 2637 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 15 MVA | Mixed Gen/Demand
GRANGE (DR) | GRANGE_38-T42_10_MVA | 110 KV | 38 kV - MV | 1 | GRANGE_38 | T42_10_MVA | 3661 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
GRANGE (DR) | GRANGE_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | GRANGE_110 | T142_63MVA | 2663 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
GRANGE (SR) | GRANGE (SR)-T42_5_MVA GRANGE-SR | 38 KV | 38 kV - MV | 1 | GRANGE (SR) | T42_5_MVA GRANGE-SR | 3166 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
GRANGE CASTLE | GRANGECASTLE_2-T124_20MVA | 110 KV | 110 kV - MV | 1 | GRANGECASTLE_2 | T124_20MVA | 8269 | 110 | 21.4 | 32 | 64 |  | Mixed-Standalone-110-MV | 110/20 kV - 1 x 20 MVA | Mixed Gen/Demand
GRANGE CASTLE | GRANGE CASTLE_110-T141_63MVA | 110 KV | 110 - 38 kV | 1 | GRANGE CASTLE_110 | T141_63MVA | 2683 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
GRANGE CASTLE | GRANGE CASTLE_110-T122_20MVA | 110 KV | 110 kV - MV | 2 | GRANGE CASTLE_110 | T122_20MVA | 5384 | 110 | 21.4 | 32 | 64 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 20 MVA | Mixed Gen/Demand
GREAT CONNELL | GREAT CONNELL | 110 kV |  |  | GREAT CONNELL |  |  |  |  | 0 | 0
GREAT ISLAND | Great Island_110-T141_63MVA | 220 KV | 110 - 38 kV | 1 | Great Island_110 | T141_63MVA | 3715 | 110 | 41.6 | 32 | 16 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 63 MVA | Mixed Gen/Demand
GREAT ISLAND | Great Island_110-T141_63_MVA | 220 KV | 110 - 38 kV | 1 | Great Island_110 | T141_63_MVA | 13328 | 110 | 41.6 |  | 48 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
GREENHILLS | GREENHILLS-T42_10_MVA | 38 KV | 38 kV - MV | 1 | GREENHILLS | T42_10_MVA | 3482 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
GREYGROVE | GREYGROVE | 38 KV |  |  | GREYGROVE |  |  |  |  | 0 | 0
GREYSTONES | GREYSTONES-T42_10_MVA | 38 KV | 38 kV - MV | 1 | GREYSTONES | T42_10_MVA | 4144 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
GRIFFINRATH | GRIFFINRATH_110_2-T142_63MVA | 110 KV | 110 - 38 kV | 1 | GRIFFINRATH_110_2 | T142_63MVA | 2668 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
GURRANEBANE | GURRANEBANE-T422_5_MVA GURRANEBANE | 38 KV | 38 kV - MV | 1 | GURRANEBANE | T422_5_MVA GURRANEBANE | 3623 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
GURTEEN | GURTEEN-T41_5_MVA | 38 KV | 38 kV - MV | 1 | GURTEEN | T41_5_MVA | 3861 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
GWEEDORE | GWEEDORE-T421_5MVA | 38 KV | 38 kV - MV | 1 | GWEEDORE | T421_5MVA | 3167 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
HARBOUR | HARBOUR | 38 KV |  |  | HARBOUR |  |  |  |  | 0 | 0
HAROLDS CROSS | Harolds Cross_110-T102_20MVA | 110 KV | 110 kV - MV | 1 | Harolds Cross_110 | T102_20MVA | 8273 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
HARTNETTS CROSS | Hartnetts Cross-T121_20MVA | 110 KV | 110 kV - MV | 1 | Hartnetts Cross | T121_20MVA | 9281 | 110 | 21.4 | 24 | 64 |  | Mixed-Standalone-110-MV | 110/20 kV - 1 x 20 MVA | Mixed Gen/Demand
HARTNETTS CROSS | Hartnetts Cross_38-T421_10MVA | 110 KV | 38 kV - MV | 2 | Hartnetts Cross_38 | T421_10MVA | 9279 | 41.6 | 21.4 | 24 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
HAULBOWLINE | HAULBOWLINE | 110 KV |  |  | HAULBOWLINE |  |  |  |  | 0 | 0
HAZELWOOD | HAZELWOOD | 38 KV |  |  | HAZELWOOD |  |  |  |  | 0 | 0 | Retired per central mapping FL list
HEADFORD | HEADFORD-T42_10_MVA_TEMP | 38 KV | 38 kV - MV | 1 | HEADFORD | T42_10_MVA_TEMP | 13327 | 41.6 | 10.7 |  | 60 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
HEADFORD | HEADFORD-T42_10 _MVA_Temp | 38 KV | 38 kV - MV | 1 | HEADFORD | T42_10 _MVA_Temp | 3972 | 41.6 | 10.7 | 32 | 4 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
HEADFORD ROAD | Headford Road-T42_10_MVA | 38 KV | 38 kV - MV | 1 | Headford Road | T42_10_MVA | 3428 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
HERNSBROOK | HERNSBROOK | 38 KV |  |  | HERNSBROOK |  |  |  |  | 0 | 0
HEUSTON SQUARE | Heuston Square-T102_20MVA | 110 KV | 110 kV - MV | 1 | Heuston Square | T102_20MVA | 8205 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
HOLLY HILL | HOLLY HILL | 38 KV |  |  | HOLLY HILL |  |  |  |  | 0 | 0
HOLYCROSS ROAD | HOLYCROSS RD-T42_5_MVA HOLYCROSS RD | 38 KV | 38 kV - MV | 1 | HOLYCROSS RD | T42_5_MVA HOLYCROSS RD | 3536 | 41.6 | 10.7 | 32 | 4 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
HOLYCROSS ROAD | HOLYCROSS RD-T42_15_MVA | 38 KV | 38 kV - MV | 1 | HOLYCROSS RD | T42_15_MVA | 12878 | 41.6 | 10.7 |  | 60 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
HOLYROOD PARK | HOLYROOD PARK | 38 KV |  |  | HOLYROOD PARK |  |  |  |  | 0 | 0
HOWTH JUNCTION | HOWTH JUNCTI-T42_10_MVA | 38 KV | 38 kV - MV | 1 | HOWTH JUNCTI | T42_10_MVA | 3549 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
HUNTSTOWN | HUNTSTOWN | 220 KV |  |  | HUNTSTOWN |  |  |  |  | 0 | 0
IIG | IIG | 38 KV |  |  | IIG |  |  |  |  | 0 | 0
IKERRIN | IKERRIN_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | IKERRIN_110 | T141_31_5MVA | 3662 | 110 | 41.6 | 32 | 20 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
IKERRIN | IKERRIN_110-T141_31.5_MVA | 110 KV | 110 - 38 kV | 1 | IKERRIN_110 | T141_31.5_MVA | 13321 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
INCH | INCH-T422_5_MVA INCH | 38 KV | 38 kV - MV | 1 | INCH | T422_5_MVA INCH | 3386 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
INCHERA | INCHERA | 38 KV |  |  | INCHERA |  |  |  |  | 0 | 0 | Retired per central mapping FL list
INCHICORE | INCHICORE_A1 110-T145_63MVA_Inchicore_Orange | 110 KV | 110 - 38 kV | 1 | INCHICORE_A1 110 | T145_63MVA_Inchicore_Orange | 2846 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA (Mesh) | Mixed Gen/Demand
INCHICORE | INCHICORE_B1_110-T143_63MVA_Inchicore_Green | 110 KV | 110 - 38 kV | 2 | INCHICORE_B1_110 | T143_63MVA_Inchicore_Green | 2670 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA (Mesh) | Mixed Gen/Demand
INCHICORE | INCHICORE_T41-T41_10_MVA | 110 KV | 38 kV - MV | 1 | INCHICORE_T41 | T41_10_MVA | 3665 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
INCHICORE | INCHCR_T141-T43_10_MVA | 110 KV | 38 kV - MV | 2 | INCHCR_T141 | T43_10_MVA | 3663 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
INCHICORE CENTRAL | INCHICORE CENTRAL | 110 KV |  |  | INCHICORE CENTRAL |  |  |  |  | 0 | 0
INCHICORE NORTH | INCHICORE NORTH | 38 KV |  |  | INCHICORE NORTH |  |  |  |  | 0 | 0
INCHINASHING | INCHINASHLING | 38 KV |  |  | INCHINASHLING |  |  |  |  | 0 | 0
INNISCARRA | INNISCARRA | 110 KV |  |  | INNISCARRA |  |  |  |  | 0 | 0
IRISHTOWN | IRISHTOWN | 220 KV |  |  | IRISHTOWN |  |  |  |  | 0 | 0
ISLAND | ISLAND | 38 KV |  |  | ISLAND |  |  |  |  | 0 | 0
JENKINSTOWN | JENKINSTOWN-T422_5_MVA_JENKINST | 38 KV | 38 kV - MV | 1 | JENKINSTOWN | T422_5_MVA_JENKINST | 3432 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
JOHNSTOWN | JOHNSTOWN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | JOHNSTOWN | T42_10_MVA | 3941 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
JULIANSTOWN | JULIANSTOWN-T422_5_MVA_JULIANSTOWN | 38 KV | 38 kV - MV | 1 | JULIANSTOWN | T422_5_MVA_JULIANSTOWN | 3516 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
KANTURK | KANTURK-T42_5_MVA KANTURK | 38 KV | 38 kV - MV | 1 | KANTURK | T42_5_MVA KANTURK | 2918 | 41.6 | 10.7 | 12 | 4 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
KANTURK | KANTURK-T41_10_MVA | 38 KV | 38 kV - MV | 1 | KANTURK | T41_10_MVA | 9270 | 41.6 | 10.7 | 20 | 60 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
KEALKILL | KEALKILL | 38 KV |  |  | KEALKILL |  |  |  |  | 0 | 0
KEELNAGORE | KEELNAGORE | 38 KV |  |  | KEELNAGORE |  |  |  |  | 0 | 0
KEENAHONE | KEENAHONE | 38 KV |  |  | KEENAHONE |  |  |  |  | 0 | 0
KELLIS | KELLIS | 220 KV |  |  | KELLIS |  |  |  |  | 0 | 0
KELLS | KELLS-T42_5_MVA_KELLS | 38 KV | 38 kV - MV | 1 | KELLS | T42_5_MVA_KELLS | 3126 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
KENMARE | KENMARE-T42_5_MVA | 38 KV | 38 kV - MV | 1 | KENMARE | T42_5_MVA | 3784 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
KENMARE | KENMARE_T421-T421_5_MVA | 38 KV | 38 kV - MV | 1 | KENMARE_T421 | T421_5_MVA | 3785 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
KENTSTOWN | KENTSTOWN | 110 kV |  |  | KENTSTOWN |  |  |  |  | 0 | 0
KILBARRY | Kilbarry_T43 | 110 KV | 38 kV - MV | 1 | Kilbarry_T43 | T43_15_MVA | 3666 | 41.6 | 10.7 | 64 | 64 |  | Mixed-Uneven-110-MV-38 | 38/10 kV (1x15MVA) + 110/10 kV (1x20MVA) | Mixed Gen/Demand
KILBARRY | KILBARRY_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | KILBARRY_110 | T142_63MVA | 2672 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
KILBARRY | KILBARRY_110-T101_20MVA | 110 KV | 110 kV - MV | 1 | KILBARRY_110-T101_20MVA | T101_20MVA | 5426 | 110 | 10.7 | 32 | 0
KILCAR | KILCAR-T41_5_MVA | 38 KV | 38 kV - MV | 1 | KILCAR | T41_5_MVA | 3936 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
KILCARAGH | Kilcarragh-T422_5_MVA KILCARAGH_38 | 38 KV | 38 kV - MV | 1 | Kilcarragh | T422_5_MVA KILCARAGH_38 | 4272 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
KILCLOHER | KILCLOHER-T42_5_MVA | 38 KV | 38 kV - MV | 1 | KILCLOHER | T42_5_MVA | 3402 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
KILCOCK | KILCOCK-T422_10_MVA_KILCOCK | 38 KV | 38 kV - MV | 1 | KILCOCK | T422_10_MVA_KILCOCK | 3400 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
KILCOLGAN | KILCOLGAN-T42_5_MVA | 38 KV | 38 kV - MV | 1 | KILCOLGAN | T42_5_MVA | 4213 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
KILCOLGAN | KILCOLGAN_T421-T421_5_MVA | 38 KV | 38 kV - MV | 1 | KILCOLGAN_T421 | T421_5_MVA | 4214 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
KILCOOLE | KILCOOLE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | KILCOOLE | T42_10_MVA | 3928 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
KILCULLEN | KILCULLEN-T42_5_MVA KILCULLEN | 38 KV | 38 kV - MV | 1 | KILCULLEN | T42_5_MVA KILCULLEN | 3529 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
KILCULLEN | KILCULLEN_T424-T424_10_MVA | 38 KV | 38 kV - MV | 1 | KILCULLEN_T424 | T424_10_MVA | 3530 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
KILDARE | KILDARE-T42_15_MVA | 38 KV | 38 kV - MV | 1 | KILDARE | T42_15_MVA | 3013 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
KILDARE | KILDARE-T422_15_MVA | 38 KV | 38 kV - MV | 1 | KILDARE | T422_15_MVA | 12041 | 41.6 | 21.4 |  | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 15 MVA (Gen only) | Gen Only
KILDONAN | KILDONAN | 110 KV |  |  | KILDONAN |  |  |  |  | 0 | 0
KILFADDA | KILFADDA | 38 KV |  |  | KILFADDA |  |  |  |  | 0 | 0
KILFLYNN | KILFLYNN-T41_5_MVA | 38 KV | 38 kV - MV | 1 | KILFLYNN | T41_5_MVA | 2976 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
KILGARVAN | Kilgarvin-T421_5_MVA | 38 KV | 38 kV - MV | 1 | Kilgarvin | T421_5_MVA | 2780 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
KILKEE | KILKEE-T41_5_MVA | 38 KV | 38 kV - MV | 1 | KILKEE | T41_5_MVA | 3455 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
KILKENNY | KILKENNY_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | KILKENNY_110 | T142_63MVA | 2679 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
KILLIN HILL | KILLIN_HILL-T41_15_MVA | 38 KV | 38 kV - MV | 1 | KILLIN_HILL | T41_15_MVA | 3506 | 41.6 | 21.4 | 0 | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 15 MVA (Gen only) | Gen Only
KILLACLOYNE | Killacloyne_110-T121_20_MVA | 38 KV | 110 kV - MV | 1 | Killacloyne_110 | T121_20_MVA | 13018 | 110 | 21.4 |  | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 20 MVA | Mixed Gen/Demand
KILLACLOYNE | KILLACLOYNE-T42_5_MVA KILLACLOYNE | 38 KV | 38 kV - MV | 1 | KILLACLOYNE | T42_5_MVA KILLACLOYNE | 3978 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
KILLACLOYNE | KILLACLOYNE_T43-T43_10MVA | 38 KV | 38 kV - MV | 2 | KILLACLOYNE_T43 | T43_10MVA | 3979 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
KILLAVOY | KILLAVOY | 38 kV |  |  | KILLAVOY |  |  |  |  | 0 | 0
KILLEAGH | KILLEAGH | 38 KV |  |  | KILLEAGH |  |  |  |  | 0 | 0 | Retired per central mapping FL list
KILLESHANDRA | KILLESHANDRA-T42_5_MVA | 38 KV | 38 kV - MV | 1 | KILLESHANDRA | T42_5_MVA | 3434 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
KILLINICK | KILLINICK-T422_10_MVA | 38 KV | 38 kV - MV | 1 | KILLINICK | T422_10_MVA | 3493 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
NEW KILLINICK | Killinick_110-T122_31.5_MVA | 110 KV | 110 kV - MV | 1 | Killinick_110 | T122_31.5_MVA | 12892 | 110 | 21.4 |  | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
KILLONAN | KILLONAN | 220 KV |  |  | KILLONAN |  |  |  |  | 0 | 0
KILLOTERAN | KILLOTERAN_110-T101_20_MVA | 110 KV | 110 kV - MV | 1 | KILLOTERAN_110 | T101_20_MVA | 9168 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
KILLYBEGS | KILLYBEGS-T422_15_MVA | 38 KV | 38 kV - MV | 1 | KILLYBEGS | T422_15_MVA | 3416 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
KILLYGARRY | Killygarry_38-T422_15_MVA | 38 KV | 38 kV - MV | 1 | Killygarry_38 | T422_15_MVA | 13155 | 41.6 | 21.4 |  | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
KILMACTHOMAS | KILMACTHOMAS-T422_5_MVA KILMACTHOMAS | 38 KV | 38 kV - MV | 1 | KILMACTHOMAS | T422_5_MVA KILMACTHOMAS | 3490 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
KILMAGIG | KILMAGIG-T42_5_MVA | 38 KV | 38 kV - MV | 1 | KILMAGIG | T42_5_MVA | 3500 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
KILMAHUD | KILMAHUD | 110 KV |  |  | KILMAHUD |  |  |  |  | 0 | 0
KILMALLOCK | KILMALLOCK-T42_5_MVA | 38 KV | 38 kV - MV | 1 | KILMALLOCK | T42_5_MVA | 3781 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
KILMARTIN | KILMARTIN-T41_5_MVA | 38 KV | 38 kV - MV | 1 | KILMARTIN | T41_5_MVA | 3545 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
KILMEADEN | KILMEADEN-T42_5_MVA | 38 KV | 38 kV - MV | 1 | KILMEADEN | T42_5_MVA | 4025 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
KILMONEY | KILMONEY | 38 KV | 38 kV - MV | 1 | KILMONEY | T42_5_MVA | 3900 | 41.6 | 10.7 | 96 | 64 |  | Mixed-Uneven-38-MV | 38/10 kV (1x10MVA) + (1x5MVA) | Mixed Gen/Demand
KILMORE | KILMORE-T101_20MVA | 110 KV | 110 kV - MV | 1 | KILMORE | T101_20MVA | 8277 | 110 | 10.7 | 32 | 64 |  | Mixed-Three-110-MV | 110/10 kV - 3 x 20 MVA | Mixed Gen/Demand
KILNAP | KILNAP_110-T122_31.5_MVA | 110 KV | 110 kV - MV | 1 | KILNAP_110 | T122_31.5_MVA | 13175 | 110 | 21.4 |  | 52 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
KILPADDOGE | Kilpaddoge_110-T101_20_MVA | 220 KV | 110 kV - MV | 1 | Kilpaddoge_110-T101_20_MVA |  |  |  |  | 0 | 0
KILPADDOGE | Kilpaddoge_110-T122_20_MVA | 220 KV | 110 kV - MV | 1 | Kilpaddoge_110 | T122_20_MVA | 9171 | 110 | 21.4 |  | 64 |  | Generation-Standalone-110-MV | 110/20 kV - 1 x 20 MVA (Gen only) | Gen Only
KILROE | KILROE | 38 kV |  |  | KILROE |  |  |  |  | 0 | 0
KILROSS ROAD | Kilross Road-T42_5_MVA | 38 KV | 38 kV - MV | 1 | Kilross Road | T42_5_MVA | 3317 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
KILROSS ROAD | Kilross Road_T421-T421_5_MVA | 38 KV | 38 kV - MV | 1 | Kilross Road_T421 | T421_5_MVA | 3318 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
KILRUSH | KILRUSH-T42_5_MVA | 38 KV | 38 kV - MV | 1 | KILRUSH | T42_5_MVA | 4266 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
KILSARAN | KILSARAN-T41_5_MVA_KILSARAN | 38 KV | 38 kV - MV | 1 | KILSARAN | T41_5_MVA_KILSARAN | 4016 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
KILSHANNY | KILSHANNY-T42_2_MVA KILSHANNY | 38 KV | 38 kV - MV | 1 | KILSHANNY | T42_2_MVA KILSHANNY | 2945 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 2 MVA | Mixed Gen/Demand
KILTEEL | KILTEEL_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | KILTEEL_110 | T142_31_5MVA | 2716 | 110 | 41.6 | 32 | 20 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
KILTEEL | KILTEEL_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | KILTEEL_110 | T142_63_MVA | 12871 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
KILTIMAGH | KILTIMAGH-T41_5_MVA | 38 KV | 38 kV - MV | 1 | KILTIMAGH | T41_5_MVA | 3575 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
KILTOY | KILTOY | 38 KV |  |  | KILTOY |  |  |  |  | 0 | 0
KIMMAGE | KIMMAGE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | KIMMAGE | T42_10_MVA | 2996 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
KINGSBRIDGE | KINGSBRIDGE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | KINGSBRIDGE | T42_10_MVA | 2726 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
KINGSCOURT | KINGSCOURT-T42_10_MVA_KINGSCOURT | 38 KV | 38 kV - MV | 1 | KINGSCOURT | T42_10_MVA_KINGSCOURT | 2934 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
KINGSCOURT | KINGSCOURT-T423_15MVA_KINGSCOURT | 38 KV | 38 kV - MV | 1 | KINGSCOURT | T423_15MVA_KINGSCOURT | 2935 | 41.6 | 21.4 | 0 | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 15 MVA (Gen only) | Gen Only
KINGSCOURT 400KV | KINGSCOURT 400KV | 400 kV |  |  | KINGSCOURT 400KV |  |  |  |  | 0 | 0
KINNEGAD | KINNEGAD | 110 KV |  |  | KINNEGAD |  |  |  |  | 0 | 0
KINSALE | KINSALE-T42_5_MVA KINSALE | 38 KV | 38 kV - MV | 1 | KINSALE | T42_5_MVA KINSALE | 3353 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
KINSALE | KINSALE-T423_10_MVA | 38 KV | 38 kV - MV | 1 | KINSALE | T423_10_MVA | 4880 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
KNOCKACUMMER | KNOCKACUMMER | 110 KV |  |  | KNOCKACUMMER |  |  |  |  | 0 | 0
KNOCKAFUTERA | KNOCKAFUTERA | 38 KV |  |  | KNOCKAFUTERA |  |  |  |  | 0 | 0
KNOCKALOUGH | KNOCKALOUGH | 110 KV |  |  | KNOCKALOUGH |  |  |  |  | 0 | 0
KNOCKANE | KNOCKANE | 110 kV |  |  | KNOCKANE |  |  |  |  | 0 | 0
KNOCKANURE | KNOCKANURE | 220 KV |  |  | KNOCKANURE |  |  |  |  | 0 | 0
KNOCKAPHUNTA | KNOCKAPHUNTA-T42_5_MVA KNOCKAPHUNTA | 38 KV | 38 kV - MV | 1 | KNOCKAPHUNTA | T42_5_MVA KNOCKAPHUNTA | 4274 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
KNOCKAWARRIGA | KNOCKAWARRIGA | 38 KV |  |  | KNOCKAWARRIGA |  |  |  |  | 0 | 0
KNOCKBROGAN | KNOCKBROGAN | 38 KV |  |  | KNOCKBROGAN |  |  |  |  | 0 | 0 | Retired per central mapping FL list
KNOCKEARAGH | Knockearagh_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | Knockearagh_110 | T142_31_5MVA | 2677 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
KNOCKMULLEN | KNOCKMULLEN-T42_10_MVA | 38 kV | 38 kV - MV | 1 | KNOCKMULLEN | T42_10_MVA | 4242 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
KNOCKMULLEN | KNOCKMULLEN_T421-T421_10_MVA | 38 kV | 38 kV - MV | 1 | KNOCKMULLEN_T421 | T421_10_MVA | 4243 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
KNOCKNAGASHEL | KNOCKNAGASHEL | 110 kV |  |  | KNOCKNAGASHEL |  |  |  |  | 0 | 0
KNOCKNAGEE | KNOCKNAGEE_MSD_38-T42_15_MVA | 38 kV | 38 kV - MV | 1 | KNOCKNAGEE_MSD_38 | T42_15_MVA | 12202 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
KNOCKRAHA | KNOCKRAHA | 220 KV |  |  | KNOCKRAHA |  |  |  |  | 0 | 0
KNOCKRANNY | KNOCKRANNY | 110 KV |  |  | KNOCKRANNY |  |  |  |  | 0 | 0
KNOCKROUR | KNOCKROUR | 38 KV |  |  | KNOCKROUR |  |  |  |  | 0 | 0
KNOCKUMBER | KNOCKUMBER | 110 KV |  |  | KNOCKUMBER |  |  |  |  | 0 | 0
KYLEERAGH | KYLEERAGH | 38 KV | 38 kV - MV | 1 | KYLEERAGH | T42_5_MVA | 3794 | 41.6 | 10.7 | 96 | 64 |  | Mixed-Uneven-38-MV | 38/10 kV (1x10MVA) + (1x5MVA) | Mixed Gen/Demand
KYLETAUN | KYLETAUN | 38 KV |  |  | KYLETAUN |  |  |  |  | 0 | 0
LABBAN | LABBAN | 38 kV |  |  | LABBAN |  |  |  |  | 0 | 0
LACKA | LACKA-T421_10_MVA LACKA_38 | 38 KV | 38 kV - MV | 1 | LACKA-T421_10_MVA LACKA_38 | T421_10_MVA LACKA_38 | 3713 | 41.6 | 21.4 | 0 | 0 | Customer trafos - to be removed
LAKE | LAKE | 38 KV |  |  | LAKE |  |  |  |  | 0 | 0 | Retired per central mapping FL list
LANESBOROUGH | LANESBORO_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | LANESBORO_110 | T141_31_5MVA | 2790 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
LARGAN HILL | LARGAN HILL | 38 KV |  |  | LARGAN HILL |  |  |  |  | 0 | 0
LAUNLUSH | LAUNLUSH | 38 kV |  |  | LAUNLUSH |  |  |  |  | 0 | 0
LAWLESSTOWN | LAWLESSTOWN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | LAWLESSTOWN | T42_10_MVA | 3985 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
LEE BRIDGE | LEE BRIDGE | 38 KV | 38 kV - MV | 1 | LEE BRIDGE |  |  |  |  | 24 | 0
LEESON STREET | Leeson Street-T42_10_MVA | 38 KV | 38 kV - MV | 1 | Leeson Street | T42_10_MVA | 3564 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
LEIXLIP | LEIXLIP-T42_10_MVA_LEIXLIP | 38 KV | 38 kV - MV | 1 | LEIXLIP | T42_10_MVA_LEIXLIP | 3478 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
LEIXLIP GENERATOR | LEIXLIP GENERATOR | 38 KV |  |  | LEIXLIP GENERATOR |  |  |  |  | 0 | 0
LETTERAGH | LETTERAGH | 38 kV |  |  | LETTERAGH |  |  |  |  | 0 | 0
LETTERKENNY | LETTERKENY_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | LETTERKENY_110 | T142_63MVA | 2688 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
LIBERTY STREET | Liberty Street_110-T101_20MVA | 110 KV | 110 kV - MV | 1 | Liberty Street_110 | T101_20MVA | 9447 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
LIFFEY VALLEY | LIFFEY VALLEY-T42_10MVA | 38 KV | 38 kV - MV | 1 | LIFFEY VALLEY | T42_10MVA | 4085 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
LIMERICK | LIMERICK_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | LIMERICK_110 | T142_63MVA | 2692 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
LISDRUM | LISDRUM_38-T422_5_MVA_LISDRUM | 110 KV | 38 kV - MV | 1 | LISDRUM_38 | T422_5_MVA_LISDRUM | 3668 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
LISDRUM | LISDRUM_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | LISDRUM_110 | T142_31_5MVA | 2694 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
LISGLENNON | LISGLENNON | 38 kV |  |  | LISGLENNON |  |  |  |  | 0 | 0
LISHEEN | LISHEEN_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | LISHEEN_110 | T142_63MVA | 2905 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
LISMORE | LISMORE-T42_5_MVA LISMORE | 38 KV | 38 kV - MV | 1 | LISMORE | T42_5_MVA LISMORE | 3619 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
LITTLE BRAY | LITTLE BRAY-T42_10_MVA | 38 KV | 38 kV - MV | 1 | LITTLE BRAY | T42_10_MVA | 3350 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
LITTLE ISLAND | LITTLE ISLAND | 38 KV |  |  | LITTLE ISLAND |  |  |  |  | 0 | 0 | Retired per central mapping FL list
LITTLE MILLS | LITTLE MILLS-T41_5_MVA_LITTLE MI | 38 KV | 38 kV - MV | 1 | LITTLE MILLS | T41_5_MVA_LITTLE MI | 3525 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
LLOYD | LLOYD_38-T42_5_MVA_LLOYD | 38 KV | 38 kV - MV | 1 | LLOYD_38 | T42_5_MVA_LLOYD | 4140 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
LODGEWOOD | LODGEWOOD | 220 KV |  |  | LODGEWOOD |  |  |  |  | 0 | 0
LONGFORD | LONGFORD-T422_10_MVA | 38 KV | 38 kV - MV | 1 | LONGFORD | T422_10_MVA | 3934 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
LONGPOINT | LONGPOINT | 220 KV |  |  | LONGPOINT |  |  |  |  | 0 | 0
LOUGH DOO | LOUGH DOO | 38 kV |  |  | LOUGH DOO |  |  |  |  | 0 | 0
LOUGHAN | LOUGHAN | 38 kV |  |  | LOUGHAN |  |  |  |  | 0 | 0
LOUGHANALLA | LOUGHANALLA-T42_5_MVA_LOUGHAN | 38 KV | 38 kV - MV | 1 | LOUGHANALLA | T42_5_MVA_LOUGHAN | 4066 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
LOUGHBEG | LOUGHBEG | 38 KV |  |  | LOUGHBEG |  |  |  |  | 0 | 0
LOUGHDALE | LOUGHDALE | 38 KV |  |  | LOUGHDALE |  |  |  |  | 0 | 0
LOUGHDERRYDUFF | LOUGHDERRYDUFF | 38 KV |  |  | LOUGHDERRYDUFF |  |  |  |  | 0 | 0
LOUGHLINSTOWN | Loughlinstown-T42_10_MVA LOUGHLINSTWN | 38 KV | 38 kV - MV | 1 | Loughlinstown | T42_10_MVA LOUGHLINSTWN | 3183 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
LOUGHREA | LOUGHREA-T42_5_MVA LOUGHREA | 38 KV | 38 kV - MV | 1 | LOUGHREA | T42_5_MVA LOUGHREA | 2963 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
LOUGHSHINNY | LOUGHSHINNY-T42_10_MVA_LOUGHSHINNY | 38 KV | 38 kV - MV | 1 | LOUGHSHINNY | T42_10_MVA_LOUGHSHINNY | 3095 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
LOUGHTAGALLA | LOUGHTAGALLA-T42_5_MVA LOUGHTAGALLA | 38 KV | 38 kV - MV | 1 | LOUGHTAGALLA | T42_5_MVA LOUGHTAGALLA | 2948 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
LOUTH | LOUTH | 220 KV |  |  | LOUTH |  |  |  |  | 0 | 0
LUCAN EAST | LUCAN EAST-T42_5_MVA LUCAN EAST | 38 KV | 38 kV - MV | 1 | LUCAN EAST | T42_5_MVA LUCAN EAST | 3592 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
LUMCLOON | LUMCLOON-T422_5_MVA LUMCLOON | 38 KV | 38 kV - MV | 1 | LUMCLOON | T422_5_MVA LUMCLOON | 3005 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
MACETOWN | MACETOWN_110-T102_20MVA | 110 KV | 110 kV - MV | 1 | MACETOWN_110 | T102_20MVA | 8200 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
MACROOM | MACROOM_38-T422_5_MVA | 110 KV | 38 kV - MV | 1 | MACROOM_38 | T422_5_MVA | 3669 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
MACROOM | MACROOM_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | MACROOM_110 | T142_31_5MVA | 2697 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
MALAHIDE | MALAHIDE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | MALAHIDE | T42_10_MVA | 3313 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MALLOW | MALLOW_38-T42_10_MVA | 110 KV | 38 kV - MV | 1 | MALLOW_38 | T42_10_MVA | 3673 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MALLOW | MALLOW_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | MALLOW_110 | T142_31_5MVA | 2707 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
MANGANS | MANGANS_38-T421_20MVA | 38 KV | 38 kV - MV | 1 | MANGANS_38 | T421_20MVA | 3710 | 41.6 | 21.4 | 0 | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 20 MVA (Gen only) | Gen Only
MANOR STREET | MANOR ST-T42_10_MVA | 38 KV | 38 kV - MV | 1 | MANOR ST | T42_10_MVA | 3571 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MANORHAMILTON | Manorhamilton-T422_5_MVA | 38 KV | 38 kV - MV | 1 | Manorhamilton | T422_5_MVA | 3568 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
MANORHAMILTON | Manorhamilton-T424_15_MVA | 38 KV | 38 kV - MV | 2 | Manorhamilton | T424_15_MVA | 3569 | 41.6 | 21.4 |  | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 15 MVA (Gen only) | Gen Only
MARINA | MARINA_110-T105_20_MVA | 110 KV | 110 kV - MV | 1 | MARINA_110 | T105_20_MVA | 9185 | 110 | 10.7 | 32 | 4 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
MARINA | MARINA_110-T105_31.5_MVA | 110 KV | 110 kV - MV | 1 | MARINA_110 | T105_31.5_MVA | 13285 | 110 | 10.7 |  | 60 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 31.5 MVA | Mixed Gen/Demand
MARINA | MARINA_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | MARINA_110 | T142_63_MVA | 13287 | 110 | 41.6 |  | 60 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
MARROWBONE LANE | MARROWBONE LANE-T42_15_MVA | 38 KV | 38 kV - MV | 1 | MARROWBONE LANE | T42_15_MVA | 2950 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 15 MVA | Mixed Gen/Demand
MARSHES | MARSHES-T42_10_MVA_MARSHES | 38 KV | 38 kV - MV | 1 | MARSHES | T42_10_MVA_MARSHES | 3590 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MARSHES | MARSHES-T423_10MVA_MARSHES | 38 KV | 38 kV - MV | 1 | MARSHES | T423_10MVA_MARSHES | 3591 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
MAYFIELD | MAYFIELD-T42_10_MVA MAYFIELD | 38 KV | 38 kV - MV | 1 | MAYFIELD | T42_10_MVA MAYFIELD | 3499 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MAYNOOTH | MAYNOOTH | 220 KV |  |  | MAYNOOTH |  |  |  |  | 0 | 0
MCDERMOTT | MCDERMOT_110-T141_63MVA_MCDERMOTMauve | 110 KV | 110 - 38 kV | 1 | MCDERMOT_110 | T141_63MVA_MCDERMOTMauve | 2695 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA (Mesh) | Mixed Gen/Demand
MCDERMOTT | MCDERMOT_110-T122_31.5_MVA | 110 KV | 110 kV - MV | 1 | MCDERMOT_110 | T122_31.5_MVA | 13080 | 110 | 21.4 |  | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
MCDONAGH | MCDONAGH_38-T42_10_MVA | 38 KV | 38 kV - MV | 1 | MCDONAGH_38 | T42_10_MVA | 3745 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MEATH HILL | MEATH_HIL110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | MEATH_HIL110 | T142_63_MVA | 2675 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
MEELICK | MEELICK | 38 KV |  |  | MEELICK |  |  |  |  | 0 | 0
MEENACHULLALAN | MEENACHULLALAN | 38 KV |  |  | MEENACHULLALAN |  |  |  |  | 0 | 0
MEENACLOY | MEENACLOY | 0 |  |  | MEENACLOY |  |  |  |  | 0 | 0
MEENADREEN[MULREAVY] | MEENADREEN[MULREAVY] | 110 kV |  |  | MEENADREEN[MULREAVY] |  |  |  |  | 0 | 0
MEENBOG | MEENBOG | 110 KV |  |  | MEENBOG |  |  |  |  | 0 | 0
MEENTYCAT | MEENTYCAT | 110 KV |  |  | MEENTYCAT |  |  |  |  | 0 | 0
MELBOURNE | MELBOURNE | 110 kV |  |  | MELBOURNE |  |  |  |  | 0 | 0
MERRION SQUARE | Merrion Square-T42_10_MVA | 38 KV | 38 kV - MV | 1 | Merrion Square | T42_10_MVA | 2690 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MERVILLE | MERVILLE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | MERVILLE | T42_10_MVA | 3208 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MERVUE | MERVUE | 38 KV |  |  | MERVUE |  |  |  |  | 0 | 0 | Retired per central mapping FL list
MIDLETON | MIDLETON_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | MIDLETON_110 | T141_31_5MVA | 2700 | 110 | 41.6 | 32 | 20 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
MIDLETON | MIDLETON_110-T141_63_MVA | 110 KV | 110 - 38 kV | 1 | MIDLETON_110 | T141_63_MVA | 12059 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
MIDLETON | MIDLETON_110-T102_20MVA | 110 KV | 110 kV - MV | 1 | MIDLETON_110 | T102_20MVA | 5557 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
MILANE HILL | MILANE HILL | 38 KV |  |  | MILANE HILL |  |  |  |  | 0 | 0
MILESTONE | MILESTONE | 38 KV |  |  | MILESTONE |  |  |  |  | 0 | 0
MILFORD (MWR) | MILFORD-MWR-T41_5_MVA | 38 KV | 38 kV - MV | 1 | MILFORD-MWR | T41_5_MVA | 3373 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
MILFORD (MWR) | MILFORD-MWR_T422-T422_10_MVA | 38 KV | 38 kV - MV | 1 | MILFORD-MWR_T422 | T422_10_MVA | 3374 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
MILFORD (NR) | MILFORD_NR_2-T42_5MVA | 38 KV | 38 kV - MV | 1 | MILFORD_NR_2 | T42_5MVA | 4338 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
MILFORD (NR) | MILFORD_NR_2-T42_15_MVA | 38 KV | 38 kV - MV | 1 | MILFORD_NR_2 | T42_15_MVA | 12075 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
MILLTOWN (DR) | MILLTOWN_B_110-T102_20MVA | 110 KV | 110 kV - MV | 1 | MILLTOWN_B_110 | T102_20MVA | 8262 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
MILLTOWN (DR) | MILLTOWN_A_110-T141_63MVA_Milltown_Blue | 110 KV | 110 - 38 kV | 1 | MILLTOWN_A_110 | T141_63MVA_Milltown_Blue | 2876 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA (Mesh) | Mixed Gen/Demand
MILLTOWN (SR) | MILLTOWN-SR-T422_10_MVA | 38 KV | 38 kV - MV | 1 | MILLTOWN-SR | T422_10_MVA | 3389 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
MILLTOWN MALBAY | Milltown Malbay-T42_5_MVA | 38 KV | 38 kV - MV | 1 | Milltown Malbay | T42_5_MVA | 3830 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
MISERY HILL | Misery Hill-T102_20MVA | 110 KV | 110 kV - MV | 1 | Misery Hill | T102_20MVA | 8230 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
MOANMORE | MOANMORE | 38 KV |  |  | MOANMORE |  |  |  |  | 0 | 0
MOATE | MOATE-T42_5_MVA | 38 KV | 38 kV - MV | 1 | MOATE | T42_5_MVA | 4156 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
MOHILL | MOHILL-T422_5_MVA MOHILL | 38 KV | 38 kV - MV | 1 | MOHILL | T422_5_MVA MOHILL | 3917 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
MONAVEA | MONAVEA | 38 KV |  |  | MONAVEA |  |  |  |  | 0 | 0
MONEENAGHIESHA | MONEENAGEISHA-T42_10_MVA | 38 KV | 38 kV - MV | 1 | MONEENAGEISHA | T42_10_MVA | 3756 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MONETEEN | MONETEEN | 110 KV |  |  | MONETEEN |  |  |  |  | 0 | 0
MONEYCOOLEY | Moneycooley-T44_10_MVA_MONEYCOOLY | 38 KV | 38 kV - MV | 1 | Moneycooley | T44_10_MVA_MONEYCOOLY | 3997 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Three-38-MV | 38/10 kV - 3 x 10 MVA | Mixed Gen/Demand
MONEYPOINT | MONEYPOINT | 400 KV |  |  | MONEYPOINT |  |  |  |  | 0 | 0
MONFIN | MONFIN | 38 KV | 38 kV - MV | 1 | MONFIN | T42_2_MVA | 3492 | 41.6 | 10.7 | 96 | 64 |  | Mixed-Uneven-38-MV | 38/10 kV (1x5MVA) + (1x2MVA) | Mixed Gen/Demand
MONKSLAND | MONKSLAND | 38 KV |  |  | MONKSLAND |  |  |  |  | 0 | 0
MONKSTOWN | MONKSTOWN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | MONKSTOWN | T42_10_MVA | 3348 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MONREAD | MONREAD-T102_20MVA | 110 KV | 110 kV - MV | 1 | MONREAD | T102_20MVA | 8254 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
MORNINGTON ROAD | Mornington Road-T42_10_MVA_MORNINGTON | 38 KV | 38 kV - MV | 1 | Mornington Road | T42_10_MVA_MORNINGTON | 3085 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MORRISTOWN | MORRISTOWN-T42_5_MVA | 38 KV | 38 kV - MV | 1 | MORRISTOWN | T42_5_MVA | 2931 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
MORRISTOWN | MORRISTOWN-T42_15_MVA | 38 KV | 38 kV - MV | 1 | MORRISTOWN | T42_15_MVA | 12896 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
MOUNT CRONALAGHT | MOUNT CRONALAGHT | 38 KV |  |  | MOUNT CRONALAGHT |  |  |  |  | 0 | 0
MOUNT LUCAS | MOUNT LUCAS | 110 KV |  |  | MOUNT LUCAS |  |  |  |  | 0 | 0
MOUNT MERRION | Mount Merrion-T42_10_MVA | 38 KV | 38 kV - MV | 1 | Mount Merrion | T42_10_MVA | 2621 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MOUNT MISERY | MOUNT MISERY-T42_10_MVA | 38 KV | 38 kV - MV | 1 | MOUNT MISERY | T42_10_MVA | 4280 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MOUNTGORRY | MOUNTGORRY-T42_10_MVA_MOUNTGORRY | 38 KV | 38 kV - MV | 1 | MOUNTGORRY | T42_10_MVA_MOUNTGORRY | 3968 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MOUNTGORRY | MOUNTGORRY-T423_15MVA | 38 KV | 38 kV - MV | 1 | MOUNTGORRY | T423_15MVA | 9338 | 41.6 | 21.4 | 20 | 60 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 15 MVA | Mixed Gen/Demand
MOUNTMELLICK | MOUNTMELLICK-T42_5_MVA | 38 KV | 38 kV - MV | 1 | MOUNTMELLICK | T42_5_MVA | 3718 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
MOUNTRATH | MOUNTRATH-T42_5_MVA | 38 KV | 38 kV - MV | 1 | MOUNTRATH | T42_5_MVA | 3723 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
MOVILLE | MOVILLE-T422_5_MVA | 38 KV | 38 kV - MV | 1 | MOVILLE | T422_5_MVA | 3771 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
MOY | MOY_38-T422_10MVA | 110 KV | 38 kV - MV | 1 | MOY_38 | T422_10MVA | 3675 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
MOY | MOY_110-T142_31.5MVA | 110 KV | 110 - 38 kV | 1 | MOY_110 | T142_31.5MVA | 4795 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
MOYLISH | MOYLISH-T42_5_MVA MOYLISH | 38 KV | 38 kV - MV | 1 | MOYLISH | T42_5_MVA MOYLISH | 3768 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
MUINGNAMINNANE | MUINGNAMINNANE | 38 KV |  |  | MUINGNAMINNANE |  |  |  |  | 0 | 0
MUINGS | MUINGS | 38 kV |  |  | MUINGS |  |  |  |  | 0 | 0
MULGANNON | MULGANNON-T42_10_MVA | 38 KV | 38 kV - MV | 1 | MULGANNON | T42_10_MVA | 3106 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
MULLAGH | MULLAGH-T42_5_MVA_MULLAGH | 38 KV | 38 kV - MV | 1 | MULLAGH | T42_5_MVA_MULLAGH | 3808 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
MULLAGH | MULLAGH_T44-T44_5_MVA_MULLAGH | 38 KV | 38 kV - MV | 2 | MULLAGH_T44 | T44_5_MVA_MULLAGH | 3806 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
MULLAGHARLIN | Mullagharlin_110-T121_31.5_MVA | 110 KV | 110 kV - MV | 1 | Mullagharlin_110 | T121_31.5_MVA | 9209 | 110 | 21.4 | 32 | 64 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
MULLASAWNY | MULLASAWNY | 38 kV |  |  | MULLASAWNY |  |  |  |  | 0 | 0
MULLINANALT | MULLANANALT | 38 KV |  |  | MULLANANALT |  |  |  |  | 0 | 0
MULLINGAR | MULLINGAR_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | MULLINGAR_110 | T142_31_5MVA | 2713 | 110 | 41.6 | 32 | 20 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
MULLINGAR | MULLINGAR_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | MULLINGAR_110 | T142_63_MVA | 12085 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
MULLINGAR | MULLINGAR_110-T101_20MVA | 110 KV | 110 kV - MV | 1 | MULLINGAR_110 | T101_20MVA | 9211 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
MULMOSOG | MULMOSOG | 38 kV |  |  | MULMOSOG |  |  |  |  | 0 | 0
MULREAVY | MULREAVY | 110 KV |  |  | MULREAVY |  |  |  |  | 0 | 0
MULTEEN | MULTEEN | 38 KV |  |  | MULTEEN |  |  |  |  | 0 | 0
MUNGRET | MUNGRET | 110 KV |  |  | MUNGRET |  |  |  |  | 0 | 0
NAAS | NAAS-T42_10_MVA | 38 KV | 38 kV - MV | 1 | NAAS | T42_10_MVA | 3067 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
NAVAN | NAVAN_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | NAVAN_110 | T142_63MVA | 2717 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
NENAGH | NENAGH_38-T42_10_MVA | 110 KV | 38 kV - MV | 1 | NENAGH_38 | T42_10_MVA | 3696 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
NENAGH | NENAGH_T422-T422_10_MVA | 110 KV | 38 kV - MV | 1 | NENAGH_T422 | T422_10_MVA | 3698 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
NENAGH | NENAGH_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | NENAGH_110 | T141_31_5MVA | 2792 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
NEW GURRANEBANE | NEW Gurranebane_38-T422_10_MVA | 38 KV | 38 kV - MV | 1 | NEW Gurranebane_38 | T422_10_MVA | 12968 | 41.6 | 21.4 |  | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
NEW KILMONEY-CARRIGALINE STATION | New Kilmoney-Carrigaline Station_38-T422_15_MVA | 38 KV | 38 kV - MV | 1 | New Kilmoney-Carrigaline Station_38 | T422_15_MVA | 12141 | 41.6 | 21.4 |  | 52 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
NEW MAYFIELD-RIVERSTOWN STATION | New Mayfield-Riverstown Station _110-T122_31.5_MVA | 110 KV | 110 kV - MV | 1 | New Mayfield-Riverstown Station _110 | T122_31.5_MVA | 12132 | 110 | 21.4 |  | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
NEW MONAGHAN | MONAGHAN__110-T123_31.5_MVA | 110 KV | 110 kV - MV | 1 | MONAGHAN__110 | T123_31.5_MVA | 13281 | 110 | 21.4 |  | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
NEW ROSS | NEW ROSS | 38 KV |  |  | NEW ROSS |  |  |  |  | 0 | 0 | Retired per central mapping FL list
NEW TINAHASK | New Tinahask_38-T422_15_MVA | 38 KV | 38 kV - MV | 1 | New Tinahask_38 | T422_15_MVA | 12976 | 41.6 | 21.4 |  | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
NEWBRIDGE | NEWBRIDGE_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | NEWBRIDGE_110 | T142_31_5MVA | 2721 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
NEWBRIDGE EAST | NEWBRIDGE EAST_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | NEWBRIDGE EAST_110 | T142_63_MVA | 13137 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
NEWBROOK | NEWBROOK-T42_5_MVA_NEWBROOK | 38 KV | 38 kV - MV | 1 | NEWBROOK | T42_5_MVA_NEWBROOK | 3872 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
NEWBURY | NEWBURY | 110 KV |  |  | NEWBURY |  |  |  |  | 0 | 0
NEWCASTLEWEST | Newcastlewest-T42_5_MVA NEWCASTLEWES | 38 KV | 38 kV - MV | 1 | Newcastlewest | T42_5_MVA NEWCASTLEWES | 3136 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
NEWMARKET (DR) | NEWMARKET (DR)-T41_10_MVA | 38 KV | 38 kV - MV | 1 | NEWMARKET (DR) | T41_10_MVA | 3336 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
NEWMARKET (SR) | NEWMARKET (SR)-T42_5_MVA NEWMARKET_SR | 38 KV | 38 kV - MV | 1 | NEWMARKET (SR) | T42_5_MVA NEWMARKET_SR | 3897 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
NEWPORT | NEWPORT-T421_5_MVA | 38 KV | 38 kV - MV | 1 | NEWPORT | T421_5_MVA | 3425 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
NEWTOWNCUNNINGHAM | Newtowncunningham-T42_5_MVA | 38 KV | 38 kV - MV | 1 | Newtowncunningham | T42_5_MVA | 3939 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
NEWTOWNSTALABAN | NEWTOWNSTALABAN | 38 KV |  |  | NEWTOWNSTALABAN |  |  |  |  | 0 | 0
NORTH CITY JUNCTION | North City Junction_110-T121_31.5_MVA | 110 KV | 110 kV - MV | 1 | North City Junction_110 | T121_31.5_MVA | 13046 | 110 | 21.4 |  | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
NORTH EAST CASHEL | North-East Cashel_110-T122_20_MVA | 110 KV | 110 kV - MV | 1 | North-East Cashel_110 | T122_20_MVA | 12237 | 110 | 21.4 |  | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 20 MVA | Mixed Gen/Demand
NORTH KERRY | NORTH KERRY | 220 kV |  |  | NORTH KERRY |  |  |  |  | 0 | 0
NORTH QUAYS | North Quays-T102_20MVA | 110 KV | 110 kV - MV | 1 | North Quays | T102_20MVA | 8228 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
NORTH WALL | NORTH WALL | 220 KV |  |  | NORTH WALL |  |  |  |  | 0 | 0
NOVARTIS | NOVARTIS | 38 KV |  |  | NOVARTIS |  |  |  |  | 0 | 0
NOWLAN PARK | NOWLAN PARK | 38 KV |  |  | NOWLAN PARK |  |  |  |  | 0 | 0 | Retired per central mapping FL list
NUTLEY LANE | Nutley Lane-T122_31.5_MVA | 110 KV | 110 kV - MV | 1 | Nutley Lane | T122_31.5_MVA | 13198 | 110 | 10.7 |  | 44 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 31.5 MVA | Mixed Gen/Demand
OAKFIELD | OAKFIELD-T42_10_MVA | 38 KV | 38 kV - MV | 1 | OAKFIELD | T42_10_MVA | 3380 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
OLDBAWN | OLD BAWN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | OLD BAWN | T42_10_MVA | 3607 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
OLDCASTLE | OLDCASTLE-T41_5_MVA_OLDCASTLE | 38 KV | 38 kV - MV | 1 | OLDCASTLE | T41_5_MVA_OLDCASTLE | 3980 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
OLDCASTLE | OLDCASTLE_T422-T422_5_MVA_OLDCASTLE | 38 KV | 38 kV - MV | 1 | OLDCASTLE_T422 | T422_5_MVA_OLDCASTLE | 3981 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
OLDCOURT | OLDCOURT | 110 KV |  |  | OLDCOURT |  |  |  |  | 0 | 0
OLDSTREET | OLDSTREET | 400 KV |  |  | OLDSTREET |  |  |  |  | 0 | 0
OLDTOWN | OLDTOWN | 38 KV |  |  | OLDTOWN |  |  |  |  | 0 | 0
ORANMORE | ORANMORE-T44_10_MVA | 38 KV | 38 kV - MV | 1 | ORANMORE | T44_10_MVA | 3911 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
OUGHTERARD | OUGHTERARD-T42_5_MVA OUGHTERARD | 38 KV | 38 kV - MV | 1 | OUGHTERARD | T42_5_MVA OUGHTERARD | 3843 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
OUGHTRAGH | OUGHTRAGH_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | OUGHTRAGH_110 | T141_31_5MVA | 2999 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
PALLAS | PALLAS-T42_5_MVA PALLAS | 38 KV | 38 kV - MV | 1 | PALLAS | T42_5_MVA PALLAS | 4012 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
PALMERSTOWN | PALMERSTOWN-T42_10_MVA PALMERSTOWN | 38 KV | 38 kV - MV | 1 | PALMERSTOWN | T42_10_MVA PALMERSTOWN | 3502 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
PARKMORE | PARKMORE-T42_5_MVA PARKMORE | 38 KV | 38 kV - MV | 1 | PARKMORE | T42_5_MVA PARKMORE | 4000 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
PARKROE | PARKROE | 38 kV |  |  | PARKROE |  |  |  |  | 0 | 0
PARKVIEW | PARKVIEW | 38 KV |  |  | PARKVIEW |  |  |  |  | 0 | 0
PATRICKSWELL | PATRICKSWELL-T422_5_MVA PATRICKSWELL | 38 KV | 38 kV - MV | 1 | PATRICKSWELL | T422_5_MVA PATRICKSWELL | 4171 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
PEARSE STREET | PEARSE STREET | 38 KV |  |  | PEARSE STREET |  |  |  |  | 0 | 0
PELLETSTOWN | PELLETSTOWN-T102_20MVA | 110 KV | 110 kV - MV | 1 | PELLETSTOWN | T102_20MVA | 8202 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
PEMBROKE | PEMBROKE-T44_10_MVA | 38 KV | 38 kV - MV | 1 | PEMBROKE | T44_10_MVA | 4262 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Three-38-MV | 38/10 kV - 3 x 10 MVA | Mixed Gen/Demand
PEMBROKE | PEMBROKE_T42-T42_10_MVA | 38 KV | 38 kV - MV | 2 | PEMBROKE_T42 | T42_10_MVA | 4263 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
PEMBROKE | Pembroke_110-T102_31.5_MVA | 38 KV | 110 kV - MV | 1 | Pembroke_110 | T102_31.5_MVA | 12853 | 110 | 10.7 |  | 44 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 31.5 MVA | Mixed Gen/Demand
PHIBSBORO | PHIBSBORO-T42_10_MVA | 38 KV | 38 kV - MV | 1 | PHIBSBORO | T42_10_MVA | 3508 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
PIPERHILL | PIPERHILL | 38 KV |  |  | PIPERHILL |  |  |  |  | 0 | 0
PLATIN | PLATIN | 110 KV |  |  | PLATIN |  |  |  |  | 0 | 0
POLLAPHUCA | POLLAPHUCA | 110 KV |  |  | POLLAPHUCA |  |  |  |  | 0 | 0
POLLERTON | POLLERTON-T42_10_MVA | 38 KV | 38 kV - MV | 1 | POLLERTON | T42_10_MVA | 3384 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
POOLBEG | POOLBEG | 220 KV |  |  | POOLBEG |  |  |  |  | 0 | 0
POPPINTREE | POPPINTREE-T102_20MVA | 110 KV | 110 kV - MV | 1 | POPPINTREE | T102_20MVA | 8216 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
POPPINTREE | POPPINTREE-T121_31.5_MVA | 110 KV | 110 kV - MV | 1 | POPPINTREE | T121_31.5_MVA | 12972 | 110 | 21.4 |  | 44 |  | Mixed-Standalone-110-MV | 110/20 kV - 1 x 31.5 MVA | Mixed Gen/Demand
PORTAN | PORTAN | 400 KV |  |  | PORTAN |  |  |  |  | 0 | 0
PORTARLINGTON | Portarlington-T42_5_MVA PORTARLINGTO | 38 KV | 38 kV - MV | 1 | Portarlington | T42_5_MVA PORTARLINGTO | 3068 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
PORTARLINGTON | Portarlington_T43-T43_5_MVA | 38 KV | 38 kV - MV | 2 | Portarlington_T43 | T43_5_MVA | 4194 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
PORTLAOISE | PORTLAOIS_38-T424_10_MVA | 110 KV | 38 kV - MV | 1 | PORTLAOIS_38 | T424_10_MVA | 3679 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
PORTLAOISE | PORTLAOIS_38-T42_10_MVA | 110 KV | 38 kV - MV | 1 | PORTLAOIS_38 | T42_10_MVA | 3676 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
PORTLAOISE | PORTLAOIS_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | PORTLAOIS_110-T142_31_5MVA |  |  |  |  | 32 | 0
PORTLAOISE | PORTLAOIS_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | PORTLAOIS_110 | T142_63_MVA | 2731 | 110 | 41.6 |  | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
PORTLAW | PORTLAW_38 | 38 KV | 38 kV - MV | 1 | PORTLAW_38 | T42_2_MVA PORTLAW | 3883 | 41.6 | 10.7 | 96 | 64 |  | Mixed-Uneven-38-MV | 38/10 kV (1x5MVA) + (1x2MVA) | Mixed Gen/Demand
PORTMARNOCK | PORTMARNOCK | 38 KV |  |  | PORTMARNOCK |  |  |  |  | 0 | 0
POTTERY ROAD | Pottery Road-T102_20MVA | 110 KV | 110 kV - MV | 1 | Pottery Road | T102_20MVA | 8226 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
PROSPECT | PROSPECT | 220 KV |  |  | PROSPECT |  |  |  |  | 0 | 0
PURCELLS INCH | Purcells Inch | 38 KV | 38 kV - MV | 1 | Purcells Inch | T41_5_MVA | 3907 | 41.6 | 10.7 | 96 | 64 |  | Mixed-Uneven-38-MV | 38/10 kV (1x5MVA) + (1x10MVA) | Mixed Gen/Demand
RAFFEEN | RAFFEEN | 220 KV |  |  | RAFFEEN |  |  |  |  | 0 | 0
RAHANS | RAHANS-T41_5_MVA | 38 KV | 38 kV - MV | 1 | RAHANS | T41_5_MVA | 3865 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
RAHEEN | RAHEEN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | RAHEEN | T42_10_MVA | 3765 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
RAHEEN (Lineschool) | RAHEEN (Lineschool) | 38 KV |  |  | RAHEEN (Lineschool) |  |  |  |  | 0 | 0
RAHEEN BARR | RAHEEN BARR | 38 KV |  |  | RAHEEN BARR |  |  |  |  | 0 | 0
RAHENY | RAHENY | 38 KV |  |  | RAHENY |  |  |  |  | 0 | 0
RAMPARTS | RAMPARTS-T42_10_MVA_RAMPARTS | 38 KV | 38 kV - MV | 1 | RAMPARTS | T42_10_MVA_RAMPARTS | 3108 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
RAMSTOWN | RAMSTOWN | 38 KV |  |  | RAMSTOWN |  |  |  |  | 0 | 0
RANDALSTOWN | RANDALSTOWN-T41_5_MVA_RANDALS | 38 KV | 38 kV - MV | 1 | RANDALSTOWN | T41_5_MVA_RANDALS | 3868 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
RANDALSTOWN | RANDALSTOWN_T422-T422_5_MVA_RANDALS | 38 KV | 38 kV - MV | 1 | RANDALSTOWN_T422 | T422_5_MVA_RANDALS | 3869 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
RATHCAHILL | RATHCAHILL | 38 KV |  |  | RATHCAHILL |  |  |  |  | 0 | 0
RATHDOWN | RATHDOWN | 38 KV |  |  | RATHDOWN |  |  |  |  | 0 | 0
RATHDOWNEY | RATHDOWNEY-T42_5_MVA | 38 KV | 38 kV - MV | 1 | RATHDOWNEY | T42_5_MVA | 3746 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
RATHDRUM | RATHDRUM-T42_5_MVA | 38 KV | 38 kV - MV | 1 | RATHDRUM | T42_5_MVA | 4050 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
RATHGOGGIN | RATHGOGGIN | 38 KV |  |  | RATHGOGGIN |  |  |  |  | 0 | 0
RATHKEALE | RATHKEALE_38-T422_10MVA | 110 KV | 38 kV - MV | 1 | RATHKEALE_38 | T422_10MVA | 3123 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
RATHKEALE | RATHKEALE_110-T142_30MVA | 110 KV | 110 - 38 kV | 1 | RATHKEALE_110 | T142_30MVA | 3681 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 30 MVA | Mixed Gen/Demand
RATHMORE | RATHMORE-T42_5_MVA | 38 KV | 38 kV - MV | 1 | RATHMORE | T42_5_MVA | 3344 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
RATHMORE | RATHMORE_T421-T421_5_MVA | 38 KV | 38 kV - MV | 1 | RATHMORE_T421 | T421_5_MVA | 3345 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
RATHMULLAN | RATHMULLAN-T42_10_MVA_RATHM | 38 KV | 38 kV - MV | 1 | RATHMULLAN | T42_10_MVA_RATHM | 3796 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
RATHRUSSAN | RATHRUSSAN | 110 KV |  |  | RATHRUSSAN |  |  |  |  | 0 | 0
REAMORE | REAMORE_T141-T141_63MVA | 110 KV | 110 - 38 kV | 1 | REAMORE_T141 | T141_63MVA | 3039 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
REAMORE | REAMORE_T142-T142_63MVA | 110 KV | 110 - 38 kV | 2 | REAMORE_T142 | T142_63MVA | 3040 | 110 | 41.6 |  | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
REANAGOWAN | REANAGOWAN | 38 kV |  |  | REANAGOWAN |  |  |  |  | 0 | 0
RECESS | RECESS-T41_5_MVA | 38 KV | 38 kV - MV | 1 | RECESS | T41_5_MVA | 4028 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
REDMONDSTOWN | REDMONDSTOWN | 38 KV |  |  | REDMONDSTOWN |  |  |  |  | 0 | 0
RICHFIELD | RICHFIELD | 38 KV |  |  | RICHFIELD |  |  |  |  | 0 | 0
RICHMOND | RICHMOND_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | RICHMOND_110 | T142_31_5MVA | 2737 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
RINAWADE | RINAWADE_110-T142_31.5_MVA | 110 KV | 110 - 38 kV | 1 | RINAWADE_110 | T142_31.5_MVA | 13166 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
RINAWADE | RINAWADE_38-T422_15_MVA | 110 KV | 38 kV - MV | 1 | RINAWADE_38 | T422_15_MVA | 13168 | 41.6 | 21.4 | 0 | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
RINEANNA | RINEANNA-T42_10_MVA | 38 KV | 38 kV - MV | 1 | RINEANNA | T42_10_MVA | 2757 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
RINGASKIDDY 110KV | RINGASKIDDY-T42_10_MVA | 110 KV | 38 kV - MV | 1 | RINGASKIDDY | T42_10_MVA | 3682 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
RINGASKIDDY 38KV | RINGASKIDDY 38KV | 38 KV |  |  | RINGASKIDDY 38KV |  |  |  |  | 0 | 0
RINGSEND | RINGSEND_R_110-T144_63MVA_Ringsend_Brown | 110 KV | 110 - 38 kV | 1 | RINGSEND_R_110 | T144_63MVA_Ringsend_Brown | 2803 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA (Mesh) | Mixed Gen/Demand
RINGSEND | RINGSEND_B_110-T102_20MVA | 110 KV | 110 kV - MV | 1 | RINGSEND_B_110 | T102_20MVA | 8251 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
RIVERS | RIVERS | 38 KV |  |  | RIVERS |  |  |  |  | 0 | 0
RIVERSTOWN | RIVERSTOWN-T42_5_MVA RIVERSTOWN | 38 KV | 38 kV - MV | 1 | RIVERSTOWN | T42_5_MVA RIVERSTOWN | 2952 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
ROCHES STREET | ROCHES ST-T42_10_MVA | 38 KV | 38 kV - MV | 1 | ROCHES ST | T42_10_MVA | 3588 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
ROCK HILL | ROCK HILL | 38 KV |  |  | ROCK HILL |  |  |  |  | 0 | 0
ROCKBORO ROAD | ROCKBORO ROAD | 110 kV |  |  | ROCKBORO ROAD |  |  |  |  | 0 | 0
ROOSKY | ROOSKEY-T41_5_MVA | 38 KV | 38 kV - MV | 1 | ROOSKEY | T41_5_MVA | 3823 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
ROSBERCON | ROSBERCON-T42_5_MVA | 38 KV | 38 kV - MV | 1 | ROSBERCON | T42_5_MVA | 3120 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
ROSBERCON | ROSBERCON-T424_15_MVA | 38 KV | 38 kV - MV | 1 | ROSBERCON | T424_15_MVA | 3122 | 41.6 | 21.4 |  | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 15 MVA (Gen only) | Gen Only
ROSCOMMON | ROSCOMMON-T42_10_MVA | 38 KV | 38 kV - MV | 1 | ROSCOMMON | T42_10_MVA | 2975 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
ROSCOMMON | ROSCOMMON-T421_5_MVA | 38 KV | 38 kV - MV | 1 | ROSCOMMON | T421_5_MVA | 13298 | 41.6 | 21.4 |  | 52 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 5 MVA (Gen only) | Gen Only
ROSCREA | ROSCREA-T42_10_MVA | 38 KV | 38 kV - MV | 1 | ROSCREA | T42_10_MVA | 4014 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
ROSEHILL | ROSEHILL-T42_10_MVA | 38 KV | 38 kV - MV | 1 | ROSEHILL | T42_10_MVA | 3170 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
ROSS CARBERY | Rosscarberry-T42_5_MVA | 38 KV | 38 kV - MV | 1 | Rosscarberry | T42_5_MVA | 3582 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
ROSSGEIR | Rossgier-T42_5_MVA | 38 KV | 38 kV - MV | 1 | Rossgier | T42_5_MVA | 3915 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
RUSHEEN | RUSHEEN | 0 |  |  | RUSHEEN |  |  |  |  | 0 | 0
RUSHFIELD | RUSHFIELD | 38 KV |  |  | RUSHFIELD |  |  |  |  | 0 | 0
RYEBROOK | RYEBROOK | 110 KV |  |  | RYEBROOK |  |  |  |  | 0 | 0
SAGGART | SAGGART-T42_5_MVA SAGGART | 38 KV | 38 kV - MV | 1 | SAGGART | T42_5_MVA SAGGART | 3102 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
SAINT JOSEPHS ROAD | SAINT JOSEPHS ROAD | 38 KV |  |  | SAINT JOSEPHS ROAD |  |  |  |  | 0 | 0 | Retired per central mapping FL list
SALLINS | SALLINS-T42_10_MVA_SALLINS | 38 KV | 38 kV - MV | 1 | SALLINS | T42_10_MVA_SALLINS | 3443 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
SALLYNOGGIN ROAD | SALLYNOGGIN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | SALLYNOGGIN | T42_10_MVA | 2967 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
SALTHILL | SALTHILL_110-T141_63MVA | 110 KV | 110 - 38 kV | 1 | SALTHILL_110 | T141_63MVA | 2915 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 63 MVA | Mixed Gen/Demand
SALTHILL | SALTHILL_110-T101_31.5_MVA | 110 KV | 110 kV - MV | 1 | SALTHILL_110 | T101_31.5_MVA | 9220 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 31.5 MVA | Mixed Gen/Demand
SANDYFORD | SANDYFORD-T42_10_MVA | 38 KV | 38 kV - MV | 1 | SANDYFORD | T42_10_MVA | 3477 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
SANTRY | SANTRY-T42_10_MVA | 38 KV | 38 kV - MV | 1 | SANTRY | T42_10_MVA | 3524 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
SCARIFF | SCARIFF-T42_5_MVA | 38 KV | 38 kV - MV | 1 | SCARIFF | T42_5_MVA | 3358 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
SCARTEEN | SCARTEEN-T42_5_MVA SCARTEEN | 38 KV | 38 kV - MV | 1 | SCARTEEN | T42_5_MVA SCARTEEN | 3303 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
SCREEB | SCREEB-T41_5_MVA | 110 KV | 38 kV - MV | 1 | SCREEB | T41_5_MVA | 3518 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
SCREEB | SCREEB_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | SCREEB_110 | T142_31_5MVA | 2973 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
SCREGGAN | SCREGGAN | 110 kV |  |  | SCREGGAN |  |  |  |  | 0 | 0
SEAFIELD | SEAFIELD | 38 KV |  |  | SEAFIELD |  |  |  |  | 0 | 0 | Retired per central mapping FL list
SEALROCK | SEALROCK | 110 KV |  |  | SEALROCK |  |  |  |  | 0 | 0
SEECON | SEECON | 110 kV |  |  | SEECON |  |  |  |  | 0 | 0
SEMPERIT | SEMPERIT-T43_10_MVA | 38 KV | 38 kV - MV | 1 | SEMPERIT | T43_10_MVA | 3598 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Three-38-MV | 38/10 kV - 3 x 10 MVA | Mixed Gen/Demand
SERPENTINE AVENUE | SERPENTINE AVENUE | 38 KV |  |  | SERPENTINE AVENUE |  |  |  |  | 0 | 0
SHALLOW | SHALLOW | 110 kV |  |  | SHALLOW |  |  |  |  | 0 | 0
SHANDON | SHANDON | 38 KV |  |  | SHANDON |  |  |  |  | 0 | 0 | Retired per central mapping FL list
SHANKILL | SHANKILL_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | SHANKILL_110 | T142_63MVA | 2742 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
SHANKILL (DART) | SHANKILL (DART) | 38 KV |  |  | SHANKILL (DART) |  |  |  |  | 0 | 0
SHANNON | SHANNON-T42_10_MVA | 38 KV | 38 kV - MV | 1 | SHANNON | T42_10_MVA | 3534 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
SHANNONBRIDGE | SHANNONBRIDGE | 220 KV |  |  | SHANNONBRIDGE |  |  |  |  | 0 | 0
SHELLYBANKS | SHELLYBANKS | 220 KV |  |  | SHELLYBANKS |  |  |  |  | 0 | 0
SHELTON ABBEY | SHELTON ABBEY | 110 KV |  |  | SHELTON ABBEY |  |  |  |  | 0 | 0
SHERCOCK | SHERCOCK-T42_5_MVA_SHERCOCK | 38 KV | 38 kV - MV | 1 | SHERCOCK | T42_5_MVA_SHERCOCK | 3983 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
SHERIFF STREET | SHERIFF ST-T42_10_MVA | 38 KV | 38 kV - MV | 1 | SHERIFF ST | T42_10_MVA | 4035 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
SHILLELAGH | SHILLELAGH-T422_5_MVA | 38 KV | 38 kV - MV | 1 | SHILLELAGH | T422_5_MVA | 4093 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
SINGLAND | SINGLAND_110-T101_20_MVA | 110 KV | 110 kV - MV | 1 | SINGLAND_110 | T101_20_MVA | 9235 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
SKIBBEREEN | SKIBBEREEN-T42_5_MVA SKIBBEREEN | 38 KV | 38 kV - MV | 1 | SKIBBEREEN | T42_5_MVA SKIBBEREEN | 3076 | 41.6 | 10.7 | 16 | 8 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
SKIBBEREEN | SKIBBEREEN-T42_10MVA | 38 KV | 38 kV - MV | 1 | SKIBBEREEN | T42_10MVA | 9302 | 41.6 | 10.7 | 16 | 56 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
SLANE | SLANE_T421-T421_10_MVA_SLANE | 38 KV | 38 kV - MV | 1 | SLANE_T421 | T421_10_MVA_SLANE | 3292 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
SLANE | SLANE-T422_10_MVA_SLANE | 38 KV | 38 kV - MV | 2 | SLANE | T422_10_MVA_SLANE | 3291 | 41.6 | 21.4 |  | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
SLIABH BAWN | SLIABH BAWN | 110 kV |  |  | SLIABH BAWN |  |  |  |  | 0 | 0
SLIEVECALLAN | SLIEVECALLAN | 110 KV |  |  | SLIEVECALLAN |  |  |  |  | 0 | 0
SLIGO | SLIGO_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | SLIGO_110 | T142_63MVA | 2746 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
SMEARLA | SMEARLA-T42_10_MVA | 38 KV | 38 kV - MV | 1 | SMEARLA | T42_10_MVA | 3164 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
SNOWHILL | SNOWHILL | 38 KV |  |  | SNOWHILL |  |  |  |  | 0 | 0
SNUGSBOROUGH | SNUGSBOROUGH | 110 KV |  |  | SNUGSBOROUGH |  |  |  |  | 0 | 0
SOMERSET | SOMERSET_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | SOMERSET_110 | T142_31_5MVA | 2619 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
SONNAGH | SONNAGH | 38 KV |  |  | SONNAGH |  |  |  |  | 0 | 0
SORNE HILL | SORNEHILL_T122-T122_31.5_MVA | 110 KV | 110 kV - MV | 1 | SORNEHILL_T122 | T122_31.5_MVA | 9455 | 110 | 21.4 | 0 | 64 |  | Generation-Standalone-110-MV | 110/20 kV - 1 x 31.5 MVA (Gen only) | Gen Only
SORNE HILL | SORNEHILL_T124-T124_40MVA | 110 KV | 110 kV - MV | 2 | SORNEHILL_T124 | T124_40MVA | 9465 | 110 | 21.4 |  | 64 |  | Generation-Standalone-110-MV | 110/20 kV - 1 x 40 MVA (Gen only) | Gen Only
SOUTH EAST CARLOW | South East Carlow_110-T122_31.5_MVA | 110 KV | 110 kV - MV | 1 | South East Carlow_110 | T122_31.5_MVA | 12193 | 110 | 21.4 |  | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
SOUTH HILL | SOUTH HILL | 38 KV |  |  | SOUTH HILL |  |  |  |  | 0 | 0 | Retired per central mapping FL list
SOUTH KING STREET | SOUTH KING S-T42_10_MVA SOUTH KING S | 38 KV | 38 kV - MV | 1 | SOUTH KING S | T42_10_MVA SOUTH KING S | 3381 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
SOUTH NAVAN | NAVAN_110-T122_31.5_MVA | 110 kV | 110 kV - MV | 1 | NAVAN_110 | T122_31.5_MVA | 13034 | 110 | 21.4 | 28 | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
SOUTHGREEN | SOUTHGREEN | 110 kV |  |  | SOUTHGREEN |  |  |  |  | 0 | 0
SPA ROAD | SPA ROAD-T42_5_MVA SPA ROAD | 38 KV | 38 kV - MV | 1 | SPA ROAD | T42_5_MVA SPA ROAD | 3273 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
SPADDEN | SPADDEN | 38 KV |  |  | SPADDEN |  |  |  |  | 0 | 0
SPIDDAL | SPIDDAL-T421_5_MVA | 38 KV | 38 kV - MV | 1 | SPIDDAL | T421_5_MVA | 3840 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
SPRINGS | SPRINGS-T422_10_MVA SPRINGS | 38 KV | 38 kV - MV | 1 | SPRINGS | T422_10_MVA SPRINGS | 4030 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
SRAH | SRAH-T42_5_MVA SRAH | 38 KV | 38 kV - MV | 1 | SRAH | T42_5_MVA SRAH | 3904 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
SRAH | SRAH_T43-T43_10_MVA | 38 KV | 38 kV - MV | 2 | SRAH_T43 | T43_10_MVA | 3905 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
SRANANAGH | SRANANAGH | 220 KV |  |  | SRANANAGH |  |  |  |  | 0 | 0
STEPHENSTOWN | STEPHENSTOWN_110-T102_20MVA | 110 KV | 110 kV - MV | 1 | STEPHENSTOWN_110 | T102_20MVA | 8180 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
STEEVENS LANE | Steevens Lane-T122_31.5_MVA | 110 KV | 110 kV - MV | 1 | Steevens Lane | T122_31.5_MVA | 13197 | 110 | 10.7 |  | 48 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 31.5 MVA | Mixed Gen/Demand
STICKILLEN | STICKILLEN-T42_5_MVA_STICKILLEN | 38 KV | 38 kV - MV | 1 | STICKILLEN | T42_5_MVA_STICKILLEN | 4089 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
STRABANE | STRABANE | 0 |  |  | STRABANE |  |  |  |  | 0 | 0
STRADBALLY ROAD | STRADBALLY ROAD | 38 KV |  |  | STRADBALLY ROAD |  |  |  |  | 0 | 0 | Retired per central mapping FL list
STRANORLAR | STRANORLAR-T422_10_MVA | 38 KV | 38 kV - MV | 1 | STRANORLAR | T422_10_MVA | 3014 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
STRATFORD | STRATFORD_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | STRATFORD_110 | T141_31_5MVA | 2812 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
STREAMHILL | STREAMHILL | 38 KV |  |  | STREAMHILL |  |  |  |  | 0 | 0
SUTTON | SUTTON-T42_10_MVA | 38 KV | 38 kV - MV | 1 | SUTTON | T42_10_MVA | 3546 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
SWINFORD | SWINFORD-T42_5_MVA SWINFORD | 38 KV | 38 kV - MV | 1 | SWINFORD | T42_5_MVA SWINFORD | 3832 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
SWORDS | SWORDS-T42_10_MVA_SWORDS | 38 KV | 38 kV - MV | 1 | SWORDS | T42_10_MVA_SWORDS | 4120 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
TALBOTS INCH | TALBOTS INCH-T42_5_MVA TALBOTS INCH | 38 KV | 38 kV - MV | 1 | TALBOTS INCH | T42_5_MVA TALBOTS INCH | 3944 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
TALBOTS INCH/ROSEHILL | Talbots Inch/Rosehill_38-T422_15_MVA | 38 KV | 38 kV - MV | 1 | Talbots Inch/Rosehill_38 | T422_15_MVA | 12246 | 41.6 | 21.4 |  | 52 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 15 MVA | Mixed Gen/Demand
TANDRAGEE | TANDRAGEE | 275 KV |  |  | TANDRAGEE |  |  |  |  | 0 | 0
TANEY | TANEY-T102_20MVA | 110 KV | 110 kV - MV | 1 | TANEY | T102_20MVA | 8232 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
TARBERT | TARBERT | 220 KV |  |  | TARBERT |  |  |  |  | 0 | 0
TAURBEG | TAURBEG | 38 KV |  |  | TAURBEG |  |  |  |  | 0 | 0
TAWNAGHMORE | Tawnaghmore_A_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | Tawnaghmore_A_110 | T142_31_5MVA | 4819 | 110 | 41.6 | 0 | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA (Gen only) | Gen Only
TELAYDON | TELAYDON-T42_10_MVA_TELAYDON | 38 KV | 38 kV - MV | 1 | TELAYDON | T42_10_MVA_TELAYDON | 3786 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
TELAYDON | TELAYDON_T421-T421_10_MVA_TELAYDON | 38 KV | 38 kV - MV | 1 | TELAYDON_T421 | T421_10_MVA_TELAYDON | 3787 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 10 MVA | Mixed Gen/Demand
TEMPLEMORE | TEMPLEMORE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | TEMPLEMORE | T42_10_MVA | 4027 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
TEMPLEOGUE | TEMPLEOGUE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | TEMPLEOGUE | T42_10_MVA | 3003 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
TERMONFECKIN ROAD | Termonfeckin Road-T42_5_MVA_TERMNF | 38 KV | 38 kV - MV | 1 | Termonfeckin Road | T42_5_MVA_TERMNF | 3429 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
THORNSBERRY | THORNSBERRY_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | THORNSBERRY_110 | T142_63MVA | 3694 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
THURLES | THURLES_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | THURLES_110 | T142_31_5MVA | 2749 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
TIEVEBRACK | TIEVEBRACK | 110 KV |  |  | TIEVEBRACK |  |  |  |  | 0 | 0
TIMOLEAGUE | TIMOLEAGUE-T41_5_MVA | 38 KV | 38 kV - MV | 1 | TIMOLEAGUE | T41_5_MVA | 3074 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
TIMOLEAGUE | TIMOLEAGUE_T422-T422_10_MVA | 38 KV | 38 kV - MV | 1 | TIMOLEAGUE_T422 | T422_10_MVA | 9068 | 41.6 | 21.4 |  | 64 |  | Generation-Standalone-38-MV | 38/20 kV - 1 x 10 MVA (Gen only) | Gen Only
TINAHASK | TINAHASK-T42_5_MVA TINAHASK | 38 KV | 38 kV - MV | 1 | TINAHASK | T42_5_MVA TINAHASK | 3601 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
TIPPERARY | TIPPERARY_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | TIPPERARY_110 | T141_31_5MVA | 2733 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
TOGHER | TOGHER-T42_10_MVA TOGHER | 38 KV | 38 kV - MV | 1 | TOGHER | T42_10_MVA TOGHER | 3552 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
TONROE | TONROE_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | TONROE_110 | T142_31_5MVA | 2732 | 110 | 41.6 | 32 | 20 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
TONROE | TONROE_110-T142_31.5_MVA | 110 KV | 110 - 38 kV | 1 | TONROE_110 | T142_31.5_MVA | 13326 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
TOOMEVARA | TOOMEVARA-T42_5_MVA | 38 KV | 38 kV - MV | 1 | TOOMEVARA | T42_5_MVA | 3711 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
TOSSY | TOSSY | 38 KV |  |  | TOSSY |  |  |  |  | 0 | 0
TOURNAFULLA | TOURNAFULLA | 38 KV |  |  | TOURNAFULLA |  |  |  |  | 0 | 0
TRABEG | TRABEG_110-T142_31_5MVA | 110 KV | 110 - 38 kV | 1 | TRABEG_110 | T142_31_5MVA | 3684 | 110 | 41.6 | 16 | 20 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
TRABEG | TRABEG_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | TRABEG_110 | T142_63_MVA | 9297 | 110 | 41.6 | 16 | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
TRABEG | TRABEG_110-T101_20MVA | 110 KV | 110 kV - MV | 1 | TRABEG_110-T101_20MVA | T101_20MVA | 8858 | 110 | 10.7 | 32 | 0
TRABEG | TRABEG_110-T102_20MVA | 110 KV | 110 kV - MV | 1 | TRABEG_110 | T102_20MVA | 8857 | 110 | 10.7 |  | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
TRALEE | TRALEE_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | TRALEE_110 | T142_63MVA | 2761 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
TRAMORE | TRAMORE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | TRAMORE | T42_10_MVA | 3541 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
TRIEN | TRIEN_110-T142_31_5_MV | 110 KV | 110 - 38 kV | 1 | TRIEN_110 | T142_31_5_MV | 2753 | 110 | 41.6 | 32 | 20 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
TRIEN | TRIEN_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | TRIEN_110 | T142_63_MVA | 12073 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
TRIEN | TRIEN_T143-T143_63MVA | 110 KV | 110 - 38 kV | 2 | TRIEN_T143 | T143_63MVA | 2751 | 110 | 41.6 |  | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 63 MVA (Gen only) | Gen Only
TRILLICK | TRILLICK_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | TRILLICK_110 | T141_31_5MVA | 3027 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
TRILLICK | TRILLICK_T142-T142_31_5MVA | 110 KV | 110 - 38 kV | 2 | TRILLICK_T142 | T142_31_5MVA | 3026 | 110 | 41.6 |  | 64 |  | Generation-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA (Gen only) | Gen Only
TRIM | TRIM-T42_5_MVA_TRIM | 38 KV | 38 kV - MV | 1 | TRIM | T42_5_MVA_TRIM | 3173 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
TRIM | TRIM_T421-T421_5_MVA_TRIM | 38 KV | 38 kV - MV | 1 | TRIM_T421 | T421_5_MVA_TRIM | 3175 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
TRIMMS LANE | TRIMMS LANE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | TRIMMS LANE | T42_10_MVA | 3805 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
TRINITY | TRINITY-T102_20MVA | 110 KV | 110 kV - MV | 1 | TRINITY | T102_20MVA | 8191 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
TUAM NORTH | TUAM NORTH-T42_5_MVA TUAM NORTH | 38 KV | 38 kV - MV | 1 | TUAM NORTH | T42_5_MVA TUAM NORTH | 3411 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
TUAM NORTH | TUAM NORTH-T42_15_MVA | 38 KV | 38 kV - MV | 1 | TUAM NORTH | T42_15_MVA | 12058 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
TUAM SOUTH | TUAM SOUTH-T42_5_MVA | 38 KV | 38 kV - MV | 1 | TUAM SOUTH | T42_5_MVA | 3775 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
TUBBERCURRY | TUBBERCURRY-T42_5_MVA | 38 KV | 38 kV - MV | 1 | TUBBERCURRY | T42_5_MVA | 3586 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 5 MVA | Mixed Gen/Demand
TULLA | TULLA-T42_5_MVA | 38 KV | 38 kV - MV | 1 | TULLA | T42_5_MVA | 3131 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
TULLABRACK | TULLABRACK_110-T141_31_5MVA | 110 KV | 110 - 38 kV | 1 | TULLABRACK_110 | T141_31_5MVA | 2762 | 110 | 41.6 | 32 | 64 |  | Mixed-Standalone-110-38 | 110/38 kV - 1 x 31.5 MVA | Mixed Gen/Demand
TULLAMORE | TULLAMORE | 38 KV |  |  | TULLAMORE |  |  |  |  | 0 | 0 | Retired per central mapping FL list
TULLOW | TULLOW-T422_10_MVA | 38 KV | 38 kV - MV | 1 | TULLOW | T422_10_MVA | 3485 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
TULLYLEASE | TULLYLEASE | 38 kV |  |  | TULLYLEASE |  |  |  |  | 0 | 0
TULLYNAMALRA | TULLYNAMALRA-T42_5MVA_TULLYN | 38 KV | 38 kV - MV | 1 | TULLYNAMALRA | T42_5MVA_TULLYN | 3874 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
TURLOUGH HILL | TURLOUGH HILL | 220 KV |  |  | TURLOUGH HILL |  |  |  |  | 0 | 0
TURLOUGH ROAD | Turlough Road-T42_5_MVA | 38 KV | 38 kV - MV | 1 | Turlough Road | T42_5_MVA | 3811 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
TURSILLAGH | TURSILLAGH | 38 KV |  |  | TURSILLAGH |  |  |  |  | 0 | 0
TYCOR | TYCOR-T42_5_MVA | 38 KV | 38 kV - MV | 1 | TYCOR | T42_5_MVA | 3473 | 41.6 | 10.7 | 32 | 20 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
TYCOR | TYCOR-T42_15_MVA | 38 KV | 38 kV - MV | 1 | TYCOR | T42_15_MVA | 12875 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
TYMON | TYMON-T42_10_MVA | 38 KV | 38 kV - MV | 1 | TYMON | T42_10_MVA | 3799 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
TYNAGH | TYNAGH | 220 KV |  |  | TYNAGH |  |  |  |  | 0 | 0
TYONE | TYONE | 38 KV |  |  | TYONE |  |  |  |  | 0 | 0 | Retired per central mapping FL list
UGGOOL | UGGOOL | 110 KV |  |  | UGGOOL |  |  |  |  | 0 | 0
UNIDARE | UNIDARE-T42_10_MVA | 38 KV | 38 kV - MV | 1 | UNIDARE | T42_10_MVA | 3394 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
URLINGFORD | URLINGFORD-T422_5_MVA | 38 kV | 38 kV - MV | 1 | URLINGFORD | T422_5_MVA | 12889 | 41.6 | 21.4 | 0 | 60 |  | Mixed-Standalone-38-MV | 38/20 kV - 1 x 5 MVA | Mixed Gen/Demand
VACORNEEN | VACORNEEN | 38 kV |  |  | VACORNEEN |  |  |  |  | 0 | 0
VIRGINIA | VIRGINIA-T42_5_MVA_VIRGINIA | 38 KV | 38 kV - MV | 1 | VIRGINIA | T42_5_MVA_VIRGINIA | 3852 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
WALLINGSTOWN | WALLINGSTOWN | 38 KV |  |  | WALLINGSTOWN |  |  |  |  | 0 | 0 | Retired per central mapping FL list
WALTERSTOWN | Walterstown_110-T142_63_MVA | 110 KV |  |  | Walterstown_110 | T142_63_MVA | 12257 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
WALTERSTOWN | Walterstown_38-T422_10_MVA | 110 KV |  |  | Walterstown_38 | T422_10_MVA | 12258 | 41.6 | 21.4 |  | 44 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
WATERFORD | WATERFORD_38-T42_5_MVA | 110 KV | 38 kV - MV | 1 | WATERFORD_38 | T42_5_MVA | 3686 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 5 MVA | Mixed Gen/Demand
WATERFORD | WATERFORD_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | WATERFORD_110 | T142_63MVA | 2764 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
WATERFORD IND EST | WATERFORD IN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | WATERFORD IN | T42_10_MVA | 3573 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
WATLING STREET | Watling Street-T42_10_MVA | 38 KV | 38 kV - MV | 1 | Watling Street | T42_10_MVA | 3599 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
WEST PORTLAOISE | West Portlaoise_110-T142_31.5_MVA | 110 KV | 110 - 38 kV | 1 | West Portlaoise_110 | T142_31.5_MVA | 13089 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 31.5 MVA | Mixed Gen/Demand
WEST PORTLAOISE | West Portlaoise_110-T122_31.5_MVA | 110 KV | 110 kV - MV | 1 | West Portlaoise_110 | T122_31.5_MVA | 13345 | 110 | 21.4 |  | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
WESTPORT | WESTPORT-T422_10_MVA WESTPORT | 38 KV | 38 kV - MV | 1 | WESTPORT | T422_10_MVA WESTPORT | 2878 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
WEXFORD | WEXFORD_110-T142_63MVA | 110 KV | 110 - 38 kV | 1 | WEXFORD_110 | T142_63MVA | 4807 | 110 | 41.6 | 32 | 64 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
WEXFORD | WEXFORD_110-T122_20MVA | 110 KV | 110 kV - MV | 1 | WEXFORD_110 | T122_20MVA | 4808 | 110 | 21.4 | 32 | 64 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 20 MVA | Mixed Gen/Demand
WHITEBANK | WHITEBANK | 110 KV |  |  | WHITEBANK |  |  |  |  | 0 | 0
WHITECHURCH | WHITECHURCH-T422_10_MVA | 38 KV | 38 kV - MV | 1 | WHITECHURCH | T422_10_MVA | 3081 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 10 MVA | Mixed Gen/Demand
WHITEGATE | WHITEGATE | 110 KV |  |  | WHITEGATE |  |  |  |  | 0 | 0
WHITEHALL | WHITEHALL-T41_10_MVA | 38 KV | 38 kV - MV | 1 | WHITEHALL | T41_10_MVA | 3132 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Standalone-38-MV | 38/10 kV - 1 x 10 MVA | Mixed Gen/Demand
WHITESTOWN | WHITESTOWN-T42_10_MVA | 38 KV | 38 kV - MV | 1 | WHITESTOWN | T42_10_MVA | 3798 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
WICKLOW | WICKLOW | 38 KV |  |  | WICKLOW |  |  |  |  | 0 | 0 | Retired per central mapping FL list
WILTON | Wilton_110-T142_63_MVA | 110 KV | 110 - 38 kV | 1 | Wilton_110 | T142_63_MVA | 12907 | 110 | 41.6 |  | 44 |  | Mixed-Dual-110-38 | 110/38 kV - 2 x 63 MVA | Mixed Gen/Demand
WILTON | Wilton_38-T42_15_MVA | 110 KV | 38 kV - MV | 1 | Wilton_38 | T42_15_MVA | 12910 | 41.6 | 10.7 |  | 44 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 15 MVA | Mixed Gen/Demand
WINDSOR | Windsor Road-T422_5_MVA | 38 KV | 38 kV - MV | 1 | Windsor Road | T422_5_MVA | 4057 | 41.6 | 21.4 | 32 | 64 |  | Mixed-Dual-38-MV | 38/20 kV - 2 x 5 MVA | Mixed Gen/Demand
WOLFE TONE STREET | Wolfe Tone Street-T102_20MVA | 110 KV | 110 kV - MV | 1 | Wolfe Tone Street | T102_20MVA | 8195 | 110 | 10.7 | 32 | 64 |  | Mixed-Dual-110-MV | 110/10 kV - 2 x 20 MVA | Mixed Gen/Demand
WOODFORD | WOODFORD-T42_10_MVA WOODFORD | 38 KV | 38 kV - MV | 1 | WOODFORD | T42_10_MVA WOODFORD | 3457 | 41.6 | 10.7 | 32 | 64 |  | Mixed-Dual-38-MV | 38/10 kV - 2 x 10 MVA | Mixed Gen/Demand
WOODHOUSE | WOODHOUSE | 110 KV |  |  | WOODHOUSE |  |  |  |  | 0 | 0
WOODLAND | WOODLAND | 400 KV |  |  | WOODLAND |  |  |  |  | 0 | 0
YELLOWMEADOWS | YELLOWMEADOWS_A1-T124_31.5_MVA | 110 KV | 110 kV - MV | 1 | YELLOWMEADOWS_A1 | T124_31.5_MVA | 13056 | 110 | 21.4 |  | 44 |  | Mixed-Dual-110-MV | 110/20 kV - 2 x 31.5 MVA | Mixed Gen/Demand
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To Allign with Station Coordinates
Note on E2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: =COUNTIFS([Station Name],[@[Station Name]],[Vn2 '[kV']],[@[Vn2 '[kV']]])
Note on K3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: =COUNTIF('T:\ESB Networks Projects\PSS Sincal model for ESB Networks\11. NDP - Capacity Workbooks\Phase 2 Transformer and Line Capacity Workbook\[Demand Capacity Headroom Report V0.3.xlsx]Master Results Sheet'!$Q:$Q,ConnectionMethods[@[SINCAL Name]:[SINCAL Name]])
Note on A346: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AKA Loughteeog
Note on A441: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Barrysparks
Note on A661: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is this connection still available?
Note on A767: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: AKA Meenbog
Note on A902: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: (Lineschool)
Note on A988: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 018000?

## Traffo Lookup (hidden)
Element_ID | Node 1 | Node 2 | Element Name | Vn1 [kV] | Vn2 [kV] | Frequency of occurrence | Orig order | present in Master results?
2589 | DEANSGRANGE | DEANSGR2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 1 | 0
2602 | PORTLAOI3_10 | PORTLAOI1_20 | IFT_5_MVA | 10.7 | 21.4 | 0 | 2 | 0
2612 | DONEGAL1_10 | DONEGAL2_20 | T22_5MVA | 10.7 | 21.4 | 0 | 3 | 0
2613 | DONEGAL2_10 | DONEGAL1_20 | T21_5MVA | 10.7 | 21.4 | 0 | 4 | 0
2614 | STRANORL2_20 | STRANORL_10 | T21_5_MVA | 21.4 | 10.7 | 0 | 5 | 0
2620 | Mount Merrion | MT MERRI1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 6 | 0
2621 | Mount Merrion | MT MERRI2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 7 | 64
2637 | GRANBY ROW | GRANBY RW_10 | T41_15_MVA | 41.6 | 10.7 | 1 | 8 | 64
2656 | CAMDEN ROW | CAMDEN RW_10 | T41_15_MVA | 41.6 | 10.7 | 1 | 9 | 64
2689 | Merrion Square | MERRION 1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 10 | 0
2690 | Merrion Square | MERRION 2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 11 | 64
2725 | KINGSBRIDGE | KINGSBDGE_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 12 | 0
2726 | KINGSBRIDGE | KINGSBRDG_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 13 | 64
2738 | BALLYSHANNON | BALYSHAN1_10 | T41_5_MVA_BALYS | 41.6 | 10.7 | 0 | 14 | 0
2739 | BALLYSHANNON | BALYSHAN2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 15 | 64
2756 | RINEANNA | RINEANN1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 16 | 0
2757 | RINEANNA | RINEANN2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 17 | 64
2758 | BALLYHALE | BALLYHALE_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 18 | 64
2759 | BALLYHALE | BALLYHALE_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 19 | 0
2780 | Kilgarvin | KILGARV_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 20 | 64
2783 | DEANSGRANGE | DEANSGR1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 21 | 64
2798 | BANTRY | BANTRY1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 22 | 0
2799 | BANTRY | BANTRY2_10 | T42_5_MVA BANTRY | 41.6 | 10.7 | 1 | 23 | 64
2815 | East Wall Road | EWR_B1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 24 | 0
2816 | East Wall Road | EWR_B2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 25 | 64
2827 | FAIRVIEW | FAIRVIEW_10 | T41_15_MVA | 41.6 | 10.7 | 1 | 26 | 64
2849 | GLASNEVIN | GLASNEVIN_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 27 | 64
2865 | Gloucester Place | GLOUCES1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 28 | 64
2866 | Gloucester Place | GLOUCES2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 29 | 0
2877 | WESTPORT | WESTPORT1_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 30 | 0
2878 | WESTPORT | WESTPORT2_20 | T422_10_MVA WESTPORT | 41.6 | 21.4 | 1 | 31 | 64
2890 | COLLOONEY | COLLOONY1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 32 | 0
2891 | COLLOONEY | COLLOONY2_20 | T422_5_MVA Collooney | 41.6 | 21.4 | 1 | 33 | 64
2902 | BALLINASLOE | BALLINAS1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 34 | 0
2903 | BALLINASLOE | BALLINAS2_10 | T42_5_MVA BALLINASLOE | 41.6 | 10.7 | 1 | 35 | 64
2917 | KANTURK | KANTURK1_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 36 | 0
2918 | KANTURK | KANTURK2_10 | T42_5_MVA KANTURK | 41.6 | 10.7 | 1 | 37 | 4
2931 | MORRISTOWN | MORRIST1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 38 | 20
2932 | MORRISTOWN | MORRIST2_10 | T41_5_MVA MORRISTOWN | 41.6 | 10.7 | 1 | 39 | 0
2933 | KINGSCOURT | KINGSCO1_10 | T41_10_MVA_KINGSCOURT | 41.6 | 10.7 | 0 | 40 | 0
2934 | KINGSCOURT | KINGSCO2_10 | T42_10_MVA_KINGSCOURT | 41.6 | 10.7 | 1 | 41 | 64
2935 | KINGSCOURT | KINGSCOUR_20 | T423_15MVA_KINGSCOURT | 41.6 | 21.4 | 1 | 42 | 64
2940 | DELVIN | DELVIN1_10 | T41_5_MVA_DELVIN | 41.6 | 10.7 | 1 | 43 | 0
2941 | DELVIN | DELVIN2_10 | T42_3.2_MVA_DELVIN | 41.6 | 10.7 | 1 | 44 | 12
2942 | AGHAMORE | AGHAMOR1_10 | T41_2_MVA | 41.6 | 10.7 | 0 | 45 | 0
2943 | AGHAMORE | AGHAMOR2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 46 | 64
2944 | KILSHANNY | KILSHAN1_10 | T41_2_MVA | 41.6 | 10.7 | 0 | 47 | 0
2945 | KILSHANNY | KILSHAN2_10 | T42_2_MVA KILSHANNY | 41.6 | 10.7 | 1 | 48 | 64
2946 | BALLINACURRA | BALLINAC1_10 | T42_10_MVA | 41.6 | 10.7 | 0 | 49 | 0
2947 | BALLINACURRA | BALLINAC2_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 50 | 64
2948 | LOUGHTAGALLA | LOUGHTA1_10 | T42_5_MVA LOUGHTAGALLA | 41.6 | 10.7 | 1 | 51 | 64
2949 | LOUGHTAGALLA | LOUGHTA2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 52 | 0
2950 | MARROWBONE LANE | MARROWBON_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 53 | 64
2951 | RIVERSTOWN | RIVERST1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 54 | 0
2952 | RIVERSTOWN | RIVERST2_10 | T42_5_MVA RIVERSTOWN | 41.6 | 10.7 | 1 | 55 | 64
2953 | GRAIGUE | GRAIGUE1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 56 | 64
2954 | GRAIGUE | GRAIGUE2_10 | T41_10_MVA GRAIGUE | 41.6 | 10.7 | 0 | 57 | 0
2957 | Edgeworthstown | EDGEWORT1_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 58 | 0
2958 | Edgeworthstown | EDGEWORT2_20 | T422_10_MVA EDGEWORT2_20 | 41.6 | 21.4 | 1 | 59 | 64
2962 | LOUGHREA | LOUGHRE1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 60 | 0
2963 | LOUGHREA | LOUGHRE2_10 | T42_5_MVA LOUGHREA | 41.6 | 10.7 | 1 | 61 | 64
2966 | SALLYNOGGIN | SALLYNOG1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 62 | 0
2967 | SALLYNOGGIN | SALLYNOG2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 63 | 64
2970 | DUNDRUM | DUNDRUM1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 64 | 64
2971 | DUNDRUM | DUNDRUM2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 65 | 0
2972 | LOUGHDOO_38 | LOUGHDOO_20 | T32_12MVA | 41.6 | 21.4 | 0 | 66 | 0
2974 | ROSCOMMON | ROSCOMM1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 67 | 0
2975 | ROSCOMMON | ROSCOMM2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 68 | 64
2976 | KILFLYNN | KILFLYNN_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 69 | 64
2977 | BAILIEBORO | BAILIEBO1_10 | T41_5_MVA_BAILIEBORO | 41.6 | 10.7 | 0 | 70 | 0
2978 | BAILIEBORO | BAILIEBO2_10 | T42_5_MVA_BAILIEBORO | 41.6 | 10.7 | 1 | 71 | 64
2979 | BAILIEBORO | BAILIEBORO1_20 | T423_15_MVA_BAILIEBORO | 41.6 | 21.4 | 1 | 72 | 64
2980 | Ballyjamesduff | BALLYJA1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 73 | 0
2981 | Ballyjamesduff | BALLYJA2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 74 | 64
2982 | ATHENRY | ATHENRY1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 75 | 0
2983 | ATHENRY | ATHENRY2_10 | T42_5_MVA_ATHENRY | 41.6 | 10.7 | 1 | 76 | 64
2984 | CASTLECOMER | CASTLEC1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 77 | 20
2985 | CASTLECOMER | CASTLEC2_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 78 | 0
2995 | KIMMAGE | KIMMAGE1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 79 | 0
2996 | KIMMAGE | KIMMAGE2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 80 | 64
3002 | TEMPLEOGUE | TEMPLEOG_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 81 | 0
3003 | TEMPLEOGUE | TEMPLEOG_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 82 | 64
3004 | LUMCLOON | LUMCLOON1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 83 | 0
3005 | LUMCLOON | LUMCLOON2_20 | T422_5_MVA LUMCLOON | 41.6 | 21.4 | 1 | 84 | 64
3010 | DONEGAL | DONEGAL1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 85 | 0
3011 | DONEGAL | DONEGAL2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 86 | 64
3012 | KILDARE | KILDARE1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 87 | 0
3013 | KILDARE | KILDARE2_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 88 | 64
3014 | STRANORLAR | STRANORL1_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 89 | 64
3015 | STRANORLAR | STRANORL2_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 90 | 0
3021 | BRUFF | BRUFF2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 91 | 64
3022 | BRUFF_T421 | BRUFF_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 92 | 64
3023 | CAPPAMORE | CAPPAMOR1_10 | T42_5_MVA CAPPAMORE | 41.6 | 10.7 | 1 | 93 | 64
3024 | CAPPAMORE | CAPPAMOR2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 94 | 0
3025 | CAPPAMORE | CAPPAMOR3_20 | T424_10_MVA | 41.6 | 21.4 | 0 | 95 | 0
3030 | BIRDHILL | BIRDHILL1_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 96 | 0
3031 | BIRDHILL | BIRDHILL2_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 97 | 64
3043 | CASTLEKNOCK | CASTLEKN1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 98 | 0
3044 | CASTLEKNOCK | CASTLEKN2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 99 | 64
3058 | DRUMDOWNEY | DRUMDOWNEY_6 | CUST_8_MVA | 41.6 | 6.6 | 0 | 100 | 0
3059 | DRUMBEAR | DRUMBEAR1_10 | T42_5_MVA_DRUMBEAR | 41.6 | 10.7 | 2 | 101 | 16
3060 | DRUMBEAR | DRUMBEAR2_10 | T41_5_MVA_DRUMBEAR | 41.6 | 10.7 | 0 | 102 | 0
3061 | CARRIGALLEN | CARRIGALL_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 103 | 64
3062 | CARRIGAL_38B | CARRIGALLEN | BOOSTER | 41.6 | 41.6 | 0 | 104 | 0
3063 | ENNISTYMON | ENNISTY1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 105 | 0
3064 | ENNISTYMON | ENNISTY2_10 | T42_5_MVA ENNISTYMON | 41.6 | 10.7 | 2 | 106 | 20
3065 | DERRYNADIVVA | DERYNDIVA_WF | T421_18MVA | 41.6 | 21.4 | 0 | 107 | 0
3066 | NAAS | NAAS1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 108 | 0
3067 | NAAS | NAAS2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 109 | 64
3068 | Portarlington | PORTARL1_10 | T42_5_MVA PORTARLINGTO | 41.6 | 10.7 | 1 | 110 | 64
3069 | Portarlington | PORTARL2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 111 | 0
3070 | CONVOY | CONVOY1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 112 | 0
3071 | CONVOY | CONVOY2_10 | T42_10_MVA CONVOY | 41.6 | 10.7 | 1 | 113 | 64
3074 | TIMOLEAGUE | TIMOLEAGE_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 114 | 64
3075 | SKIBBEREEN | SKIBBERE1_10 | SKIBBEREEN T41_5_MVA | 41.6 | 10.7 | 0 | 115 | 0
3076 | SKIBBEREEN | SKIBBERE2_10 | T42_5_MVA SKIBBEREEN | 41.6 | 10.7 | 2 | 116 | 8
3077 | CLONAKILTY | CLONAKI1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 117 | 0
3078 | CLONAKILTY | CLONAKI2_10 | T42_5_MVA CLONAKILTY | 41.6 | 10.7 | 2 | 118 | 20
3079 | CARRIGALINE | CARRIGA1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 119 | 0
3080 | CARRIGALINE | CARRIGA2_10 | T42_5_MVA CARRIGALINE | 41.6 | 10.7 | 1 | 120 | 64
3081 | WHITECHURCH | WHITECHR1_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 121 | 64
3082 | WHITECHURCH | WHITECHR2_20 | T421_10_MVA WHITECHURCH | 41.6 | 21.4 | 0 | 122 | 0
3084 | Mornington Road | MORNING1_10 | T41_10_MVA_MORNINGTON | 41.6 | 10.7 | 0 | 123 | 0
3085 | Mornington Road | MORNING2_10 | T42_10_MVA_MORNINGTON | 41.6 | 10.7 | 1 | 124 | 64
3089 | CASHEL | CASHEL1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 125 | 64
3090 | CASHEL | CASHEL2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 126 | 0
3091 | CELBRIDGE | CELBRID1_10 | T41_10_MVA_CELBRIDGE | 41.6 | 10.7 | 0 | 127 | 0
3092 | CELBRIDGE | CELBRID2_10 | T42_10_MVA_CELBRIDGE | 41.6 | 10.7 | 1 | 128 | 64
3095 | LOUGHSHINNY | LOUGHSH1_10 | T42_10_MVA_LOUGHSHINNY | 41.6 | 10.7 | 1 | 129 | 64
3096 | LOUGHSHINNY | LOUGHSH2_10 | T41_10_MVA_LOUGHSHINNY | 41.6 | 10.7 | 0 | 130 | 0
3101 | SAGGART | SAGGART1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 131 | 0
3102 | SAGGART | SAGGART2_10 | T42_5_MVA SAGGART | 41.6 | 10.7 | 1 | 132 | 64
3103 | BALLYRICKARD | BALLYRIC1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 133 | 64
3104 | BALLYRICKARD | BALLYRIC2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 134 | 0
3105 | MULGANNON | MULGANNO1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 135 | 0
3106 | MULGANNON | MULGANNO2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 136 | 64
3107 | RAMPARTS | RAMPARTS1_10 | T41_10_MVA_RAMPARTS | 41.6 | 10.7 | 0 | 137 | 0
3108 | RAMPARTS | RAMPARTS2_10 | T42_10_MVA_RAMPARTS | 41.6 | 10.7 | 1 | 138 | 64
3112 | ATHBOY | ATHBOY2_10 | T42_5_MVA_ATHBOY | 41.6 | 10.7 | 1 | 139 | 64
3113 | ATHBOY_T423 | ATHBOY_20 | T423_5_MVA_ATHBOY | 41.6 | 21.4 | 1 | 140 | 64
3114 | Cloughkeating | CLOUGHKE1_20 | T421_15_MVA CUSTOMER | 41.6 | 21.4 | 0 | 141 | 0
3115 | Cloughkeating | CLOUGHKE2_20 | T422_15_MVA CUSTOMER | 41.6 | 21.4 | 0 | 142 | 0
3120 | ROSBERCON | ROSBERCON_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 143 | 64
3121 | ROSBERCON | ROSBERCO2_10 | T41_2_MVA | 41.6 | 10.7 | 0 | 144 | 0
3122 | ROSBERCON | ROSBERCO3_20 | T424_15_MVA | 41.6 | 21.4 | 1 | 145 | 64
3123 | RATHKEALE_38 | RATHKEAL2_20 | T422_10MVA | 41.6 | 21.4 | 1 | 146 | 64
3124 | RATHKEALE_38 | RATHKEAL1_20 | T421_10MVA | 41.6 | 21.4 | 0 | 147 | 0
3125 | KELLS | KELLS1_10 | T41_5_MVA_KELLS | 41.6 | 10.7 | 0 | 148 | 0
3126 | KELLS | KELLS2_10 | T42_5_MVA_KELLS | 41.6 | 10.7 | 1 | 149 | 64
3128 | CREGG ROAD | CREGG R1_10 | T42_2_MVA_CREGG ROAD | 41.6 | 10.7 | 1 | 150 | 64
3129 | CREGG ROAD | CREGG R2_10 | T41_2_MVA | 41.6 | 10.7 | 0 | 151 | 0
3130 | TULLA | TULLA1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 152 | 0
3131 | TULLA | TULLA2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 153 | 64
3132 | WHITEHALL | WHITEHALL_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 154 | 64
3133 | Castleblayney | CASTLEB1_10 | T41_10MVA_CASTLEBLAYNEY | 41.6 | 10.7 | 0 | 155 | 0
3134 | Castleblayney | CASTLEB2_10 | T42_10MVA_CASTLEBLAYENY | 41.6 | 10.7 | 1 | 156 | 64
3136 | Newcastlewest | NEWCAST1_10 | T42_5_MVA NEWCASTLEWES | 41.6 | 10.7 | 1 | 157 | 64
3137 | Newcastlewest | NEWCAST2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 158 | 0
3148 | Cahercalla | CAHIRCALL1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 159 | 0
3149 | Cahercalla | CAHIRCALL2_10 | T42_5_MVA CAHIRCALLA | 41.6 | 10.7 | 1 | 160 | 64
3156 | CARRIGLAWN | CARRIGLW1_10 | T42_5_MVA CARRIGLAWN | 41.6 | 10.7 | 1 | 161 | 64
3157 | CARRIGLAWN | CARRIGLW2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 162 | 0
3163 | SMEARLA | SMEARLA1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 163 | 0
3164 | SMEARLA | SMEARLA2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 164 | 64
3165 | GRANGE (SR) | GRANGE1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 165 | 0
3166 | GRANGE (SR) | GRANGE2_10 | T42_5_MVA GRANGE-SR | 41.6 | 10.7 | 1 | 166 | 64
3167 | GWEEDORE | GWEEDORE_20 | T421_5MVA | 41.6 | 21.4 | 1 | 167 | 64
3168 | GWEEDORE | GWEEDORE_38B | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 168 | 0
3169 | ROSEHILL | ROSEHILL1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 169 | 0
3170 | ROSEHILL | ROSEHILL2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 170 | 64
3171 | CORBALLY | CORBALL1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 171 | 64
3172 | CORBALLY | CORBALL2_10 | T41_5_MVA CORBALLY | 41.6 | 10.7 | 0 | 172 | 0
3173 | TRIM | TRIM1_10 | T42_5_MVA_TRIM | 41.6 | 10.7 | 1 | 173 | 64
3174 | TRIM | TRIM2_10 | T41_5_MVA_TRIM | 41.6 | 10.7 | 0 | 174 | 0
3175 | TRIM_T421 | TRIM1_20 | T421_5_MVA_TRIM | 41.6 | 21.4 | 1 | 175 | 64
3177 | BALLYBODEN | BALLYBO1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 176 | 0
3178 | BALLYBODEN | BALLYBO2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 177 | 64
3183 | Loughlinstown | LOUGHLIN1_10 | T42_10_MVA LOUGHLINSTWN | 41.6 | 10.7 | 1 | 178 | 64
3184 | Loughlinstown | LOUGHLIN2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 179 | 0
3185 | BALLYHALE_20 | BALLYHALE_10 | T21_5_MVA | 21.4 | 10.7 | 0 | 180 | 0
3189 | DUNMANWAY_20 | DUNMANWAY1_10 | T21_5_MVA | 21.4 | 10.7 | 0 | 181 | 0
3190 | TRAMORE1_10 | TRAMORE1_20 | T21_3_MVA | 10.7 | 21.4 | 0 | 182 | 0
3191 | TRAMORE2_10 | TRAMORE2_20 | T22_3_MVA | 10.7 | 21.4 | 0 | 183 | 0
3192 | GARRANA1_20 | GARRANA2_10 | T21_3MVA | 21.4 | 10.7 | 0 | 184 | 0
3193 | GARRANA1_20 | GARRANA3_10 | T22_3MVA | 21.4 | 10.7 | 0 | 185 | 0
3194 | GARRANA2_20 | GARRANA_10 | T23_3MVA | 21.4 | 10.7 | 0 | 186 | 0
3200 | ARDNAREE1_20 | ARDNAREE2_10 | T1_5_MVA | 21.4 | 10.7 | 0 | 187 | 0
3207 | MERVILLE | MERVILLE_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 188 | 0
3208 | MERVILLE | MERVILLE_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 189 | 64
3210 | BANTRY1_20 | BANTRY2_10 | T12_3_MVA | 21.4 | 10.7 | 0 | 190 | 0
3213 | BAILIEBO_20 | BAILIEBO2_10 | T12_5MVA | 21.4 | 10.7 | 0 | 191 | 0
3214 | LUMCLOON2_20 | LUMCLOON1_10 | T22_5_MVA | 21.4 | 10.7 | 0 | 192 | 0
3218 | BIRDHILL1_20 | BIRDHILL1_10 | T21_3_MVA | 21.4 | 10.7 | 0 | 193 | 0
3219 | BIRDHILL2_20 | BIRDHILL2_10 | T24_3_MVA | 21.4 | 10.7 | 0 | 194 | 0
3220 | SKIBEREEN_20 | SKIBBERE1_10 | T421_5MVA | 21.4 | 10.7 | 0 | 195 | 0
3224 | ROSBERCO4_20 | ROSBERCON_10 | T12_5MVA | 21.4 | 10.7 | 0 | 196 | 0
3231 | BUNCRANA2_20 | BUNCRANA_10 | T22_5_MVA | 21.4 | 10.7 | 0 | 197 | 0
3232 | MLFRD_NR1_10 | MILFRD_20 | T22_5_MVA_MIL | 10.7 | 21.4 | 0 | 198 | 0
3233 | RATHMORE1_20 | RATHMORE9_10 | T12_3_MVA | 21.4 | 10.7 | 0 | 199 | 0
3234 | CLOYNE1_20 | CLOYNE1_10 | T21_3_MVA | 21.4 | 10.7 | 0 | 200 | 0
3235 | CASTLEISLAND_20 | CASTLEISLAND1_10 | T421_5_MVA | 21.4 | 10.7 | 0 | 201 | 0
3236 | CASTLEISLAND_20 | CASTLEISLAND_10 | T422_5_MVA | 21.4 | 10.7 | 0 | 202 | 0
3237 | BALLYCR1_20 | BALLYCR1_10 | T21_3_MVA | 21.4 | 10.7 | 0 | 203 | 0
3238 | KILMAGIG1_20 | KILMAGIG1_10 | T21_5_MVA | 21.4 | 10.7 | 0 | 204 | 0
3243 | BEALISTO2_10 | BEALISTO1_20 | T21_3_MVA | 21.4 | 10.7 | 0 | 205 | 0
3246 | GLENGARRI_20 | GLENGAR1_10 | T21_3_MVA | 21.4 | 10.7 | 0 | 206 | 0
3247 | ATHGARVAN_20 | ATHGARVAN_10 | T21_5MVA | 21.4 | 10.7 | 0 | 207 | 0
3248 | EDENDERRY | EDENDERY1_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 208 | 64
3249 | EDENDERRY | EDENDERY2_20 | T421_10_MVA EDENDERRY | 41.6 | 21.4 | 0 | 209 | 0
3250 | ABBEYFEAL_20 | ABBEYFEA2_10 | T21_5_MVA | 21.4 | 10.7 | 0 | 210 | 0
3251 | CARRIGS1_20 | CARRIGSHA_10 | T21_5_MVA | 21.4 | 10.7 | 0 | 211 | 0
3256 | BUNCRANA | BUNCRANA1_20 | T421_5_MVA_BUN | 41.6 | 21.4 | 0 | 212 | 0
3257 | BUNCRANA | BUNCRANA2_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 213 | 64
3258 | NEWTOWNCU_20 | NEWTOWNCU_10 | T412_3_MVA | 21.4 | 10.7 | 0 | 214 | 0
3259 | CTWNBERE1_20 | CTWNBERE1_10 | T21_3_MVA | 21.4 | 10.7 | 0 | 215 | 0
3260 | CREAGH_T421 | CREAGH1_10 | T21_5_MVA | 21.4 | 10.7 | 0 | 216 | 0
3265 | LAWLESSTOWN1_20 | LAWLESSTOWN_10 | T21_3_MVA | 21.4 | 10.7 | 0 | 217 | 0
3266 | LAWLESSTOWN1_20 | SEAGATE_10 | T23_3_MVA | 21.4 | 10.7 | 0 | 218 | 0
3267 | LAWLESSTOWN1_20 | SEAGATE_10 | T22_3_MVA | 21.4 | 10.7 | 0 | 219 | 0
3270 | FINNEA_20 | FINNEA_10 | T21_3_MVA | 21.4 | 10.7 | 0 | 220 | 0
3271 | CAVAN_20 | CAVAN_10 | T21_5_MVA | 21.4 | 10.7 | 0 | 221 | 0
3272 | SPA ROAD | SPA RD1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 222 | 0
3273 | SPA ROAD | SPA RD2_10 | T42_5_MVA SPA ROAD | 41.6 | 10.7 | 1 | 223 | 64
3286 | BANGOR ERRIS | BANGOR E1_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 224 | 64
3287 | GLENGOOLE | GLENGOOL1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 225 | 64
3288 | GLENGOOLE | GLENGOOL2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 226 | 0
3291 | SLANE | SLANE2_20 | T422_10_MVA_SLANE | 41.6 | 21.4 | 1 | 227 | 64
3292 | SLANE_T421 | SLANE_20 | T421_10_MVA_SLANE | 41.6 | 21.4 | 1 | 228 | 64
3294 | COOLCORCORAN | COOLCOR1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 229 | 0
3295 | COOLCORCORAN | COOLCOR2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 230 | 64
3298 | Carrickmacross | CARRICK1_10 | T41_10_MVA_CARICKMACROS | 41.6 | 10.7 | 0 | 231 | 0
3299 | Carrickmacross | CARRICK2_10 | T42_10_MVA_CARICKMACROS | 41.6 | 10.7 | 1 | 232 | 64
3302 | SCARTEEN | SCARTEEN2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 233 | 0
3303 | SCARTEEN | SCARTEEN3_10 | T42_5_MVA SCARTEEN | 41.6 | 10.7 | 1 | 234 | 64
3312 | MALAHIDE | MALAHIDE1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 235 | 0
3313 | MALAHIDE | MALAHIDE2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 236 | 64
3314 | MALAHIDE | MALAHIDE3_10 | CUST1_3_2_MV MALAHIDE | 41.6 | 1.5 | 0 | 237 | 0
3315 | MALAHIDE | MALAHIDE4_10 | CUST2_3_2_MV | 41.6 | 1.5 | 0 | 238 | 0
3317 | Kilross Road | KILROSS2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 239 | 64
3318 | Kilross Road_T421 | KILROSS1_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 240 | 64
3319 | DRUMQUIN | DRUMQUIN_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 241 | 64
3326 | Gartnaneane | Gartnaneane_20 | T421_12MVA_GARTN | 41.6 | 21.4 | 0 | 242 | 0
3334 | GLENTIES | GLENTIES1_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 243 | 64
3335 | GLENTIES | GLENTIES2_10 | T42_2_MVA | 41.6 | 10.7 | 0 | 244 | 0
3336 | NEWMARKET (DR) | NEWMARKET_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 245 | 64
3338 | Redmondstown | REDMONDS_10-1 | T41_Customer_10_MVA | 41.6 | 10.7 | 0 | 246 | 0
3339 | Redmondstown | REDMONDS_10 | T42_Customer_10_MVA | 41.6 | 10.7 | 0 | 247 | 0
3340 | BOGHALL RD | BOGHRD1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 248 | 0
3341 | BOGHALL RD | BOGHRD2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 249 | 64
3342 | CROSSMOLINA | CROSSMOL1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 250 | 64
3343 | CROSSMOLINA | CROSSMOL2_10 | T41_2_MVA | 41.6 | 10.7 | 0 | 251 | 0
3344 | RATHMORE | RATHMORE1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 252 | 64
3345 | RATHMORE_T421 | RATHMORE1_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 253 | 64
3346 | RATHMORE | RATHMORE_38B | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 254 | 0
3347 | MONKSTOWN | MONKSTOWN1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 255 | 0
3348 | MONKSTOWN | MONKSTOWN2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 256 | 64
3349 | LITTLE BRAY | LITTLE BR_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 257 | 0
3350 | LITTLE BRAY | LITTLE BR_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 258 | 64
3351 | LOUGHDERYDUF | LOUGHD_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 259 | 0
3352 | KINSALE | KINSALE1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 260 | 0
3353 | KINSALE | KINSALE2_10 | T42_5_MVA KINSALE | 41.6 | 10.7 | 1 | 261 | 64
3354 | Granagh | GRANNAGH1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 262 | 0
3355 | Granagh | GRANNAGH2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 263 | 64
3356 | KNOCKROUR | KNOCKROUR_20 | T142_40_MVA | 41.6 | 21.4 | 0 | 264 | 0
3357 | AGHAWAY | AGHAWAY_20 | T421_24_MVA | 41.6 | 21.4 | 0 | 265 | 0
3358 | SCARIFF | SCARIFF_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 266 | 64
3359 | Garville Avenue | Garville Avenue_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 267 | 64
3360 | CLOYNE | CLOYNE1_10 | T42_2_MVA | 41.6 | 10.7 | 1 | 268 | 0
3361 | CLOYNE | CLOYNE2_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 269 | 16
3367 | CASTLEISLAND | CASTLEISLAND1_10 | T42_5_MVA | 41.6 | 10.7 | 2 | 270 | 20
3368 | CASTLEISLAND | CASTLEISLAND_10 | T41_5_MVA CASTLEISLAND | 41.6 | 10.7 | 0 | 271 | 0
3369 | COOLCARRON | COOLCARR1_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 272 | 64
3370 | COOLCARRON | COOLCARR2_10 | T42_2_MVA | 41.6 | 10.7 | 0 | 273 | 0
3372 | BEAL NA Blath | BEAL N BL_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 274 | 64
3373 | MILFORD-MWR | MILFORD1_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 275 | 64
3374 | MILFORD-MWR_T422 | MILFORD_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 276 | 64
3375 | DUNLEER | DUNLEER2_10 | T41_5_MVA_DUNLEER | 41.6 | 10.7 | 0 | 277 | 0
3376 | DUNLEER | DUNLEER1_10 | T42_5_MVA_DUNLEER | 41.6 | 10.7 | 1 | 278 | 64
3377 | BALLINROBE | BALLINRB1_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 279 | 0
3378 | BALLINROBE | BALLINRB2_20 | T422_10_MVA BALLINROBE | 41.6 | 21.4 | 1 | 280 | 64
3379 | OAKFIELD | OAKFIELD1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 281 | 0
3380 | OAKFIELD | OAKFIELD2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 282 | 64
3381 | SOUTH KING S | SOUTHKIN1_10 | T42_10_MVA SOUTH KING S | 41.6 | 10.7 | 1 | 283 | 64
3382 | SOUTH KING S | SOUTHKIN2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 284 | 0
3383 | POLLERTON | POLLERTO1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 285 | 0
3384 | POLLERTON | POLLERTO2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 286 | 64
3385 | INCH | INCH1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 287 | 0
3386 | INCH | INCH2_20 | T422_5_MVA INCH | 41.6 | 21.4 | 1 | 288 | 64
3387 | INCH | INCH_38B | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 289 | 0
3388 | MILLTOWN-SR | MILTWNSR1_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 290 | 0
3389 | MILLTOWN-SR | MILTWNSR2_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 291 | 64
3393 | UNIDARE | UNIDARE1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 292 | 0
3394 | UNIDARE | UNIDARE2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 293 | 64
3395 | CLONES | CLONES1_10 | T42_5_MVA CLONES | 41.6 | 10.7 | 1 | 294 | 64
3396 | CLONES | CLONES2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 295 | 0
3397 | GORESBRIDGE | GORESBDG1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 296 | 0
3398 | GORESBRIDGE | GORESBDG2_10 | T42_5_MVA GORESBRIDGE | 41.6 | 10.7 | 2 | 297 | 20
3399 | KILCOCK | KILCOCK1_20 | T421_10_MVA_KILCOCK | 41.6 | 21.4 | 0 | 298 | 0
3400 | KILCOCK | KILCOCK2_20 | T422_10_MVA_KILCOCK | 41.6 | 21.4 | 1 | 299 | 64
3401 | KILCLOHER | KILCLOHE1_10 | T41_2_MVA | 41.6 | 10.7 | 0 | 300 | 0
3402 | KILCLOHER | KILCLOHE2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 301 | 64
3403 | BUTTEVANT | BUTTVANT1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 302 | 0
3404 | BUTTEVANT | BUTTVANT2_10 | T42_5_MVA BUTTEVANT | 41.6 | 10.7 | 1 | 303 | 64
3405 | Ballycrossaun | BALLYCR1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 304 | 0
3406 | Ballycrossaun | BALLYCR2_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 305 | 64
3407 | CLAREGALWAY | CLAREGA2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 306 | 64
3408 | CLAREGALWAY_T421 | CLAREGA1_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 307 | 64
3409 | CLIFDEN | CLIFDEN1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 308 | 0
3410 | CLIFDEN | CLIFDEN2_10 | T42_5_MVA CLIFDEN | 41.6 | 10.7 | 1 | 309 | 64
3411 | TUAM NORTH | TUAM NORTH1_10 | T42_5_MVA TUAM NORTH | 41.6 | 10.7 | 2 | 310 | 20
3412 | TUAM NORTH | TUAM NORTH2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 311 | 0
3413 | BISHOPSTOWN | BISHOPS1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 312 | 0
3414 | BISHOPSTOWN | BISHOPS2_10 | T42_10_MVA BISHOPSTOWN | 41.6 | 10.7 | 2 | 313 | 20
3415 | KILLYBEGS | KILLYBEG2_20 | T421_15_MVA | 41.6 | 21.4 | 0 | 314 | 0
3416 | KILLYBEGS | KILLYBEGS_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 315 | 64
3417 | CASTLEREA | CASTLERE1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 316 | 0
3418 | CASTLEREA | CASTLERE2_10 | T42_5_MVA CASTLEREA | 41.6 | 10.7 | 1 | 317 | 64
3419 | CASTLERE_38B | CASTLEREA | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 318 | 0
3420 | CREESLOUGH | CREESLOUG_20 | T421_5MVA | 41.6 | 21.4 | 1 | 319 | 64
3421 | CRUMLIN | CRUMLIN2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 320 | 0
3422 | CRUMLIN | CRUMLIN1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 321 | 64
3425 | NEWPORT | NEWPORT_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 322 | 64
3426 | KEELDRUM_38 | KEELDRUM_20 | T421_20MVA | 41.6 | 21.4 | 0 | 323 | 0
3427 | Headford Road | HEADFORD1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 324 | 0
3428 | Headford Road | HEADFORD2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 325 | 64
3429 | Termonfeckin Road | TERMONFE1_10 | T42_5_MVA_TERMNF | 41.6 | 10.7 | 1 | 326 | 64
3430 | Termonfeckin Road | TERMONFE2_10 | T41_5_MVA_TERMF | 41.6 | 10.7 | 0 | 327 | 0
3431 | JENKINSTOWN | JENKINST1_20 | T421_5_MVA_JENKINST | 41.6 | 21.4 | 0 | 328 | 0
3432 | JENKINSTOWN | JENKINST2_20 | T422_5_MVA_JENKINST | 41.6 | 21.4 | 1 | 329 | 64
3433 | KILLESHANDRA | KILLESHA1_10 | T41_5_MVA Killeshandra | 41.6 | 10.7 | 0 | 330 | 0
3434 | KILLESHANDRA | KILLESHA2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 331 | 64
3435 | CARNDONAGH | CARNDONA1_20 | T421_5_MVA_CARN | 41.6 | 21.4 | 0 | 332 | 0
3436 | CARNDONAGH | CARNDONA2_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 333 | 64
3437 | COLLINSTOWN | COLLINS1_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 334 | 0
3438 | COLLINSTOWN | COLLINS2_10 | T42_5_MVA COLLINSTOWN | 41.6 | 10.7 | 1 | 335 | 20
3442 | SALLINS | SALLINS1_10 | T41_10_MVA_SALLINS | 41.6 | 10.7 | 0 | 336 | 0
3443 | SALLINS | SALLINS2_10 | T42_10_MVA_SALLINS | 41.6 | 10.7 | 1 | 337 | 64
3444 | BALLYBAILIE | BALLYBAI1_10 | T42_2_MVA_BALLYBAILIE | 41.6 | 10.7 | 0 | 338 | 0
3445 | BALLYBAILIE | BALLYBAI2_10 | T41_5_MVA-BALLYBAILIE | 41.6 | 10.7 | 1 | 339 | 64
3448 | ABBEYLANDS | ABBEYLAN1_10 | T41_10_MVA_ABBEYLANDS | 41.6 | 10.7 | 0 | 340 | 0
3449 | ABBEYLANDS | ABBEYLAN2_10 | T42_10_MVA_ABBEYLANDS | 41.6 | 10.7 | 1 | 341 | 64
3451 | MT CRONALAGH | MTCRN_G1_CM1 | T1_5MVA | 41.6 | 21.4 | 0 | 342 | 0
3452 | CRATLOE | CRATLOE1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 343 | 0
3453 | CRATLOE | CRATLOE2_20 | T422_5_MVA CRATLOE | 41.6 | 21.4 | 1 | 344 | 64
3454 | TULLINLOUGH | TULNLOUGH_20 | T421_22MVA | 41.6 | 21.4 | 0 | 345 | 0
3455 | KILKEE | KILKEE_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 346 | 64
3456 | WOODFORD | WOODFORD1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 347 | 0
3457 | WOODFORD | WOODFORD2_10 | T42_10_MVA WOODFORD | 41.6 | 10.7 | 1 | 348 | 64
3458 | COOLOCK | COOLOCK1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 349 | 0
3459 | COOLOCK | COOLOCK2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 350 | 64
3460 | BALLYARD | BALLYARD1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 351 | 0
3461 | BALLYARD | BALLYARD2_10 | T42_5_MVA BALLYARD | 41.6 | 10.7 | 2 | 352 | 20
3464 | DOUGLAS | DOUGLAS1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 353 | 0
3465 | DOUGLAS | DOUGLAS2_10 | T42_10_MVA DOUGLAS | 41.6 | 10.7 | 1 | 354 | 64
3466 | CLONTARF | CLONTARF_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 355 | 64
3467 | Dun Laoghaire | DUN LAOG1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 356 | 0
3468 | Dun Laoghaire | DUN LAOG2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 357 | 64
3472 | TYCOR | TYCOR1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 358 | 0
3473 | TYCOR | TYCOR2_10 | T42_5_MVA | 41.6 | 10.7 | 2 | 359 | 20
3474 | RAMSTOWN | RAMSTOWN1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 360 | 0
3475 | RAMSTOWN | RAMSTOWN2_10 | T42_5_MVA | 41.6 | 10.7 | 0 | 361 | 0
3476 | SANDYFORD | SANDYFOR1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 362 | 0
3477 | SANDYFORD | SANDYFOR2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 363 | 64
3478 | LEIXLIP | LEIXLIP1_10 | T42_10_MVA_LEIXLIP | 41.6 | 10.7 | 1 | 364 | 64
3479 | LEIXLIP | LEIXLIP2_10 | T41_10_MVA_LEIXLIP | 41.6 | 10.7 | 0 | 365 | 0
3482 | GREENHILLS | GREENHILL_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 366 | 64
3483 | Garryspillane | GARRYSPIL_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 367 | 64
3484 | TULLOW | TULLOW1_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 368 | 0
3485 | TULLOW | TULLOW2_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 369 | 64
3486 | BALTINGLASS | BALTINGL1_20 | T421_5MVA | 41.6 | 21.4 | 0 | 370 | 0
3487 | BALTINGLASS | BALTINGL2_20 | T422_5MVA BALTINGLASS | 41.6 | 21.4 | 2 | 371 | 4
3488 | FAUDEEN_38 | FAUDEEN_20 | T421_20_MVA | 41.6 | 21.4 | 0 | 372 | 0
3489 | KILMACTHOMAS | KILMACTH1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 373 | 0
3490 | KILMACTHOMAS | KILMACTH2_20 | T422_5_MVA KILMACTHOMAS | 41.6 | 21.4 | 1 | 374 | 64
3491 | MONFIN | MONFIN1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 375 | 0
3492 | MONFIN | MONFIN2_10 | T42_2_MVA | 41.6 | 10.7 | 1 | 376 | 64
3493 | KILLINICK | KILLIN1_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 377 | 64
3494 | KILLINICK | KILLIN2_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 378 | 0
3495 | KEENAHONE_38 | KEENAHONE_20 | T421_46_MVA | 41.6 | 21.4 | 0 | 379 | 0
3496 | BRAY | BRAY1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 380 | 0
3497 | BRAY | BRAY2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 381 | 64
3498 | MAYFIELD | MAYFIELD1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 382 | 0
3499 | MAYFIELD | MAYFIELD2_10 | T42_10_MVA MAYFIELD | 41.6 | 10.7 | 1 | 383 | 64
3500 | KILMAGIG | KILMAGIG1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 384 | 64
3501 | KILMAGIG | KILMAGIG2_10 | T41_2_MVA | 41.6 | 10.7 | 0 | 385 | 0
3502 | PALMERSTOWN | PALMERST1_10 | T42_10_MVA PALMERSTOWN | 41.6 | 10.7 | 1 | 386 | 64
3503 | PALMERSTOWN | PALMERST2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 387 | 0
3504 | BANAGHER | BANAGHER1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 388 | 0
3505 | BANAGHER | BANAGHER2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 389 | 64
3506 | KILLIN_HILL | KILLINH_20 | T41_15_MVA | 41.6 | 21.4 | 1 | 390 | 64
3507 | PHIBSBORO | PHIBSBORO_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 391 | 0
3508 | PHIBSBORO | PHIBSBORO_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 392 | 64
3509 | DONNYBROOK | DONNYBROOK_1 | T41_10_MVA | 41.6 | 10.7 | 0 | 393 | 0
3510 | DONNYBROOK | DONNYBROOK_2 | T42_10_MVA | 41.6 | 10.7 | 1 | 394 | 64
3511 | BELFIELD | BELFIELD_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 395 | 0
3512 | BELFIELD | BELFIELD1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 396 | 64
3513 | Dennehy's Cross | DENNHY X1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 397 | 0
3514 | Dennehy's Cross | DENNHY X2_10 | T42_15_MVA DENNEHYS X | 41.6 | 10.7 | 1 | 398 | 64
3515 | JULIANSTOWN | JULIANST1_20 | T421_5_MVA_JULIANST | 41.6 | 21.4 | 0 | 399 | 0
3516 | JULIANSTOWN | JULIANST2_20 | T422_5_MVA_JULIANSTOWN | 41.6 | 21.4 | 1 | 400 | 64
3517 | JULIANSTOWN | JULIAN_38B | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 401 | 0
3518 | SCREEB | SCREEBE1_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 402 | 64
3519 | SCREEB | SCREEBE2_10 | T42_2_MVA | 41.6 | 10.7 | 0 | 403 | 0
3521 | FOYNES | FOYNES1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 404 | 64
3522 | FOYNES | FOYNES2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 405 | 0
3523 | SANTRY | SANTRY1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 406 | 0
3524 | SANTRY | SANTRY2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 407 | 64
3525 | LITTLE MILLS | LITTLE MI_10 | T41_5_MVA_LITTLE MI | 41.6 | 10.7 | 1 | 408 | 64
3526 | Ballincollig HIll | BALINCOL_20 | T421_15MVA | 41.6 | 21.4 | 0 | 409 | 0
3527 | TOSSY | TOSSY_20 | T421_20_MVA_TOSSY | 41.6 | 21.4 | 0 | 410 | 0
3528 | KILCULLEN | KILCULLN1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 411 | 0
3529 | KILCULLEN | KILCULLN2_10 | T42_5_MVA KILCULLEN | 41.6 | 10.7 | 1 | 412 | 64
3530 | KILCULLEN_T424 | KILCULLN4_20 | T424_10_MVA | 41.6 | 21.4 | 1 | 413 | 64
3531 | BALLYGAR | BALLYGAR2_10 | T42_5_MVA | 41.6 | 10.7 | 2 | 414 | 20
3532 | BALLYGAR_38B | BALLYGAR | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 415 | 0
3533 | SHANNON | SHANNON1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 416 | 0
3534 | SHANNON | SHANNON2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 417 | 64
3535 | HOLYCROSS RD | HOLYCROS1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 418 | 0
3536 | HOLYCROSS RD | HOLYCROS2_10 | T42_5_MVA HOLYCROSS RD | 41.6 | 10.7 | 2 | 419 | 4
3537 | HOLYCROSS RD | DEW_VALEY_10 | T43_10_MVA | 41.6 | 10.7 | 0 | 420 | 0
3538 | HOLYCROSS RD | DEW_VALEY_10 | T44_10_MVA | 41.6 | 10.7 | 0 | 421 | 0
3539 | BALLYRAGGET | BALLYRAGG_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 422 | 0
3540 | TRAMORE | TRAMORE1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 423 | 0
3541 | TRAMORE | TRAMORE2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 424 | 64
3542 | DODDER Road | DODDER RD_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 425 | 64
3543 | BELGARD | BELGARD1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 426 | 0
3544 | BELGARD | BELGARD2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 427 | 64
3545 | KILMARTIN | KILMARTIN_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 428 | 64
3546 | SUTTON | SUTTON1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 429 | 64
3547 | SUTTON | SUTTON1_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 430 | 0
3548 | HOWTH JUNCTI | HOWTH JUN_1 | T41_10_MVA | 41.6 | 10.7 | 0 | 431 | 0
3549 | HOWTH JUNCTI | HOWTH JUN_2 | T42_10_MVA | 41.6 | 10.7 | 1 | 432 | 64
3550 | ASHBOURNE | ASHBOURN1_20 | T421_15_MVA | 41.6 | 21.4 | 0 | 433 | 0
3551 | ASHBOURNE | ASHBOURN2_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 434 | 64
3552 | TOGHER | TOGHER1_10 | T42_10_MVA TOGHER | 41.6 | 10.7 | 1 | 435 | 64
3553 | TOGHER | TOGHER2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 436 | 0
3554 | GREYGROVE | GREYGROVE_33 | T431_40_MVA | 41.6 | 33 | 0 | 437 | 0
3555 | DEERPARK | DEERPARK1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 438 | 0
3556 | DEERPARK | DEERPARK2_10 | T42_5_MVA DEERPARK | 41.6 | 10.7 | 2 | 439 | 20
3557 | DUNGLOE | DUNGLOE1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 440 | 64
3558 | DUNGLOE | DUNGLOE2_10 | T41_2_MVA | 41.6 | 10.7 | 0 | 441 | 0
3559 | DUNGLOE_38B | DUNGLOE_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 442 | 0
3560 | BALLINCOLLIG | BALLINCO1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 443 | 0
3562 | BALLINCOLLIG | BALLINCO2_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 444 | 0
3563 | BALLINCOLLIG | BALLINCO2_20 | T422_10_MVA | 41.6 | 21.4 | 0 | 445 | 0
3564 | Leeson Street | LEESONST1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 446 | 64
3565 | Leeson Street | LEESONST2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 447 | 0
3566 | DRUMCONDRA | DRUMCONDR_1 | T41_10_MVA | 41.6 | 10.7 | 0 | 448 | 0
3567 | DRUMCONDRA | DRUMCONDRA_2 | T42_10_MVA | 41.6 | 10.7 | 1 | 449 | 64
3568 | Manorhamilton | MANORHAM_20 | T422_5_MVA | 41.6 | 21.4 | 2 | 450 | 64
3569 | Manorhamilton | MANORHAM_20 | T424_15_MVA | 41.6 | 21.4 | 2 | 451 | 64
3570 | MANOR ST | MANOR ST1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 452 | 0
3571 | MANOR ST | MANOR ST2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 453 | 64
3572 | WATERFORD IN | WATERFIN1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 454 | 0
3573 | WATERFORD IN | WATERFIN2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 455 | 64
3574 | WATERFORD IN | WATERFIN3_10 | T44_10_MVA | 41.6 | 10.7 | 0 | 456 | 0
3575 | KILTIMAGH | KILTIMAGH_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 457 | 64
3576 | ARDGEEHA | ARDGEEH1_10 | T41_10MVA | 41.6 | 10.7 | 0 | 458 | 0
3577 | ARDGEEHA | ARDGEEH2_10 | T42_10MVA | 41.6 | 10.7 | 1 | 459 | 64
3578 | BUNDORAN | BUNDORAN1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 460 | 64
3579 | BUNDORAN | BUNDORAN2_10 | T41_5_MVA_BUND | 41.6 | 10.7 | 0 | 461 | 0
3581 | Rosscarberry | ROSCARB1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 462 | 0
3582 | Rosscarberry | ROSCARB2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 463 | 64
3583 | Rosscarberry | ROSCARBE_38B | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 464 | 0
3584 | KNOCKNAGO_38 | KNOCKNAGO_20 | T421_50MVA | 41.6 | 21.4 | 0 | 465 | 0
3585 | TUBBERCURRY | TUBBERCU1_10 | T41_2_MVA | 41.6 | 10.7 | 0 | 466 | 0
3586 | TUBBERCURRY | TUBBERCU2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 467 | 64
3587 | ROCHES ST | ROCHES_ST_1 | T41_10_MVA | 41.6 | 10.7 | 0 | 468 | 0
3588 | ROCHES ST | ROCHES_ST_2 | T42_10_MVA | 41.6 | 10.7 | 1 | 469 | 64
3589 | MARSHES | MARSHES1_10 | T41_10_MVA_MARSHES | 41.6 | 10.7 | 0 | 470 | 0
3590 | MARSHES | MARSHES2_10 | T42_10_MVA_MARSHES | 41.6 | 10.7 | 1 | 471 | 64
3591 | MARSHES | MARSHES_20 | T423_10MVA_MARSHES | 41.6 | 21.4 | 1 | 472 | 64
3592 | LUCAN EAST | LUCAN EA1_10 | T42_5_MVA LUCAN EAST | 41.6 | 10.7 | 1 | 473 | 64
3593 | LUCAN EAST | LUCAN EA2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 474 | 0
3596 | SEMPERIT | SEMPERIT1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 475 | 0
3597 | SEMPERIT | SEMPERIT2_10 | T42_10_MVA | 41.6 | 10.7 | 0 | 476 | 0
3598 | SEMPERIT | SEMPERIT3_10 | T43_10_MVA | 41.6 | 10.7 | 1 | 477 | 64
3599 | Watling Street | WATLING S_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 478 | 64
3600 | Watling Street | WATLING 2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 479 | 0
3601 | TINAHASK | TINAHASK1_10 | T42_5_MVA TINAHASK | 41.6 | 10.7 | 1 | 480 | 64
3602 | TINAHASK | TINAHASK2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 481 | 0
3603 | BALLYBUNION | BALLYBUN1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 482 | 0
3604 | BALLYBUNION | BALLYBUN2_20 | T422_5_MVA BALLYBUNION | 41.6 | 21.4 | 1 | 483 | 64
3605 | BALLYBUNION | BALLYBUN3_20 | T424_10_MVA | 41.6 | 21.4 | 1 | 484 | 64
3606 | OLD BAWN | OLD BAWN_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 485 | 0
3607 | OLD BAWN | OLD_BAWN_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 486 | 64
3608 | Coe's Road | COES RD_10 | T42_5_MVA_COES | 41.6 | 10.7 | 1 | 487 | 64
3609 | Coe's Road | COES RD_10 | T41_5_MVA_COES | 41.6 | 10.7 | 1 | 488 | 0
3610 | BALLYHAUNIS | BALLYHAU1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 489 | 0
3611 | BALLYHAUNIS | BALLYHAU2_10 | T42_5_MVA | 41.6 | 10.7 | 2 | 490 | 20
3612 | CLOONLOUGH | CLOONLOU1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 491 | 0
3613 | CLOONLOUGH | CLOONLOU2_10 | T42_5_MVA CLOONLOUGH | 41.6 | 10.7 | 1 | 492 | 64
3614 | GARRANACANTY | GARRANA1_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 493 | 0
3615 | GARRANACANTY | GARRANA2_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 494 | 64
3616 | FACTORY CROSS | FACTORTX1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 495 | 0
3617 | FACTORY CROSS | FACTORTX2_10 | T42_10_MVA FACTORY CROS | 41.6 | 10.7 | 1 | 496 | 64
3618 | LISMORE | LISMORE1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 497 | 0
3619 | LISMORE | LISMORE2_10 | T42_5_MVA LISMORE | 41.6 | 10.7 | 1 | 498 | 64
3620 | BEALISTOWN | BEALISTO2_10 | T422_5_MVA | 41.6 | 21.4 | 1 | 499 | 64
3621 | BEALISTOWN | BEALIST02_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 500 | 0
3622 | GURRANEBANE | GURRANEB1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 501 | 0
3623 | GURRANEBANE | GURRANEB2_20 | T422_5_MVA GURRANEBANE | 41.6 | 21.4 | 1 | 502 | 64
3624 | RAHEN_BAR_38 | RAHEN_BAR | T2_20MVA | 41.6 | 21.4 | 0 | 503 | 0
3625 | GNEEVES WF | GNEEVES_WF | T41_10_MVA | 41.6 | 21.4 | 0 | 504 | 0
3626 | NORTHWALL_38 | NORTHWALL_G3_NW3 | T43_20MVA | 41.6 | 10.7 | 0 | 505 | 0
3627 | NORTHWALL_38 | NORTHWALL_G2_NW2 | T42_20MVA | 41.6 | 10.7 | 0 | 506 | 0
3628 | NORTHWALL_38 | NORTHWALL_G1_NW1 | T41_20MVA | 41.6 | 10.7 | 0 | 507 | 0
3629 | CAHIR_38 | CAHIR_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 508 | 0
3630 | CAHIR_38 | CAHIR1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 509 | 64
3634 | Carrickmines_38 | CARIKMINS_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 510 | 0
3635 | Carrickmines_38 | CARIKMINS_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 511 | 64
3636 | CLOON_38 | CLOON_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 512 | 64
3637 | CLOON_T421 | CLOON_20 | T421_10_MVA | 41.6 | 21.4 | 1 | 513 | 64
3639 | DALTON_38 | DALTON_20 | T421_10_MVA | 41.6 | 21.4 | 1 | 514 | 0
3640 | DALTON_38 | DALTON_20 | T422_10_MVA DALTON_38 | 41.6 | 21.4 | 1 | 515 | 64
3641 | CARICKONS_38 | CARICKON2_10 | T42_5_MVA CARICKON2_10 | 41.6 | 10.7 | 1 | 516 | 64
3642 | CARICKONS_38 | CARICKON1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 517 | 0
3643 | CHARLEVILLE_38 | CHARLEVL_20 | T421_10_MVA | 41.6 | 21.4 | 1 | 518 | 64
3644 | CHARLEVILLE_38 | CHARLEVL2_20 | T422_15_MVA | 41.6 | 21.4 | 0 | 519 | 0
3646 | DUNDALK1_38 | DUNDALK1_10 | T41_10_MVA_DUNDALK | 41.6 | 10.7 | 0 | 520 | 0
3647 | DUNDALK2_38 | DUNDALK2_10 | T42_10_MVA_DUNDALK | 41.6 | 10.7 | 1 | 521 | 64
3648 | DRUMLINE_38 | DRUMLI2_20 | T422_5_MVA DRUMLINE_38 | 41.6 | 21.4 | 1 | 522 | 64
3649 | DRUMLINE_38 | DRUMLI1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 523 | 0
3651 | DUNMANWAY_38 | DUNMANWAY_10_ | T43_10MVA | 41.6 | 10.7 | 1 | 524 | 64
3652 | DUNMANWAY_T422 | DUNMANWAY_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 525 | 64
3653 | DRYBRIDGE_38 | DRYBRIDG2_10 | T41_15_MVA_DRYBRIDGE | 41.6 | 10.7 | 0 | 526 | 0
3654 | DRYBRIDGE_38 | DRYBRIDG1_10 | T42_15_MVA_DRYBRIDGE | 41.6 | 10.7 | 1 | 527 | 64
3657 | BLAKE_38 | BLAKE2_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 528 | 0
3658 | BLAKE_38 | BLAKE1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 529 | 20
3659 | BALLYLICKEY | BALLYLIKY_20 | T421_10_MVA | 41.6 | 21.4 | 1 | 530 | 64
3660 | GRANGE_38 | GRANGE2D_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 531 | 0
3661 | GRANGE_38 | GRANGE1D_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 532 | 64
3663 | INCHCR_T141 | INCHICORE_10 | T43_10_MVA | 41.6 | 10.7 | 1 | 533 | 64
3664 | INCHICORE_T143 | INCHCORE3_10 | T45_10_MVA | 41.6 | 10.7 | 0 | 534 | 0
3665 | INCHICORE_T41 | INCHCORE4_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 535 | 64
3666 | Kilbarry_T43 | KILBARRY2_10 | T43_15_MVA | 41.6 | 10.7 | 1 | 536 | 64
3668 | LISDRUM_38 | LISDRUM_20 | T422_5_MVA_LISDRUM | 41.6 | 21.4 | 1 | 537 | 64
3669 | MACROOM_38 | MACROOM_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 538 | 64
3670 | GLASMORE_38 | GLASMORE_20 | T421_10MVA_GLASMORE | 41.6 | 21.4 | 0 | 539 | 0
3671 | GLASMORE_38 | GLASMORE1_20 | T422_10MVA_GLASMORE | 41.6 | 21.4 | 1 | 540 | 64
3672 | MALLOW_38 | MALLOW1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 541 | 0
3673 | MALLOW_38 | MALLOW_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 542 | 64
3674 | MOY_38 | MOY1_20 | T421_10MVA MOY_38 | 41.6 | 21.4 | 0 | 543 | 0
3675 | MOY_38 | MOY2_20 | T422_10MVA | 41.6 | 21.4 | 1 | 544 | 64
3676 | PORTLAOIS_38 | PORTLAOI2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 545 | 64
3677 | PORTLAOIS_38 | PORTLAOI1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 546 | 0
3678 | PORTLAOIS_38 | PORTLAOI2_20 | T423_10_MVA | 41.6 | 21.4 | 0 | 547 | 0
3679 | PORTLAOIS_38 | PORTLAOI3_20 | T424_10_MVA | 41.6 | 21.4 | 1 | 548 | 64
3682 | RINGASKIDDY | RINGAS1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 549 | 64
3685 | WATERFORD_38 | WATERFOR1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 550 | 0
3686 | WATERFORD_38 | WATERFOR2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 551 | 64
3688 | BOOLTGH_38_2 | BOOLTIAGH_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 552 | 64
3689 | INISCARA_38 | INISCARA_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 553 | 0
3690 | ATHLONE_38 | ATHLONE2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 554 | 0
3691 | ATHLONE_38 | ATHLONE1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 555 | 64
3692 | BANDON_38 | BANDON_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 556 | 64
3695 | DALLOW_38 | MEENWAUN_WF | T421_10_MVA | 41.6 | 21.4 | 1 | 557 | 64
3696 | NENAGH_38 | NENAGH1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 558 | 64
3697 | NENAGH_38 | NENAGH2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 559 | 0
3698 | NENAGH_T422 | NENAGH1_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 560 | 64
3699 | BALLYDOOR_38 | BALLYDOOR_20 | CUST_18MVA | 41.6 | 21.4 | 0 | 561 | 0
3700 | CARROWBEG | CARROWB_10_1 | T41_10_MVA | 41.6 | 10.7 | 0 | 562 | 0
3701 | CARROWBEG | CARROWB_10_2 | T42_10_MVA CARROWBEG | 41.6 | 10.7 | 1 | 563 | 64
3702 | CARROWBEG_T423 | CARROWB_20 | T421_10_MVA | 41.6 | 21.4 | 1 | 564 | 64
3703 | Graiguenamanagh | GRAIGUEN1_10 | T41_2_MVA | 41.6 | 10.7 | 0 | 565 | 0
3704 | Graiguenamanagh | GRAIGUEN2_10 | T42_2_MVA GRAIGUENAMAN | 41.6 | 10.7 | 1 | 566 | 64
3705 | BALLINDERRY | BALINDER1_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 567 | 64
3706 | BALLINDERRY_T422 | BALINDER1_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 568 | 64
3707 | GLENGARRIFF | GLENGARRI_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 569 | 64
3708 | TRILLICK_38B | TRILLICK_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 570 | 0
3709 | REAMORE_38 | REAMO_HOT_LV | HOT_100_KVA | 41.6 | 0.41 | 0 | 571 | 0
3710 | MANGANS_38 | MANGANS_20 | T421_20MVA | 41.6 | 21.4 | 1 | 572 | 64
3711 | TOOMEVARA | TOOMEVARA_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 573 | 64
3712 | LACKA | LACKA1_20 | T422_10_MVA | 41.6 | 21.4 | 0 | 574 | 0
3713 | LACKA | LACKA2_20 | T421_10_MVA LACKA_38 | 41.6 | 21.4 | 0 | 575 | 0
3714 | MOANMORE | MOANMORE_20 | T421_15_MVA | 41.6 | 21.4 | 0 | 576 | 0
3716 | ARDFINNAN | ARDFINNAN_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 577 | 64
3717 | ARDFINNAN_T421 | ARDFINNAN_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 578 | 64
3718 | MOUNTMELLICK | MOUNTMEL1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 579 | 64
3719 | MOUNTMELLICK | MOUNTMEL2_10 | T41_5_MVA MOUNTMELLICK | 41.6 | 10.7 | 0 | 580 | 0
3720 | MOUNTMEL_38B | MOUNTMELLICK | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 581 | 0
3721 | COOMATAGG_38 | COOMA_HOT_LV | HOT_100_KVA | 41.6 | 0.4 | 0 | 582 | 0
3722 | MOUNTRATH | MOUNTRAT1_10 | T41_5_MVA MOUNTRATH | 41.6 | 10.7 | 0 | 583 | 0
3723 | MOUNTRATH | MOUNTRAT2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 584 | 64
3740 | BAGENALSTOWN | BAGENLST1_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 585 | 0
3741 | BAGENALSTOWN | BAGENSLT2_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 586 | 64
3742 | GORT | GORT1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 587 | 0
3743 | GORT | GORT2_10 | T42_5_MVA GORT | 41.6 | 10.7 | 1 | 588 | 64
3744 | MCDONAGH_38 | MCDONAGH2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 589 | 0
3745 | MCDONAGH_38 | MCDONAGH1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 590 | 64
3746 | RATHDOWNEY | RATHDOWNE_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 591 | 64
3747 | DUNMOYLAN_38 | DUNMOYLAN_20 | T421_5.55MVA | 41.6 | 21.4 | 0 | 592 | 0
3748 | Keelnagore_38 | KEELNGORE_20 | T41_10MVA | 41.6 | 21.4 | 0 | 593 | 0
3749 | ATHGARVAN | ATHGARVAN_10 | T44_15_MVA | 41.6 | 10.7 | 1 | 594 | 64
3750 | ATHGARVAN | ATHGARVN2_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 595 | 0
3751 | BALLINCLEA | BALLINCLE_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 596 | 64
3752 | BALLYKETT | BALLYKETT_20 | T421_15_MVA | 41.6 | 21.4 | 0 | 597 | 0
3753 | DERRYBEG | DERRYBEG1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 598 | 64
3754 | DERRYBEG | DERRYBEG2_10 | T41_5_MVA_DER | 41.6 | 10.7 | 0 | 599 | 0
3755 | MONEENAGEISHA | MNAGEISH1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 600 | 0
3756 | MONEENAGEISHA | MNAGEISH2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 601 | 64
3764 | PILBRUM_38 | PILBRUM_20 | T421_50_MVA | 41.6 | 21.4 | 0 | 602 | 0
3765 | RAHEEN | RAHEEN1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 603 | 64
3766 | RAHEEN | RAHEEN2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 604 | 0
3767 | MOYLISH | MOYLISH_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 605 | 0
3768 | MOYLISH | MOYLISH2_10 | T42_5_MVA MOYLISH | 41.6 | 10.7 | 1 | 606 | 64
3769 | DOWNS_38 | DOWNS_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 607 | 0
3770 | MOVILLE | MOVILLE_20b | T421_5_MVA_MOV | 41.6 | 21.4 | 0 | 608 | 0
3771 | MOVILLE | MOVILLE_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 609 | 64
3772 | COOLMINE | COOLMINE1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 610 | 64
3773 | COOLMINE | COOLMINE2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 611 | 0
3774 | BALLINVALLY | BALINVALY_20 | T421_45MVA | 41.6 | 21.4 | 1 | 612 | 64
3775 | TUAM SOUTH | TUAM SO_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 613 | 64
3777 | ELLAGHMORE | ELLAGHMOR_20 | T421_34MVA | 41.6 | 21.4 | 0 | 614 | 0
3778 | CLONSHAUGH | CLONAHAU1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 615 | 0
3779 | CLONSHAUGH | CLONAHAU2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 616 | 64
3780 | KILMALLOCK | KILMALLO1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 617 | 0
3781 | KILMALLOCK | KILMALLO2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 618 | 64
3782 | ENNIS NORTH | ENNIS NOR2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 619 | 0
3783 | ENNIS NORTH | ENNIS NOR1_10 | T42_5_MVA ENNIS NORTH | 41.6 | 10.7 | 1 | 620 | 64
3784 | KENMARE | KENMARE1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 621 | 64
3785 | KENMARE_T421 | KENMARE_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 622 | 64
3786 | TELAYDON | TELAYDON1_10 | T42_10_MVA_TELAYDON | 41.6 | 10.7 | 1 | 623 | 64
3787 | TELAYDON_T421 | TELAYDON_20 | T421_10_MVA_TELAYDON | 41.6 | 21.4 | 1 | 624 | 64
3788 | GLEBE | GLEBE_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 625 | 0
3789 | GLEBE | GLEBE_10 | T42_10_MVA GLEBE | 41.6 | 10.7 | 1 | 626 | 64
3790 | EDGEWORT_38 | Edgeworthstown | BOOSTER | 41.6 | 41.6 | 0 | 627 | 0
3793 | KYLEERAGH | KYLEERAGH1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 628 | 0
3794 | KYLEERAGH | KYLEERAGH2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 629 | 64
3795 | RATHMULLAN | RATHMULL1_10 | T41_10_MVA_RATHMU | 41.6 | 10.7 | 0 | 630 | 0
3796 | RATHMULLAN | RATHMULL2_10 | T42_10_MVA_RATHM | 41.6 | 10.7 | 1 | 631 | 64
3797 | WHITESTOWN | WHITESTO1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 632 | 0
3798 | WHITESTOWN | WHITESTO2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 633 | 64
3799 | TYMON | TYMON1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 634 | 64
3800 | TYMON | TYMON2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 635 | 0
3801 | CHEEVERSTOWN | CHEEVERST_10 | CUST1_5_MVA | 41.6 | 10.7 | 0 | 636 | 0
3802 | DINGLE | DINGLE1_10 | T421_10_MVA | 41.6 | 21.4 | 0 | 637 | 0
3803 | DINGLE | DINGLE2_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 638 | 64
3804 | TRIMMS LANE | TRIMMS1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 639 | 0
3805 | TRIMMS LANE | TRIMMS2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 640 | 64
3806 | MULLAGH_T44 | MULLAGH1_10 | T44_5_MVA_MULLAGH | 41.6 | 10.7 | 1 | 641 | 64
3807 | MULLAGH | MULLAGH2_10 | T41_5_MVA_MULLAGH | 41.6 | 10.7 | 0 | 642 | 0
3808 | MULLAGH | MULLAGH3_10 | T42_5_MVA_MULLAGH | 41.6 | 10.7 | 1 | 643 | 64
3809 | ABBEYFEALE | ABBEYFEA1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 644 | 64
3810 | ABBEYFEALE_T421 | ABBEYFEAL_20 | T421_10_MVA | 41.6 | 21.4 | 1 | 645 | 64
3811 | Turlough Road | TURLOUG1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 646 | 64
3812 | Turlough Road | TURLOUG2_10 | T41_5_MVA TURLOUGH RD | 41.6 | 10.7 | 0 | 647 | 0
3813 | Turlough Road | TURLOUGH3_10 | T43_5_MVA | 41.6 | 10.7 | 0 | 648 | 0
3816 | BLESSINGTON | BLESSING1_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 649 | 0
3817 | BLESSINGTON | BLESSING2_20 | T422_10MVA | 41.6 | 21.4 | 2 | 650 | 8
3818 | RATHCAHIL_38 | RATHCAHIL_20 | CUST_15MVA | 41.6 | 21.4 | 0 | 651 | 0
3819 | BLANCHFIELD | BLNCHFLD1_20 | T422_31_5MVA | 41.6 | 21.4 | 1 | 652 | 64
3820 | BLANCHFIELD | BLNCHFLD2_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 653 | 64
3821 | Ballaghaderreen | BALLAGHA1_10 | T42_5_MVA BALLAGHADERE | 41.6 | 10.7 | 2 | 654 | 20
3822 | Ballaghaderreen | BALLAGHA2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 655 | 0
3823 | ROOSKEY | ROOSKEY1_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 656 | 64
3825 | BALLYMOUNT | BALLYMNT1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 657 | 64
3826 | BALLYMOUNT | BALLYMNT2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 658 | 0
3827 | ASKEATON | ASKEATON1_10 | CUST1_5_MVA | 41.6 | 10.7 | 0 | 659 | 0
3828 | ASKEATON | ASKEATON2_10 | CUST2_5_MVA ASKEATON | 41.6 | 10.7 | 0 | 660 | 0
3829 | CLADY | CLADY_10 | T42_5MVA | 41.6 | 10.7 | 1 | 661 | 64
3830 | Milltown Malbay | MILLTOWN_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 662 | 64
3831 | SWINFORD | SWINFOR1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 663 | 0
3832 | SWINFORD | SWINFOR2_10 | T42_5_MVA SWINFORD | 41.6 | 10.7 | 1 | 664 | 64
3833 | Brwnst_gen1 | Brownstown_20 | TG1_2MVA | 0.38 | 21.4 | 0 | 665 | 0
3834 | Brwnst_gen2 | Brownstown_20 | TG2_2MVA | 0.38 | 21.4 | 0 | 666 | 0
3835 | SillHill_gen | Sill Hill_20 | TG1_2MVA | 0.38 | 21.4 | 0 | 667 | 0
3836 | Dromdeeveen_38 | Dromdeeveen_20 | T42_31_5_MVA | 41.6 | 21.4 | 0 | 668 | 0
3837 | CARRANSTOWN | CARRANSTO_10 | T41_21MVA_CARRANSTOWN | 41.6 | 10.7 | 0 | 669 | 0
3838 | BALLYRAINE | BALLYRAI1_10 | T41_5_MVA_BALLYR | 41.6 | 10.7 | 0 | 670 | 0
3839 | BALLYRAINE | BALLYRAI2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 671 | 64
3840 | SPIDDAL | SPIDDAL4_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 672 | 64
3843 | OUGHTERARD | OUGHTERA2_10 | T42_5_MVA OUGHTERARD | 41.6 | 10.7 | 1 | 673 | 64
3844 | OUGHTERARD | OUGHTERA1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 674 | 0
3845 | OUGHTERARD | OUGHTERA_38B | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 675 | 0
3846 | BALLYTIVNAN | BALLYTIV1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 676 | 0
3847 | BALLYTIVNAN | BALLYTIV2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 677 | 64
3848 | DEREEN_38 | DEREEN_33 | T431_50_MVA | 41.6 | 33 | 0 | 678 | 0
3849 | CURRALEIGH | CURRALEI1_20 | T422_5_MVA CURRALEIGH | 41.6 | 21.4 | 2 | 679 | 20
3850 | CURRALEIGH | CURRALEI2_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 680 | 0
3851 | VIRGINIA | VIRGINIA1_10 | T41_5_MVA_VIRGINIA | 41.6 | 10.7 | 0 | 681 | 0
3852 | VIRGINIA | VIRGINIA2_10 | T42_5_MVA_VIRGINIA | 41.6 | 10.7 | 1 | 682 | 64
3853 | CLARECASTLE | CLARECAST_10 | CUST1_5MVA | 41.6 | 10.7 | 0 | 683 | 0
3854 | CLARECASTLE | CLARECAST_10 | CUST2_5MVA CLARECASTLE | 41.6 | 10.7 | 0 | 684 | 0
3855 | CASTLELYONS | CASTLELY1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 685 | 0
3856 | CASTLELYONS | CASTLELY2_20 | T422_5_MVA CASTLELYONS | 41.6 | 21.4 | 1 | 686 | 64
3857 | GILLOGUE | GILLOGU1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 687 | 0
3858 | GILLOGUE | GILLOGU2_10 | T42_5_MVA GILLOGUE | 41.6 | 10.7 | 1 | 688 | 64
3859 | CARRIGSHANE | CARRIGSHA_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 689 | 0
3860 | CARRIGSHANE | CARRIGSH2_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 690 | 64
3861 | GURTEEN | GURTEEN1_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 691 | 64
3862 | CALLAN | CALLAN2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 692 | 64
3863 | CALLAN | CALLAN3_10 | T41_5MVA CALLAN | 41.6 | 10.7 | 0 | 693 | 0
3864 | CALLAN | CALLAN1_10 | CUST_3_2MVA | 41.6 | 10.7 | 0 | 694 | 0
3865 | RAHANS | RAHANS_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 695 | 64
3866 | BALLYBEGGAN | BALLYBEGGAN_1 | T43_10_MVA BALLYBEGGAN | 41.6 | 10.7 | 0 | 696 | 0
3867 | BALLYBEGGAN | BALLYBEGGAN_ | T44_10_MVA | 41.6 | 10.7 | 1 | 697 | 64
3868 | RANDALSTOWN | RANDALST_10 | T41_5_MVA_RANDALS | 41.6 | 10.7 | 1 | 698 | 64
3869 | RANDALSTOWN_T422 | RANDALST_20 | T422_5_MVA_RANDALS | 41.6 | 21.4 | 1 | 699 | 64
3870 | ANNABELLA | ANNABELLA_10 | CUST_T41_7.5 | 41.6 | 10.7 | 0 | 700 | 0
3871 | NEWBROOK | NEWBROOK_10 | CUST1_7_5_MV_NEWBROOK | 41.6 | 10.7 | 1 | 701 | 0
3872 | NEWBROOK | NEWBROOK_10 | T42_5_MVA_NEWBROOK | 41.6 | 10.7 | 1 | 702 | 64
3873 | TULLYNAMALRA | TULLYN1_10 | T41_5MVA_TULLYN | 41.6 | 10.7 | 0 | 703 | 0
3874 | TULLYNAMALRA | TULLYN2_10 | T42_5MVA_TULLYN | 41.6 | 10.7 | 1 | 704 | 64
3875 | FINAWN_38 | FINAWN_20 | GT1_40_MVA | 41.6 | 21.4 | 0 | 705 | 0
3876 | BWEENG | BWEENG_20 | T421_26MVA_2 | 41.6 | 21.4 | 0 | 706 | 0
3877 | CRANMORE | CRANMORE1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 707 | 0
3878 | CRANMORE | CRANMORE2_10 | T42_5_MVA CRANMORE | 41.6 | 10.7 | 1 | 708 | 64
3879 | BUNCLODY | BUNCLODY1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 709 | 0
3880 | BUNCLODY | BUNCLODY2_20 | T422_5_MVA BUNCLODY | 41.6 | 21.4 | 1 | 710 | 64
3881 | BUNCLODY | KILBRANIS_20 | T424_10_MVA | 41.6 | 21.4 | 0 | 711 | 0
3882 | PORTLAW_38 | PORTLAW1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 712 | 0
3883 | PORTLAW_38 | PORTLAW2_10 | T42_2_MVA PORTLAW | 41.6 | 10.7 | 1 | 713 | 64
3884 | CARRAROE | CARRAROE_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 714 | 64
3885 | BALLINEEN | BALNN_G1_CP1 | CUST_T41_10_ BALLINEEN | 41.6 | 10.7 | 0 | 715 | 0
3886 | BALLINEEN | BALLINEEN_10 | CUST_T42_5_M | 41.6 | 10.7 | 0 | 716 | 0
3887 | FLAXFORT | FLAXFORT1_10 | CUST_T42_10_ | 41.6 | 10.7 | 0 | 717 | 0
3888 | BUSHFIELD | BUSHFLD1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 718 | 64
3889 | BUSHFIELD | BUSHFLD2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 719 | 0
3890 | BALLYCONRA | BALCN_G1_BA1 | CUST1_10_MVA | 41.6 | 10.7 | 0 | 720 | 0
3891 | BALLYCONRA | BALCN_G2_BA1 | CUST2_10_MVA | 41.6 | 10.7 | 0 | 721 | 0
3892 | BALLYCONRA | BALLYCONR_20 | T423_10_MVA | 41.6 | 21.4 | 1 | 722 | 64
3893 | BOYLE | BOYLE1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 723 | 0
3894 | BOYLE | BOYLE2_10 | T42_5_MVA BOYLE | 41.6 | 10.7 | 1 | 724 | 64
3895 | FISHERSTOWN | FISHERST1_10 | CUST1_5_MVA | 41.6 | 10.7 | 0 | 725 | 0
3896 | FISHERSTOWN | FISHERST2_10 | CUST2_5_MVA | 41.6 | 10.7 | 0 | 726 | 0
3897 | NEWMARKET (SR) | NEWMKT_SR_10 | T42_5_MVA NEWMARKET_SR | 41.6 | 10.7 | 1 | 727 | 64
3898 | NEWMARKET (SR) | NEWMKT2_SR_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 728 | 0
3899 | KILMONEY | KILMONEY1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 729 | 0
3900 | KILMONEY | KILMONEY2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 730 | 64
3901 | CAUSEWAY | CAUSEWAY_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 731 | 0
3902 | CAUSEWAY | CAUSEWAY1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 732 | 64
3903 | SRAH | SRAH1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 733 | 0
3904 | SRAH | SRAH2_10 | T42_5_MVA SRAH | 41.6 | 10.7 | 1 | 734 | 64
3905 | SRAH_T43 | SRAH3_10 | T43_10_MVA | 41.6 | 10.7 | 1 | 735 | 64
3906 | SRAH | SRAH4_10 | CUST_10_MVA_ | 41.6 | 10.7 | 0 | 736 | 0
3907 | Purcells Inch | PURCELLS1_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 737 | 64
3908 | Purcells Inch | PURCELLS2_10 | T42_10_MVA | 41.6 | 10.7 | 0 | 738 | 0
3909 | FAIRHILL | FAIRHILL_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 739 | 64
3910 | ORANMORE | ORANMORE1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 740 | 0
3911 | ORANMORE | ORAN_T44 | T44_10_MVA | 41.6 | 10.7 | 1 | 741 | 64
3912 | BUSH | BUSH1_20 | T421_5_MVA_BUSH | 41.6 | 21.4 | 0 | 742 | 0
3913 | BUSH | BUSH2_20 | T422_5_MVA_BUSH | 41.6 | 21.4 | 1 | 743 | 64
3914 | Rossgier | ROSGIER_10 | T41_5_MVA_ROS | 41.6 | 10.7 | 0 | 744 | 0
3915 | Rossgier | ROSGIER1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 745 | 64
3916 | MOHILL | MOHILL1_20 | T421_5MVA | 41.6 | 21.4 | 0 | 746 | 0
3917 | MOHILL | MOHILL2_20 | T422_5_MVA MOHILL | 41.6 | 21.4 | 1 | 747 | 64
3918 | FIDDANDARRY | FIDDANDAR_20 | T421_50MVA | 41.6 | 21.4 | 0 | 748 | 0
3919 | ENNISCRONE | ENNISC1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 749 | 0
3920 | ENNISCRONE | ENNISC2_20 | T422_5_MVA ENNISCRONE | 41.6 | 21.4 | 1 | 750 | 64
3921 | ISLAND | ISLAND1_10 | CUST1_10_MVA ISLAND | 41.6 | 10.7 | 0 | 751 | 0
3922 | ISLAND | ISLAND2_10 | CUST2_10_MVA | 41.6 | 10.7 | 0 | 752 | 0
3923 | BREWERY ROAD | BREWERY_RD | T41_10_MVA | 41.6 | 10.7 | 1 | 753 | 0
3924 | BREWERY ROAD | BREWERY_RD | T42_10_MVA | 41.6 | 10.7 | 1 | 754 | 64
3925 | ACHILL | ACHILL_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 755 | 64
3926 | BALLYMOTE | BALLYMOTE_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 756 | 64
3927 | KILCOOLE | KILCOOL1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 757 | 0
3928 | KILCOOLE | KILCOOL2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 758 | 64
3933 | LONGFORD | LONGFORD_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 759 | 0
3934 | LONGFORD | LONGFORD1_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 760 | 64
3935 | BELMULLET | BELMULLET_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 761 | 64
3936 | KILCAR | KILCAR_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 762 | 64
3937 | EMYVALE | EMYVALE_20 | T422_5_MVA_EMYVALE | 41.6 | 21.4 | 1 | 763 | 64
3938 | Newtowncunningham | NEWTOWNCU_10 | T41_5_MVA_NEWT | 41.6 | 10.7 | 1 | 764 | 0
3939 | Newtowncunningham | NEWTOWNCU_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 765 | 64
3940 | CORKERMORE | CORKRMORE_20 | T421_12MVA | 41.6 | 21.4 | 1 | 766 | 64
3941 | JOHNSTOWN | JOHNSTWN1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 767 | 64
3942 | JOHNSTOWN | JOHNSTWN2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 768 | 0
3943 | CARRIGTHOMAS | BWNMRE_WF_20 | T32_31_5MVA | 41.6 | 21.4 | 0 | 769 | 0
3944 | TALBOTS INCH | TALBOTS1_10 | T42_5_MVA TALBOTS INCH | 41.6 | 10.7 | 1 | 770 | 64
3945 | TALBOTS INCH | TALBOTS2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 771 | 0
3946 | Finisklin | FINISKLIN_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 772 | 0
3947 | Finisklin | FINISKLIN_10 | T42_5_MVA FINISKLIN | 41.6 | 10.7 | 1 | 773 | 64
3948 | CASTLETOWNBERE | CTWNBERE1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 774 | 64
3949 | CASTLETOWNBERE_T421 | CTWNBERE2_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 775 | 64
3950 | BALLYCOOLIN | BALLYCOL1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 776 | 64
3951 | BALLYCOOLIN | BALLYCOL2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 777 | 0
3952 | BALLYCOOLIN | BALLYCOL3_10 | T43_10_MVA | 41.6 | 10.7 | 0 | 778 | 0
3953 | CLONROCHE | CLONROCHE_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 779 | 0
3954 | CLONROCHE | CLONROCHE_20 | T422_5_MVA CLONROCHE | 41.6 | 21.4 | 1 | 780 | 64
3955 | COLLIGAN | COLLIGAN1_10 | T42_10_MVA COLLIGAN | 41.6 | 10.7 | 1 | 781 | 64
3956 | COLLIGAN | COLLIGAN2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 782 | 0
3957 | ERRIGAL | ERRIGAL_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 783 | 64
3958 | ERRIGAL_T422 | ERRIGAL_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 784 | 64
3959 | INCHINASHING | INCHINASH_10 | T41_10_MVA INCHINASHING Customer | 41.6 | 10.7 | 0 | 785 | 0
3960 | INCHINASHING | INCHINASH_10 | T42_Customer_10_MVA | 41.6 | 10.7 | 0 | 786 | 0
3961 | CREAGH | CREAGH_T421 | T421_5MVA | 41.6 | 21.4 | 0 | 787 | 0
3962 | CREAGH | CREAGH_T422 | T422_5MVA | 41.6 | 21.4 | 1 | 788 | 64
3963 | CLARA | CLARA1_10 | T421_10_MVA | 41.6 | 21.4 | 0 | 789 | 0
3964 | CLARA | CLARA1_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 790 | 64
3965 | MEELICK_38 | MEELICK1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 791 | 0
3966 | MEELICK_38 | MEELICK2_10 | T42_5_MVA | 41.6 | 10.7 | 0 | 792 | 0
3967 | Hernsbrook | HERNSBROK_20 | T421_15MVA | 41.6 | 21.4 | 0 | 793 | 0
3968 | MOUNTGORRY | MOUNTGOR1_10 | T42_10_MVA_MOUNTGORRY | 41.6 | 10.7 | 1 | 794 | 64
3969 | MOUNTGORRY | MOUNTGOR2_10 | T41_10_MVA_MOUNTGORRY | 41.6 | 10.7 | 0 | 795 | 0
3970 | GLENAMADDY | GLENAMAD2_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 796 | 64
3972 | HEADFORD | HEADFRD2_10 | T42_10 _MVA_Temp | 41.6 | 10.7 | 2 | 797 | 4
3973 | CURRA | CURRA_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 798 | 64
3976 | BALLYDEHOB | BALLYDEHO_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 799 | 64
3977 | KILLACLOYNE | KILLACLYN_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 800 | 0
3978 | KILLACLOYNE | KILLACLYN_10 | T42_5_MVA KILLACLOYNE | 41.6 | 10.7 | 1 | 801 | 64
3979 | KILLACLOYNE_T43 | KILLACLYN_10 | T43_10MVA | 41.6 | 10.7 | 1 | 802 | 64
3980 | OLDCASTLE | OLDCSTLE2_10 | T41_5_MVA_OLDCASTLE | 41.6 | 10.7 | 1 | 803 | 64
3981 | OLDCASTLE_T422 | OLDCSTLE1_20 | T422_5_MVA_OLDCASTLE | 41.6 | 21.4 | 1 | 804 | 64
3982 | SHERCOCK | SHERCOCK1_10 | T41_5_MVA_SHERCOCK | 41.6 | 10.7 | 0 | 805 | 0
3983 | SHERCOCK | SHERCOCK2_10 | T42_5_MVA_SHERCOCK | 41.6 | 10.7 | 1 | 806 | 64
3984 | SPADDEN | SPADDEN_20 | GT1_20_MVA | 41.6 | 21.4 | 0 | 807 | 0
3985 | LAWLESSTOWN | LAWLESSTOWN_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 808 | 64
3986 | LAWLESSTOWN | LAWLESSTOWN1_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 809 | 0
3987 | CLOONFGNA_38 | Cloonfaughna | T421_50_MVA | 41.6 | 33 | 0 | 810 | 0
3988 | DERRYCRAMPH | DERRYCRA1_10 | T41_5MVA | 41.6 | 10.7 | 0 | 811 | 0
3989 | DERRYCRAMPH | DERRYCRA2_10 | T42_5MVA DERRYCRAMPH | 41.6 | 10.7 | 1 | 812 | 64
3990 | DULEEK | DULEEK1_20 | T421_5_MVA_DULEEK | 41.6 | 21.4 | 0 | 813 | 0
3991 | DULEEK | DULEEK_20 | T422_5_MVA_DULEEK | 41.6 | 21.4 | 1 | 814 | 64
3992 | CLONARD | CLONARD1_10 | T42_5_MVA CLONARD | 41.6 | 10.7 | 1 | 815 | 64
3993 | CLONARD | CLONARD2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 816 | 0
3994 | LOUGHDALE_38 | LOUGHDALE_20 | T421_50MVA | 41.6 | 21.4 | 0 | 817 | 0
3995 | Moneycooley | MONEYCOL1_10 | T42_10_MVA_MONEYCOOLY | 41.6 | 10.7 | 0 | 818 | 0
3996 | Moneycooley | MONEYCOL2_10 | T41_10_MVA_MONEYCOOLY | 41.6 | 10.7 | 0 | 819 | 0
3997 | Moneycooley | MONEYCOL3_10 | T44_10_MVA_MONEYCOOLY | 41.6 | 10.7 | 1 | 820 | 64
3999 | PARKMORE | PARKMORE_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 821 | 0
4000 | PARKMORE | PARKMORE_10 | T42_5_MVA PARKMORE | 41.6 | 10.7 | 1 | 822 | 64
4001 | BAYSIDE | BAYSIDE1_10 | CUST2_3_2_MV | 41.6 | 1.5 | 0 | 823 | 0
4002 | BAYSIDE | BAYSIDE2_10 | CUST1_3_2_MV | 41.6 | 1.5 | 0 | 824 | 0
4003 | PARKVIEW | PARKVIEW1_10 | CUST2_3_2_MV PARKVIEW | 41.6 | 1.5 | 0 | 825 | 0
4004 | PARKVIEW | PARKVIEW2_10 | CUST1_3_2_MV | 41.6 | 1.5 | 0 | 826 | 0
4005 | HOLYROOD PARK | HLYRODPK_1 | CUST2_3_2_MV | 41.6 | 1.5 | 0 | 827 | 0
4006 | HOLYROOD PARK | HLYRODPK_2 | CUST1_3_2_MV HOLYROOD PAR | 41.6 | 1.5 | 0 | 828 | 0
4007 | SHANKILL-D | SHANKILL1_10 | CUST2_3_2_MV SHANKILL-D | 41.6 | 10.7 | 0 | 829 | 0
4008 | SHANKILL-D | SHANKILL2_10 | CUST1_3_2_MV | 41.6 | 10.7 | 0 | 830 | 0
4009 | CASTLETROY | CASLTRY1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 831 | 0
4010 | CASTLETROY | CASLTRY2_10 | T42_5_MVA CASTLETROY | 41.6 | 10.7 | 1 | 832 | 64
4011 | PALLAS | PALLAS1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 833 | 0
4012 | PALLAS | PALLAS2_10 | T42_5_MVA PALLAS | 41.6 | 10.7 | 1 | 834 | 64
4013 | ROSCREA | ROSCREA1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 835 | 0
4014 | ROSCREA | ROSCREA2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 836 | 64
4015 | OLDTOWN_38 | OLDTOWN_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 837 | 0
4016 | KILSARAN | KILSARAN_10 | T41_5_MVA_KILSARAN | 41.6 | 10.7 | 1 | 838 | 64
4017 | FERMOY NORTH | FERMOYNT1_10 | T42_5_MVA FERMOY NORTH | 41.6 | 10.7 | 1 | 839 | 64
4018 | FERMOY NORTH | FERMOYNT2_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 840 | 0
4019 | BIRR | BIRR1_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 841 | 64
4020 | BIRR_T422 | BIRR_20kV | T422_10_MVA | 41.6 | 21.4 | 1 | 842 | 64
4021 | BALLYCONNELL | BALLYCON1_20 | T421_5MVA Ballyconnell | 41.6 | 21.4 | 0 | 843 | 0
4022 | BALLYCONNELL | BALLYCON2_20 | T422_5MVA | 41.6 | 21.4 | 1 | 844 | 64
4023 | HOLLY HILL | HOLLYHIL1_10 | CUST_T41_5_M | 41.6 | 10.7 | 0 | 845 | 0
4024 | HOLLY HILL | HOLLYHIL2_10 | CUST_T42_5_M | 41.6 | 10.7 | 0 | 846 | 0
4025 | KILMEADEN | KILMEADEN_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 847 | 64
4026 | TEMPLEMORE | TEMPLEM1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 848 | 0
4027 | TEMPLEMORE | TEMPLEM2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 849 | 64
4028 | RECESS | RECESS_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 850 | 64
4029 | CRANNY | CRANNY1_10 | T41_2_MVA | 41.6 | 10.7 | 1 | 851 | 64
4030 | SPRINGS | SPRINGS1_20 | T422_10_MVA SPRINGS | 41.6 | 21.4 | 1 | 852 | 64
4031 | SPRINGS | SPRINGS2_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 853 | 0
4032 | CURRAGLASS | CURRAGLAS_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 854 | 64
4033 | FINNEA | FINNEA_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 855 | 0
4034 | FINNEA | FINNEA2_20 | T422_5_MVA FINNEA | 41.6 | 21.4 | 1 | 856 | 64
4035 | SHERIFF ST | SHERIFF1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 857 | 64
4036 | SHERIFF ST | SHERIFF2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 858 | 0
4037 | CALLEE_38 | CALLEE_20 | T42_40_MVA | 41.6 | 21.4 | 0 | 859 | 0
4038 | CONG | CONG1_20 | T422_5MVA | 41.6 | 21.4 | 1 | 860 | 64
4039 | CONG | CONG2_20 | T421_5MVA CONG | 41.6 | 21.4 | 0 | 861 | 0
4040 | DUNDERROW | DUNDER1_10 | T41_customer_15_MVA | 41.6 | 10.7 | 0 | 862 | 0
4041 | DUNDERROW | DUNDER2_10 | T42_customer_15_MVA | 41.6 | 10.7 | 0 | 863 | 0
4042 | CASTLEFARM | CSTLEFRM1_10 | T42_10_MVA CASTLEFARM_Customer | 41.6 | 10.7 | 0 | 864 | 0
4043 | CASTLEFARM | CSTLEFRM2_10 | T41_10_MVA_Customer | 41.6 | 10.7 | 0 | 865 | 0
4044 | GALMOY | GALMOY1_6.6 | T41_10_MVA | 41.6 | 6.6 | 0 | 866 | 0
4045 | GALMOY | GALMOY_6.6 | T42_10_MVA | 41.6 | 6.6 | 0 | 867 | 0
4046 | CAVAN | CAVAN3_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 868 | 64
4047 | CAVAN_T421 | CAVAN_20 | T421_10_MVA | 41.6 | 21.4 | 1 | 869 | 64
4050 | RATHDRUM | RATHDR1_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 870 | 64
4051 | RATHDRUM | RATHDR2_10 | CUST2_5_MVA | 41.6 | 10.7 | 0 | 871 | 0
4052 | RATHDRUM | RATHDR3_10 | CUST1_5_MVA RATHDRUM | 41.6 | 10.7 | 0 | 872 | 0
4054 | BELVIEW | BELVIE1_20-1 | T421_15_MVA | 41.6 | 21.4 | 0 | 873 | 0
4055 | BELVIEW | BELVIE1_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 874 | 64
4056 | BALLYMACARRY | BALLYMAC_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 875 | 64
4057 | Windsor Road | WINDSR_RD_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 876 | 64
4058 | Windsor Road | WINDSR_RD1_20 | T421_5_MVA WINDSOR RD | 41.6 | 21.4 | 0 | 877 | 0
4059 | ANALOG | ANALOG1_10 | CUST1_15MVA | 41.6 | 10.7 | 0 | 878 | 0
4060 | ANALOG | ANALOG2_10 | CUST2_15MVA | 41.6 | 10.7 | 0 | 879 | 0
4063 | SNOWHILL | SNOWHILL_20 | T421_10_MVA cUSTOMER | 41.6 | 21.4 | 0 | 880 | 0
4064 | CROSSANA | CROSSANA_20 | GT1_47MVA | 41.6 | 21.4 | 0 | 881 | 0
4065 | LOUGHANALLA | LOUGHANA1_10 | T41_5_MVA_LOUGHAN | 41.6 | 10.7 | 0 | 882 | 0
4066 | LOUGHANALLA | LOUGHANA2_10 | T42_5_MVA_LOUGHAN | 41.6 | 10.7 | 1 | 883 | 64
4067 | LOUGHAN_38B | LOUGHANALLA | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 884 | 0
4068 | RUSHEEN_38 | RUSHEEN_20 | T421_20_MVA | 41.6 | 21.4 | 0 | 885 | 0
4069 | BALLYBAY | BALLYBAY1_10 | T41_10_MVA_BALLYBAY | 41.6 | 10.7 | 1 | 886 | 0
4070 | BALLYBAY | BALLYBAY2_10 | T42_10_MVA_BALLYBAY | 41.6 | 10.7 | 1 | 887 | 20
4072 | FOXHOLE | FOXHOLE1_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 888 | 0
4073 | FOXHOLE | FOXHOLE2_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 889 | 64
4074 | BALGADDY | BALGADDY | T41_10MVA | 41.6 | 10.7 | 1 | 890 | 0
4075 | BALGADDY | BALGADDY | T42_10MVA | 41.6 | 10.7 | 1 | 891 | 64
4076 | MONKSLAND | MONKSLA1_10 | T41_Customer_10_MVA | 41.6 | 10.7 | 0 | 892 | 0
4077 | MONKSLAND | MONKSLA2_10 | T42_Customer_10_MVA | 41.6 | 10.7 | 0 | 893 | 0
4078 | BALLYBRIT_38 | BALLYBRIT_20 | T422_16_MVA CUSTOMER | 41.6 | 21.4 | 0 | 894 | 0
4079 | BALLYBRIT_38 | BALLYBRIT_20 | T421_16_MVA CUSTOMER | 41.6 | 21.4 | 0 | 895 | 0
4080 | ACADEMY_STREET_T44 | ACADEMY_10 | T44_10_MVA_ACADEMY | 41.6 | 10.7 | 1 | 896 | 64
4081 | ACADEMY_STREET | ACADEMY1_20 | T421_5_MVA_ACADEMY | 41.6 | 21.4 | 0 | 897 | 0
4082 | ACADEMY_STREET | ACADEMY2_20 | T422_5_MVA_ACADEMY | 41.6 | 21.4 | 1 | 898 | 64
4083 | Clarkstown | CLARKESTN_10 | T41_5_MVA_CLARKESTN | 41.6 | 10.7 | 1 | 899 | 64
4084 | LIFFEY VALLEY | LIFFEYVALY_1 | T41_10MVA | 41.6 | 10.7 | 0 | 900 | 0
4085 | LIFFEY VALLEY | LIFFEYVALY_2 | T42_10MVA | 41.6 | 10.7 | 1 | 901 | 64
4086 | DOCK ROAD | DOCK ROAD_5 | T41_5_MVA | 41.6 | 10.7 | 0 | 902 | 0
4087 | DOCK ROAD | DOCK_ROAD_5 | T42_5_MVA DOCK ROAD | 41.6 | 10.7 | 2 | 903 | 8
4088 | STICKILLEN | STICKILEN_10 | T41_5_MVA_STICKILLEN | 41.6 | 10.7 | 0 | 904 | 0
4089 | STICKILLEN | STICKILN2_10 | T42_5_MVA_STICKILLEN | 41.6 | 10.7 | 1 | 905 | 64
4090 | CARRIGCANNON | CARRIGCN_20 | T421_26MVA_1 | 41.6 | 21.4 | 0 | 906 | 0
4091 | CARNSORE_WF | CRNSR_G1_CNS | T41_15_MVA | 41.6 | 21.4 | 0 | 907 | 0
4092 | SHILLELAGH | SHILLEL1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 908 | 0
4093 | SHILLELAGH | SHILLEL2_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 909 | 64
4094 | AGHAGAD | AGHAGAD1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 910 | 0
4095 | AGHAGAD | AGHAGAD2_10 | T42_5_MVA AGHAGAD | 41.6 | 10.7 | 1 | 911 | 64
4096 | AGHAGAD | AGHAGAD_38B | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 912 | 0
4097 | CLONMINCH | CLONMINCH_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 913 | 64
4098 | CLONMINCH_T422 | CLONMINCH_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 914 | 64
4099 | GLENMORE_38 | GLENMORE_20 | T41_20MVA | 41.6 | 21.4 | 0 | 915 | 0
4100 | KNOCKAWGA_38 | KNOCKAWGA_20 | GT1_30_6MVA | 41.6 | 21.4 | 0 | 916 | 0
4101 | MULLINANALT | MULLINAN_20 | T421_10MVA_MULLINAN | 41.6 | 21.4 | 0 | 917 | 0
4102 | Meenachullalan_38 | Meenachullalan | T41_15MVA | 41.6 | 21.4 | 0 | 918 | 0
4103 | CARLISLE | Carlisle1_1.5 | CUST_3_2_MVA | 41.6 | 1.5 | 0 | 919 | 0
4104 | CARLISLE | Carlisle2_1.5 | CUST2_3_2_MV | 41.6 | 1.5 | 0 | 920 | 0
4105 | BALBRIGGAN | BALBRIG1_10 | T41_10_MVA_BALBRIGGAN | 41.6 | 10.7 | 0 | 921 | 0
4106 | BALBRIGGAN | BALBRIG2_10 | T42_10_MVA_BALBRIGGAN | 41.6 | 10.7 | 1 | 922 | 12
4107 | RATHDOWN | RATHDOWN1_10 | T41_customer_2_MVA | 41.6 | 10.7 | 0 | 923 | 0
4108 | RATHDOWN | RATHDOWN2_10 | T42_customer_2_MVA RATHDOWN | 41.6 | 10.7 | 0 | 924 | 0
4109 | PEARSE Street | PEARS S1_1.5 | CUST_3_2_MVA | 41.6 | 1.5 | 0 | 925 | 0
4110 | PEARSE Street | PEARS S2_1.5 | CUST2_3_2_MV PEARSE ST | 41.6 | 1.5 | 0 | 926 | 0
4111 | RAHENY | RAHENY 1.5 | CUST_3_2_MVA | 41.6 | 1.5 | 0 | 927 | 0
4112 | RAHENY | RAHENY 1.5 | CUST_3_2_MVA | 41.6 | 1.5 | 0 | 928 | 0
4113 | PORTMARNOCK | PORTMARNOCK | CUST1_3_2_MV | 41.6 | 1.5 | 0 | 929 | 0
4114 | PORTMARNOCK | PORTMARNOCK | CUST2_3_2_MV | 41.6 | 1.5 | 0 | 930 | 0
4115 | DALKEY | DALKEY_1.5 | CUST_3_2_MVA | 41.6 | 1.5 | 0 | 931 | 0
4116 | DALKEY | DALKEY_1.5 | CUST2_3_2_MV | 41.6 | 1.5 | 0 | 932 | 0
4117 | ROCK HILL | Rock Hill1.5 | CUST_3_2_MVA | 41.6 | 1.5 | 0 | 933 | 0
4118 | ROCK HILL | Rock Hill1.5_1 | CUST_3_2_MVA ROCK HILL | 41.6 | 1.5 | 0 | 934 | 0
4119 | SWORDS | SWORDS1_10 | T41_10_MVA_SWORDS | 41.6 | 10.7 | 0 | 935 | 0
4120 | SWORDS | SWORDS2_10 | T42_10_MVA_SWORDS | 41.6 | 10.7 | 1 | 936 | 64
4121 | GARRYOWEN | GARRYOWN1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 937 | 0
4122 | GARRYOWEN | GARRYOWN2_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 938 | 64
4123 | BEDFORD ROWB | BDFORD B1_10 | T42_15_MVA BEDFORD ROWB | 41.6 | 10.7 | 1 | 939 | 64
4124 | BEDFORD ROWB | BDFORD B2_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 940 | 0
4125 | TURSILLAGH | TURSILLA_20 | T421_16MVA | 41.6 | 21.4 | 0 | 941 | 0
4126 | TURSILLAGH | TURSILLA2_20 | T422_7_5MVA | 41.6 | 21.4 | 0 | 942 | 0
4127 | MILANE_HILL | MILANE_HILL_20 | T1_7_65MVA | 41.6 | 21.4 | 0 | 943 | 0
4128 | Bellfield | BELLEFLD1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 944 | 0
4129 | Bellfield | BELLEFLD2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 945 | 64
4130 | LEIXLIP_G38 | LEIXLIP_G5_LI5 | T41_5_4MVA_LEIXLIP generation | 41.6 | 10.7 | 0 | 946 | 0
4131 | DUNSINK | DUNSINK_GEN | T1_5MVA | 41.6 | 10.7 | 0 | 947 | 0
4132 | Currabwee Wind Farm | Currabwee Wind Farm_20 | T_AER_5MVA | 41.6 | 21.4 | 0 | 948 | 0
4133 | CULLIAGH | CULLIAGH_20 | T1_15MVA | 41.6 | 21.4 | 0 | 949 | 0
4134 | CARK | CARK_20 | T1_16MVA | 41.6 | 21.4 | 0 | 950 | 0
4135 | DRUMLOUGH | DRUMLOUGH_22 | TI_5_2MVA | 41.6 | 21.4 | 0 | 951 | 0
4136 | LARGAN HILL | LARGAN_H_20 | T1_5MVA | 41.6 | 21.4 | 0 | 952 | 0
4137 | CLOONBANNIN | CLOONBA_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 953 | 64
4138 | CLOONBANNIN_T421 | CLOONBA_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 954 | 64
4139 | LLOYD_38 | LLOYD1_10 | T41_5_MVA_LLOYD | 41.6 | 10.7 | 0 | 955 | 0
4140 | LLOYD_38 | LLOYD2_10 | T42_5_MVA_LLOYD | 41.6 | 10.7 | 1 | 956 | 64
4141 | BEAMHILL_38 | BEAMHILL_20 | T421_16MVA | 41.6 | 21.4 | 0 | 957 | 0
4142 | RICHFIELD_38 | RICHFIELD_20 | T421_31MVA | 41.6 | 21.4 | 0 | 958 | 0
4143 | GREYSTONES | GREYSTO1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 959 | 0
4144 | GREYSTONES | GREYSTO2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 960 | 64
4145 | Serpentine Avenue | SERPENTINE_1 | CUST_6_MVA | 41.6 | 10.7 | 0 | 961 | 0
4146 | Serpentine Avenue | SERPENTINE_2 | CUST_6_MVA SERPENTINE | 41.6 | 10.7 | 0 | 962 | 0
4147 | CLONDALKIN | CLONDALK1_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 963 | 64
4148 | CLONDALKIN | CLONDALK2_10 | T42_10_MVA | 41.6 | 10.7 | 0 | 964 | 0
4149 | CLONDALKIN | CLONDALK3_10 | T44_10_MVA | 41.6 | 10.7 | 0 | 965 | 0
4150 | CROCKAHENNY | CROCKAHEN_20 | T1_5_MVA | 41.6 | 21.4 | 0 | 966 | 0
4151 | HARBOUR | HARBOUR1_10 | CUST1_3_2_MV | 41.6 | 1.5 | 0 | 967 | 0
4152 | HARBOUR | HARBOUR2_10 | CUST2_3_2_MV HARBOUR | 41.6 | 1.5 | 0 | 968 | 0
4153 | MUINGNMINANE | MUINGANE_20 | T421_17_5MVA | 41.6 | 21.4 | 0 | 969 | 0
4154 | GLANTA COMMONS | GLANTA_20 | T421_60_MVA | 41.6 | 21.4 | 0 | 970 | 0
4155 | MOATE | MOATE1_10 | T41_5_MVA_ST | 41.6 | 10.7 | 0 | 971 | 0
4156 | MOATE | MOATE2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 972 | 64
4157 | BURNWOOD_38 | BURNWOOD_10 | T42_5_MVA | 41.6 | 10.7 | 0 | 973 | 0
4158 | BURNWOOD_38 | BURNWOOD_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 974 | 0
4159 | PARKROE | PARKROE_20 | T421_60MVA | 41.6 | 21.4 | 0 | 975 | 0
4160 | CROUGHMARKE | CROUGHMAR_20 | CUST_35MVA | 41.6 | 21.4 | 0 | 976 | 0
4161 | MULTEEN_38 | MULTEEN1_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 977 | 0
4162 | MULTEEN_38 | MULTEEN2_20 | CUST_40MVA | 41.6 | 21.4 | 0 | 978 | 0
4163 | MILESTONE_38 | MILESTONE_20 | T422_16MVA | 41.6 | 21.4 | 0 | 979 | 0
4164 | STREAMHILL | STREAMHIL_20 | T421_40_MVA_ | 41.6 | 21.4 | 0 | 980 | 0
4165 | PIPERHILL_38 | PIPERHILL_20 | T421_40_MVA_ | 41.6 | 21.4 | 0 | 981 | 0
4166 | KNOCKAFUTERA | KNOCKAFUTERA_20 | T421_25_MVA | 41.6 | 21.4 | 0 | 982 | 0
4167 | FERNS | FERNS1_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 983 | 64
4168 | BALLYMAHON | BALLYMAH1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 984 | 0
4169 | BALLYMAHON | BALLYMAH2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 985 | 64
4170 | PATRICKSWELL | PATRICKW1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 986 | 0
4171 | PATRICKSWELL | PATRICKW2_20 | T422_5_MVA PATRICKSWELL | 41.6 | 21.4 | 1 | 987 | 64
4172 | CHARLESTOWN | CHARLESTN_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 988 | 64
4173 | IIG_CUSTOMER | IIG_CUSTOMER | CUST1_10MVA | 41.6 | 10.7 | 0 | 989 | 0
4174 | BEDFORD ROWA | BEDFRDA1_10 | T43_15_MVA | 41.6 | 10.7 | 0 | 990 | 0
4175 | BEDFORD ROWA | BEDFRDA2_10 | T44_15_MVA | 41.6 | 10.7 | 1 | 991 | 64
4177 | BRUFF_38S | BRUFF_38B | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 992 | 0
4178 | TRAMORE_38S | TRAMORE_38B | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 993 | 0
4179 | GURRANE_38B | GURRANEBANE | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 994 | 0
4181 | GURTEEN_38B | GURTEEN1_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 995 | 0
4182 | CLARA_38B | CLARA_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 996 | 0
4183 | KILRUSH_38B | KILRUSH_38S | BOOSTER | 41.6 | 41.6 | 0 | 997 | 0
4184 | Castletownroche | CASTLETNR_10 | T41_5_MVA | 41.6 | 10.7 | 1 | 998 | 64
4185 | KILGARV_38B | KILGARV1_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 999 | 0
4187 | KLSHAN_38B | KILSHAN1_38S | BOOSTER | 41.6 | 41.6 | 0 | 1000 | 0
4188 | LOUGHRE1_38B | LOUGHRE1_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1001 | 0
4189 | LOUGHRE2_38B | LOUGHRE_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1002 | 0
4190 | ROSCOMON_38B | ROSCOMM_38S | BOOSTER | 41.6 | 41.6 | 0 | 1003 | 0
4191 | BALLYJAM_38B | BALLYJA1_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1004 | 0
4192 | ATHENRY_T423 | ATHENRY_20 | T423_10_MVA | 41.6 | 21.4 | 1 | 1005 | 64
4193 | LUMCLOON_38B | LUMCLOON_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1006 | 0
4194 | Portarlington_T43 | PORTARL3_10 | T43_5_MVA | 41.6 | 10.7 | 1 | 1007 | 64
4195 | PORTARL_38B | Portarlington_T43 | BOOSTER | 41.6 | 41.6 | 0 | 1008 | 0
4196 | ROSBER_38B | ROSBER_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1009 | 0
4199 | TRIM_38B | TRIM1_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1010 | 0
4201 | CARRIKM_38B | CARRICKM_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1011 | 0
4202 | KILROSS_38B | KILROSS1_38S | BOOSTER | 41.6 | 41.6 | 0 | 1012 | 0
4203 | BALLYKEE_38S | BALLYKEE_38B | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1013 | 0
4204 | KILLESHA_38B | KILLESH1_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1014 | 0
4205 | RAMSTOW_38B | RAMSTOW1_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1015 | 0
4206 | BALTING_38S | BALTINGL_38B | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1016 | 0
4207 | LISMORE1_38S | LISMORE2_38S | BOOSTER | 41.6 | 41.6 | 0 | 1017 | 0
4208 | ARK_BKS_38S | ARK_BKS_WF | L_27MVA_ISOL | 41.6 | 41.6 | 0 | 1018 | 0
4209 | DUNGARVN_HoT | DUNGR_HoT_LV | HOT_100_KVA | 41.6 | 0.38 | 0 | 1019 | 0
4210 | NENAGH_38B | NENAGH2_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1020 | 0
4211 | MOUNTRATH | MTRATH_38B | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1021 | 0
4213 | KILCOLGAN | KILCOLGAN_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 1022 | 64
4214 | KILCOLGAN_T421 | KILCOLGAN_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 1023 | 64
4215 | NEWTOWN_38B | NEWTOWN_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1024 | 0
4216 | ERRIGAL_38B | ERRIGAL_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1025 | 0
4217 | LAWLESST_38S | LAWLESSTO_10 | T43_10_MVA_CUSTOMER | 41.6 | 10.7 | 0 | 1026 | 0
4218 | LAWLESST_38S | LAWLESSTO_10 | T44_10_MVA_CUSTOMER | 41.6 | 10.7 | 0 | 1027 | 0
4219 | RECESS1 | RECESS_38B | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1028 | 0
4220 | FINNEA_38B | FINNEA | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1029 | 0
4221 | GORTLEE | GORTLEE1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 1030 | 0
4222 | GORTLEE | GORTLEE2_10 | T42_10_MVA GORTLEE | 41.6 | 10.7 | 1 | 1031 | 64
4223 | ARTHURSTOWN | ARTR_G10_ATW | T410_1_6_MVA | 41.6 | 0.38 | 0 | 1032 | 0
4224 | ARTHURSTOWN | ARTR_G11_ATW | T411_1_6_MVA | 41.6 | 0.38 | 0 | 1033 | 0
4226 | ARTHURSTOWN | ARTR_G2_ATW | T42_1_6_MVA | 41.6 | 0.38 | 0 | 1034 | 0
4230 | ARTHURSTOWN | ARTR_G6_ATW | T46_1_6_MVA | 41.6 | 0.38 | 0 | 1035 | 0
4231 | ARTHURSTOWN | ARTR_G7_ATW | T47_1_6_MVA | 41.6 | 0.38 | 0 | 1036 | 0
4232 | ARTHURSTOWN | ARTR_G8_ATW | T48_1_6_MVA | 41.6 | 0.38 | 0 | 1037 | 0
4233 | ARTHURSTOWN | ARTR_G9_ATW | T49_1_6_MVA | 41.6 | 0.38 | 0 | 1038 | 0
4234 | RUSHFIELD_38 | RUSHFIELD_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 1039 | 0
4235 | CLONM_38S | CLONM_38B | BOOSTER | 41.6 | 41.6 | 0 | 1040 | 0
4236 | TOURNAFULLA | TOURNAFUL_20 | T41_10MVA | 41.6 | 21.4 | 0 | 1041 | 0
4237 | LOUGHBEG | LOUGHB1_10 | CUST1_5_MVA | 41.6 | 10.7 | 0 | 1042 | 0
4238 | SONNAGH | SONGH_G1_KST | T421_10_MVA | 41.6 | 21.4 | 0 | 1043 | 0
4239 | BALLYDHB_38B | BALLYDEHOB T | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1044 | 0
4240 | ARDNAREE | ARDNAREE1_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 1045 | 64
4241 | ARDNAREE_T421 | ARDNAREE1_20 | T421_10_MVA | 41.6 | 21.4 | 1 | 1046 | 64
4242 | KNOCKMULLEN | KNOCKMULLEN_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 1047 | 64
4243 | KNOCKMULLEN_T421 | KNOCKMULLEN_20 | T421_10_MVA | 41.6 | 21.4 | 1 | 1048 | 64
4250 | ENNISKEANE | ENNISKE1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 1049 | 0
4251 | ENNISKEANE | ENNISKE2_10 | T42_5_MVA ENNISKEANE | 41.6 | 10.7 | 1 | 1050 | 64
4252 | Newtownstalaban | NEWTOWN1_3.3 | CUST_T41_4_M_NEWTOWN | 41.6 | 3.3 | 0 | 1051 | 0
4253 | Newtownstalaban | NEWTOWN2_3.3 | CUST_T42_4_M_NEWTOWN | 41.6 | 3.3 | 0 | 1052 | 0
4254 | Newtownstalaban | NEWTOWN4_3.3 | CUST_T44_4_M_NEWTOWNST | 41.6 | 3.3 | 0 | 1053 | 0
4256 | MSD_38 | MERCK_SHA_10 | CUST2_10_MVA | 41.6 | 10.7 | 0 | 1054 | 0
4258 | BALLYMUN | BALLYMUN1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 1055 | 0
4259 | BALLYMUN | BALLYMUN2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 1056 | 64
4260 | PEMBROKE | PEMBROKE1_10 | T43_10_MVA | 41.6 | 10.7 | 0 | 1057 | 0
4261 | PEMBROKE | PEMBROKE2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 1058 | 0
4262 | PEMBROKE | PEMBROKE3_10 | T44_10_MVA | 41.6 | 10.7 | 1 | 1059 | 20
4263 | PEMBROKE_T42 | PEMBROKE4_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 1060 | 20
4264 | Monavea | MON/GORT_20 | T1_21_5_MVA | 41.6 | 21.4 | 0 | 1061 | 0
4265 | KILRUSH | KILRUSH1_10 | T41_5_MVA KILRUSH | 41.6 | 10.7 | 0 | 1062 | 0
4266 | KILRUSH | KILRUSH2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 1063 | 64
4267 | CHURCHTOWN | CHURCTWN1_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 1064 | 64
4268 | CHURCHTOWN_T422 | CHURCHTOWN_2 | T422_10_MVA | 41.6 | 21.4 | 1 | 1065 | 64
4269 | GARRYCASTLE | GARRYCAS1_10 | T41_15MVA | 41.6 | 10.7 | 0 | 1066 | 0
4270 | GARRYCASTLE | GARRYCAS2_10 | T42_15MVA | 41.6 | 10.7 | 1 | 1067 | 64
4271 | Kilcarragh | KILCARAGH1_20 | T421_5_MVA | 41.6 | 21.4 | 0 | 1068 | 0
4272 | Kilcarragh | KILCARAGH_20 | T422_5_MVA KILCARAGH_38 | 41.6 | 21.4 | 1 | 1069 | 64
4273 | KNOCKAPHUNTA | KNOCKAP1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 1070 | 0
4274 | KNOCKAPHUNTA | KNOCKAP2_10 | T42_5_MVA KNOCKAPHUNTA | 41.6 | 10.7 | 1 | 1071 | 64
4275 | CAHERDAVIN | CAHERDA1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 1072 | 0
4276 | CAHERDAVIN | CAHERDA2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 1073 | 64
4277 | CULLION | CULLION1_10 | T41_5_MVA_CUL | 41.6 | 10.7 | 0 | 1074 | 0
4278 | CULLION | CULLION2_10 | T42_5_MVA | 41.6 | 10.7 | 1 | 1075 | 64
4279 | MOUNT MISERY | MOUNT M1_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 1076 | 0
4280 | MOUNT MISERY | MOUNT M2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 1077 | 64
4338 | MILFORD_NR_2 | MLFRD_NR2_10 | T42_5MVA | 41.6 | 10.7 | 2 | 1078 | 20
4340 | MILFORD_NR_1 | MLFRD_NR1_10 | T41_5_MVA_MIL | 41.6 | 10.7 | 0 | 1079 | 0
4803 | ARTHURSTOWN | ARTR_G5_ATW | T45_1_6_MVA | 41.6 | 0.38 | 0 | 1080 | 0
4804 | ARTHURSTOWN | ARTR_G4_ATW | T44_1_6_MVA | 41.6 | 0.38 | 0 | 1081 | 0
4805 | ARTHURSTOWN | ARTR_G3_ATW | T43_1_6_MVA | 41.6 | 0.38 | 0 | 1082 | 0
4806 | ARTHURSTOWN | ARTR_G1_ATW | T41_1_6_MVA | 41.6 | 0.38 | 0 | 1083 | 0
4815 | LOUGHAN_38 | LOUGHAN_20 | T421_40_MVA | 41.6 | 21.4 | 0 | 1084 | 0
4816 | LISGLENNO_38 | LISGLENNO_20 | T421_30MVA | 41.6 | 21.4 | 0 | 1085 | 0
4823 | TAWNAH_B_110 | TAWNAH_6 | T102_8MVA | 110 | 6 | 0 | 1086 | 0
4824 | TAWNAH_B_110 | TAWNAH_6 | T101_8MVA | 110 | 6 | 0 | 1087 | 0
4833 | DONEGAL_38S | DONEGAL1_38S | BOOSTER_REVERSABLE | 41.6 | 41.6 | 0 | 1088 | 0
4840 | BORRISOLEIGH | BRISLIGH2_10 | T42_5_MVA | 41.6 | 10.7 | 0 | 1089 | 0
4841 | BORRISOLEIGH | BRISLIGH1_10 | T41_5_MVA BORRISOLEIGH | 41.6 | 10.7 | 0 | 1090 | 0
4846 | ABBEYLEIX | ABBEYLEIX_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 1091 | 64
4853 | KILTIMAGH_10 | KILTIMAGH_20 | T12_5_MVA | 10.7 | 21.4 | 0 | 1092 | 0
4864 | GLASLECK | GLASLECK_20 | T421_27_5MVA | 41.6 | 21.4 | 0 | 1093 | 0
4866 | CLOVASS | AVONBEG_20 | T41_20MVA | 41.6 | 21.4 | 0 | 1094 | 0
4870 | BOOLABAWN | BOOLBWN1_65 | CUST1_1_75_MVA | 41.6 | 0.65 | 0 | 1095 | 0
4873 | BOOLABAWN | BOOLBWN2_65 | 2T4873 | 41.6 | 0.65 | 0 | 1096 | 0
4880 | KINSALE | KINSALE1_20 | T423_10_MVA | 41.6 | 21.4 | 1 | 1097 | 64
5833 | COWCROSS_38 | COWCROSS1_10 | T41_15_MVA | 41.6 | 10.7 | 1 | 1098 | 64
5839 | URLINGFORD | URLINGFORD_20 | T421_10MVA | 41.6 | 21.4 | 1 | 1099 | 0
7990 | BARNAGEERAGH_110 | BARNAGEE3_11 | T103_50MVA | 110 | 10.7 | 0 | 1100 | 0
7991 | BARNAGEERAGH_110 | BARNAGEE1_11 | T101_50MVA | 110 | 10.7 | 0 | 1101 | 0
8088 | POPPINTREE_3 | POPPINTREE_4 | Cust 6.5MV | 10.7 | 10.7 | 0 | 1102 | 0
8189 | RINAWADE_110 | RINAWADE1_20 | T122_20MVA | 110 | 21.4 | 0 | 1103 | 0
8190 | RINAWADE_110 | RINAWADE1_20 | T121_20MVA | 110 | 21.4 | 0 | 1104 | 0
8194 | WHITEBANK_110 | WHITEBANK_11 | CUST_85MVA | 110 | 10.7 | 0 | 1105 | 0
8197 | POOLBEG_110H | PLBEG_TF1 | TF1_30MVA | 110 | 10.7 | 0 | 1106 | 0
8236 | DERRYIRON | DRIRN_G2_RP2 | T102_47MVA | 110 | 10.7 | 0 | 1107 | 0
8237 | DERRYIRON | DRIRN_G1_RP1 | T101_47MVA | 110 | 10.7 | 0 | 1108 | 0
8238 | RYEBROOK1 | RYBROOKA1_10 | T105_40MVA | 110 | 10.7 | 0 | 1109 | 0
8239 | RYEBROOK1 | RYEBROOKG_10 | T102_31_5MVA | 110 | 10.7 | 0 | 1110 | 0
8240 | RYEBROOK1 | RYEBROOKA_10 | T103_40MVA | 110 | 10.7 | 0 | 1111 | 0
8241 | RYEBROOK2 | RYBROOKG1_10 | T101_31_5MVA | 110 | 10.7 | 0 | 1112 | 0
8242 | RYEBROOK2 | RYBROOKB1_10 | T106_40MVA | 110 | 10.7 | 0 | 1113 | 0
8243 | RYEBROOK2 | RYEBROOKB_10 | T104_40MVA | 110 | 10.7 | 0 | 1114 | 0
8244 | NANGOR_110 | NANGOR_20 | T122_66_7MVA CUSTOMER | 110 | 21.4 | 0 | 1115 | 0
8245 | NANGOR1_110 | NANGOR_20 | T121_66_7MVA CUSTOMER | 110 | 21.4 | 0 | 1116 | 0
8272 | Harolds Cross_110 | HAROLDSX_10 | T101_20MVA | 110 | 10.7 | 0 | 1117 | 0
8560 | ARDFINNAN | ARDFINNAN2_10 | T424_10_MVA | 41.6 | 21.4 | 0 | 1118 | 0
8566 | MUINGS_38 | MUINGS_20 | 25MVA_2023 | 41.6 | 21.4 | 0 | 1119 | 0
8674 | BALLINCOLLIG | BALLINCO2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 1120 | 64
8675 | SWINFOR_38B | SWINFOR1_38S | Booster | 41.6 | 41.6 | 0 | 1121 | 0
8868 | BALLYRAGGET | BALLYRAGG_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 1122 | 64
8876 | BEAL NA Blath | BEAL N BL_20 | T421_10_MVA | 41.6 | 21.4 | 1 | 1123 | 0
8939 | SLANE_20 | SLANE_10 | T22_5_MVA | 21.4 | 10.7 | 0 | 1124 | 0
9065 | SPIDDAL | SPIDDAL_20 | T422_5_MVA | 41.6 | 21.4 | 0 | 1125 | 0
9068 | TIMOLEAGUE_T422 | TIMOLEAGE_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 1126 | 64
9071 | Loughona | Loughona_20 | T421_21MVA | 41.6 | 21.4 | 0 | 1127 | 0
9074 | SPIDDAL | SPIDDAL_38B | SPIDDAL_BOOSTER | 41.6 | 41.6 | 0 | 1128 | 0
9269 | HEADFORD | HEADFRD1_10 | T41_10 MVA | 41.6 | 10.7 | 0 | 1129 | 0
9270 | KANTURK | KANTURK1_10 | T41_10_MVA | 41.6 | 10.7 | 1 | 1130 | 60
9271 | KANTURK | KANTURK2_10 | T42_10_MVA | 41.6 | 10.7 | 1 | 1131 | 0
9272 | CLONAKILTY | CLONAKI1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1132 | 0
9273 | CLONAKILTY | CLONAKI2_10 | T42_15_MVA | 41.6 | 10.7 | 2 | 1133 | 44
9279 | Hartnetts Cross_38 | Hartnetts CrossT422_20 | T421_10MVA | 41.6 | 21.4 | 1 | 1134 | 64
9294 | KILYBEGS_38S | KILYBEGS_38B | BOOSTER_Reversable_20MVA | 41.6 | 41.6 | 0 | 1135 | 0
9302 | SKIBBEREEN | SKIBBERE2_10 | T42_10MVA | 41.6 | 10.7 | 2 | 1136 | 56
9303 | SKIBBEREEN | SKIBBERE1_10 | T41_10MVA | 41.6 | 10.7 | 0 | 1137 | 0
9338 | MOUNTGORRY | Mountgorry_20 | T423_15MVA | 41.6 | 21.4 | 1 | 1138 | 60
9370 | Donore Road_38 | Donore Road_10 | T41_15_MVA | 41.6 | 10.7 | 1 | 1139 | 44
9371 | Donore Road_38 | Donore Road_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 1140 | 0
9410 | Cloghboola_110 | Cloghboola_33 | T131_50MVA | 110 | 33 | 0 | 1141 | 0
9465 | SORNEHILL_T124 | SORNEHILL_T124 | T124_40MVA | 110 | 21.4 | 1 | 1142 | 64
10171 | BATTER LANE_38 | Batter_Lane_20 | T421_5MVA | 41.6 | 21.4 | 0 | 1143 | 0
10175 | BREIFNE | BREIFNE1_10 | CUST1_22MVA | 41.6 | 10.7 | 0 | 1144 | 0
10176 | BREIFNE | BREIFNE2_10 | CUST2_22MVA | 41.6 | 10.7 | 0 | 1145 | 0
10179 | DERRYNAGEEHA | DERRYNAGEEHA_33 | T431_30MVA | 41.6 | 33 | 0 | 1146 | 0
12041 | KILDARE | KILDARE1_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1147 | 64
12043 | Ballynoe | Ballynoe_20 | T422_15_MVA | 41.6 | 21.4 | 0 | 1148 | 0
12046 | TULLABRACK_38 | TULLABRACK_1_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 1149 | 0
12047 | TULLABRACK_38 | TULLABRACK_2_20 | T422_10_MVA | 41.6 | 21.4 | 0 | 1150 | 0
12051 | FOYNES2_10 | FOYNES1_20 | T21_5_MVA | 10.7 | 21.4 | 0 | 1151 | 0
12052 | DRUMBEAR | DRUMBEAR2_10 | T41_10_MVA | 41.6 | 10.7 | 0 | 1152 | 0
12053 | DRUMBEAR | DRUMBEAR1_10 | T42_10_MVA | 41.6 | 10.7 | 2 | 1153 | 48
12055 | BALLYGAR | Ballygar1_10 | T42_10_MVA | 41.6 | 10.7 | 0 | 1154 | 0
12056 | BALLYGAR | BALLYGAR2_10 | T41_10_MVA | 41.6 | 10.7 | 2 | 1155 | 44
12057 | TUAM NORTH | TUAM NORTH2_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1156 | 0
12058 | TUAM NORTH | TUAM NORTH1_10 | T42_15_MVA | 41.6 | 10.7 | 2 | 1157 | 44
12062 | GORESBRIDGE | GORESBDG1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1158 | 0
12063 | GORESBRIDGE | GORESBDG2_10 | T42_15_MVA | 41.6 | 10.7 | 2 | 1159 | 44
12064 | CURRALEIGH | CURRALEI2_20 | T421_10_MVA | 41.6 | 21.4 | 0 | 1160 | 0
12065 | CURRALEIGH | CURRALEI1_20 | T422_10_MVA | 41.6 | 21.4 | 2 | 1161 | 44
12066 | BALLYHAUNIS | BALLYHAU1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1162 | 0
12067 | BALLYHAUNIS | BALLYHAU2_10 | T42_15_MVA | 41.6 | 10.7 | 2 | 1163 | 44
12069 | Carrigtwohill | CARRIGTW1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1164 | 0
12070 | Carrigtwohill | CARRIGTW2_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 1165 | 64
12074 | MILFORD_NR_1 | MLFRD_NR1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1166 | 0
12075 | MILFORD_NR_2 | MLFRD_NR2_10 | T42_15_MVA | 41.6 | 10.7 | 2 | 1167 | 44
12076 | ENNISTYMON | ENNISTY1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1168 | 0
12077 | ENNISTYMON | ENNISTY2_10 | T42_15_MVA | 41.6 | 10.7 | 2 | 1169 | 44
12080 | DEERPARK | DEERPARK1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1170 | 0
12081 | DEERPARK | DEERPARK2_10 | T42_15_MVA | 41.6 | 10.7 | 2 | 1171 | 44
12082 | CASTLEISLAND | CASTLEISLAND1_10 | T42_15_MVA | 41.6 | 10.7 | 2 | 1172 | 44
12083 | CASTLEISLAND | CASTLEISLAND_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1173 | 0
12124 | Caroline Street_38 | caroline street_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1174 | 0
12125 | Caroline Street_38 | caroline street_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1175 | 44
12141 | New Kilmoney-Carrigaline Station_38 | New Kilmoney-Carrigaline Station_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1176 | 52
12142 | New Kilmoney-Carrigaline Station_38 | New Kilmoney-Carrigaline Station_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1177 | 0
12166 | CLOYNE | CLOYNE2_10 | T41_15_MVA | 41.6 | 10.7 | 1 | 1178 | 0
12167 | CLOYNE | CLOYNE1_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 1179 | 48
12175 | Baxter Station_38 | Baxter Station_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1180 | 0
12176 | Baxter Station_38 | Baxter Station_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1181 | 44
12201 | KNOCKNAGEE_MSD_38 | KNOCKNAGEE_MSD1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1182 | 0
12202 | KNOCKNAGEE_MSD_38 | KNOCKNAGEE_MSD2_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 1183 | 44
12215 | DELVIN | DELVIN2_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 1184 | 0
12216 | DELVIN | DELVIN1_10 | T41_15_MVA | 41.6 | 10.7 | 1 | 1185 | 52
12246 | Talbots Inch/Rosehill_38 | Talbots Inch/Rosehill_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1186 | 52
12247 | Talbots Inch/Rosehill_38 | Talbots Inch/Rosehill_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1187 | 0
12258 | Walterstown_38 | Walterstown_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 1188 | 44
12259 | Walterstown_38 | Walterstown_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 1189 | 0
12327 | BALLYGAR | Ballygar1_10 | T41_5_MVA | 41.6 | 10.7 | 0 | 1190 | 0
12414 | POOLBEG3_220 | POOLBEG_11 | T2007_90MVA | 220 | 10.7 | 0 | 1191 | 0
12420 | IRISHTWN_220 | RINGSEND_11 | T2003_90MVA | 220 | 10.7 | 0 | 1192 | 0
12422 | MIDARKLT2101 | ARKLOW 110 | T2101_63MVA | 110 | 110 | 0 | 1193 | 0
12425 | MNYPT P | MNYPT_G3_MP3 | T4003_330MVA | 400 | 17 | 0 | 1194 | 0
12427 | MNYPT D | MNYPT_G2_MP2 | T4002_330MVA | 400 | 17 | 0 | 1195 | 0
12429 | MNYPT W | MNYPT_G1_MP1 | T4001_330MVA | 400 | 17 | 0 | 1196 | 0
12430 | PORTAN 400 | PORTAN_260 | T4301_585_MV | 400 | 260 | 0 | 1197 | 0
12456 | GTISLAND_220 | GTLND_GI4 | T2004_560MVA | 220 | 21.4 | 0 | 1198 | 0
12459 | SHELLYBANKSC | SHBNK_G3_PBC | T2014_180MVA | 220 | 10.7 | 0 | 1199 | 0
12460 | SHELLYBANKSB | SHBNK_G5_PBC | T2016_200MVA | 220 | 15.75 | 0 | 1200 | 0
12461 | SHELLYBANKS | SHBNK_G4_PBC | T2015_180MVA | 220 | 10.7 | 0 | 1201 | 0
12482 | TARBERT 220 | TRBRT_G4_TB4 | T2004_280MVA | 220 | 10.7 | 0 | 1202 | 0
12483 | TARBERT 220 | TRBRT_G3_TB3 | T2003_280MVA | 220 | 10.7 | 0 | 1203 | 0
12515 | GLANAGOW_220 | GLANAGOW_20 | T2001 | 220 | 21.4 | 0 | 1204 | 0
12519 | CRKMINES_AIS | CRKMINES_PST | PST2201_350M | 220 | 220 | 0 | 1205 | 0
12524 | HUNTTWN P/P2 | HNTS_G3 | T2002_460MVA | 220 | 21.4 | 0 | 1206 | 0
12526 | IRISHTOWN | DUBLB_G1_DB1 | T2001_480MVA | 220 | 21.4 | 0 | 1207 | 0
12527 | AGHADA 220 | AGHA_G4_AT4 | T2014_125MVA | 220 | 10.7 | 0 | 1208 | 0
12528 | AGHADA 220 | AGHA_G3_AT2 | T2012_125MVA | 220 | 10.7 | 0 | 1209 | 0
12529 | AGHADA 220 | AGHA_G2_AT1 | T2011_125MVA | 220 | 10.7 | 0 | 1210 | 0
12531 | LONG PT 220 | LONG PT 20 | T2002_500MVA | 220 | 21.4 | 0 | 1211 | 0
12534 | ARKLOW 220 | MIDARKLT2101 | T2101_63MVA | 220 | 110 | 0 | 1212 | 0
12547 | COOLNAN_110 | COOLNAN_33 | T131_63_MVA | 110 | 33 | 0 | 1213 | 0
12549 | CASTLEDOCKRE | CASTLEDOCKRE | T121_70_MVA | 110 | 21.4 | 0 | 1214 | 0
12554 | GORMAN_110 | GORMAN_20 | T122_60MVA | 110 | 21.4 | 0 | 1215 | 0
12560 | SEAL ROCK 4 | SEAL ROCK G4 | T104_100MVA | 110 | 10.7 | 0 | 1216 | 0
12561 | TARBERT 110 | TRBRT_G2_TB2 | T102_70MVA | 110 | 10.7 | 0 | 1217 | 0
12562 | TARBERT 110 | TRBRT_G1_TB1 | T101_70MVA | 110 | 10.7 | 0 | 1218 | 0
12563 | MARINA_110 | MARNA_G7_MRT | T107_125MVA | 110 | 10.7 | 0 | 1219 | 0
12564 | CUSHALING | CSHLN_G1_ED1 | T101_146MVA | 110 | 10.7 | 0 | 1220 | 0
12565 | CUSHALING_2 | CSHLN_G3_ED5 | T105_85MVA | 110 | 10.7 | 0 | 1221 | 0
12566 | CUSHALING_2 | CSHLN_G2_ED3 | T103_85MVA | 110 | 10.7 | 0 | 1222 | 0
12866 | COLLINSTOWN | COLLINS2_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 1223 | 0
12867 | COLLINSTOWN | COLLINS1_10 | T41_15_MVA | 41.6 | 10.7 | 1 | 1224 | 44
12868 | BALLYBAY | BALLYBAY2_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 1225 | 0
12869 | BALLYBAY | BALLYBAY1_10 | T41_15_MVA | 41.6 | 10.7 | 1 | 1226 | 44
12872 | CASTLECOMER | CASTLEC1_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 1227 | 0
12873 | CASTLECOMER | CASTLEC2_10 | T41_15_MVA | 41.6 | 10.7 | 1 | 1228 | 44
12874 | TYCOR | TYCOR1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1229 | 0
12875 | TYCOR | TYCOR2_10 | T42_15_MVA | 41.6 | 10.7 | 2 | 1230 | 44
12876 | HOLYCROSS RD | HOLYCROS1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1231 | 0
12878 | HOLYCROSS RD | HOLYCROS2_10 | T42_15_MVA | 41.6 | 10.7 | 2 | 1232 | 60
12881 | DOCK ROAD | DOCK ROAD_5 | T41_15_MVA | 41.6 | 10.7 | 0 | 1233 | 0
12882 | DOCK ROAD | DOCK_ROAD_5 | T42_15_MVA | 41.6 | 10.7 | 2 | 1234 | 56
12884 | BALLYARD | BALLYARD1_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1235 | 0
12885 | BALLYARD | BALLYARD2_10 | T42_15_MVA | 41.6 | 10.7 | 2 | 1236 | 44
12887 | Dromthacker | Dromthacker_20 | T421_10_MVA | 41.6 | 21.4 | 1 | 1237 | 0
12888 | Dromthacker | Dromthacker_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 1238 | 56
12889 | URLINGFORD | Urlingford_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 1239 | 60
12895 | MORRISTOWN | MORRIST1_10 | T41_15_MVA | 41.6 | 10.7 | 1 | 1240 | 0
12896 | MORRISTOWN | MORRIST2_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 1241 | 44
12897 | Allenwood_38 | Allenwood_20 | T421_15_MVA | 41.6 | 21.4 | 0 | 1242 | 0
12898 | Allenwood_38 | Allenwood_20 | T422_15_MVA | 41.6 | 21.4 | 0 | 1243 | 0
12900 | Ballaghaderreen | BALLAGHA2_10 | T41_15_MVA | 41.6 | 10.7 | 0 | 1244 | 0
12901 | Ballaghaderreen | BALLAGHA1_10 | T42_15_MVA | 41.6 | 10.7 | 2 | 1245 | 44
12908 | Wilton_38 | Wilton_10 | T41_15_MVA | 41.6 | 10.7 | 1 | 1246 | 0
12910 | Wilton_38 | Wilton_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 1247 | 44
12925 | Ballymakenny_38 | Ballymakenny_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1248 | 0
12926 | Ballymakenny_38 | Ballymakenny_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1249 | 52
12957 | Bettystown_38 | Bettystown_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1250 | 0
12958 | Bettystown_38 | Bettystown_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1251 | 44
12967 | NEW Gurranebane_38 | New Gurranebane_20 | T421_10_MVA | 41.6 | 21.4 | 1 | 1252 | 0
12968 | NEW Gurranebane_38 | New Gurranebane_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 1253 | 44
12975 | New Tinahask_38 | New Tinahask_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1254 | 0
12976 | New Tinahask_38 | New Tinahask_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1255 | 44
13099 | Ballycummin_38 | Ballycummin_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1256 | 44
13100 | Ballycummin_38 | Ballycummin_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1257 | 0
13109 | East Athlone_38 | East Athlone_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1258 | 0
13111 | East Athlone_38 | East Athlone_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1259 | 44
13117 | East Galway_38 | East Galway_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1260 | 0
13118 | East Galway_38 | East Galway_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1261 | 44
13146 | BELMAYNE_38 | BELMAYNE_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1262 | 0
13147 | BELMAYNE_38 | BELMAYNE_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1263 | 44
13154 | Killygarry_38 | Killygarry_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1264 | 0
13155 | Killygarry_38 | Killygarry_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1265 | 44
13167 | RINAWADE_38 | RINAWADE_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1266 | 0
13168 | RINAWADE_38 | RINAWADE_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1267 | 44
13180 | BORRISOLEIGH | Borrisoleigh_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 1268 | 0
13181 | BORRISOLEIGH | Borrisoleigh_20 | T422_5_MVA | 41.6 | 21.4 | 1 | 1269 | 60
13220 | COURTLOUGH_38 | COURTLOUGH_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1270 | 0
13221 | COURTLOUGH_38 | COURTLOUGH_20 | T422_15_MVA | 41.6 | 21.4 | 1 | 1271 | 44
13295 | ERRIGAL | ERRIGAL_20 | T423_10_MVA | 41.6 | 21.4 | 1 | 1272 | 52
13298 | ROSCOMMON | Roscommon_20 | T421_5_MVA | 41.6 | 21.4 | 1 | 1273 | 52
13301 | BLESSINGTON | BLESSING1_20 | T421_15_MVA | 41.6 | 21.4 | 0 | 1274 | 0
13302 | BLESSINGTON | BLESSING2_20 | T422_15_MVA | 41.6 | 21.4 | 2 | 1275 | 56
13314 | BALLYHALE | Ballyhale_20 | T422_10_MVA | 41.6 | 21.4 | 1 | 1276 | 52
13325 | Carrigtwohill | CARRIGTW2_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 1277 | 0
13327 | HEADFORD | HEADFRD2_10 | T42_10_MVA_TEMP | 41.6 | 10.7 | 2 | 1278 | 60
13337 | BELMULLET | BELMULLET_2_20 | T422_15_MVA | 41.6 | 21.4 | 0 | 1279 | 0
13385 | LOUGHSH_20 | LOUGHSH1_10 | T21_3_MVA | 21.4 | 10.7 | 0 | 1280 | 0
13391 | CRANE_38 | CRANE2_20 | T421_15_MVA | 41.6 | 21.4 | 1 | 1281 | 64
13396 | KILMARTI_38B | KILMARTIN | Booster_16_MVA | 41.6 | 41.6 | 0 | 1282 | 0
2592 | ARKLOW 110 | ARKLOW_38 | T141_63MVA | 110 | 41.6 | 1 | 1283 | 0
2593 | ARKLOW 110 | ARKLOW_38 | T142_63MVA | 110 | 41.6 | 1 | 1284 | 64
2606 | BLACKROCK_110 | BLACKROCK_38 | T142_63MVA | 110 | 41.6 | 1 | 1285 | 64
2607 | BLACKROCK_110 | BLACKROCK_38 | T141_63MVA | 110 | 41.6 | 1 | 1286 | 0
2608 | BUTLERSTOWN_110 | BUTLERSTOWN__38 | T141_31_5MVA | 110 | 41.6 | 2 | 1287 | 0
2609 | BUTLERSTOWN_110 | BUTLERSTOWN__38 | T142_31_5MVA | 110 | 41.6 | 2 | 1288 | 12
2610 | CARLOW_110 | CARLOW_38 | T141_63MVA | 110 | 41.6 | 1 | 1289 | 0
2611 | CARLOW_110 | CARLOW_38 | T142_63MVA | 110 | 41.6 | 1 | 1290 | 64
2615 | CASTLEBAR_110 | CASTLEBAR_38 | T141_63_MVA | 110 | 41.6 | 1 | 1291 | 44
2617 | CARRICKMINS_GIS_A_110 | Carrickmines_38 | T141_63MVA | 110 | 41.6 | 0 | 1292 | 0
2618 | CARRICKMINS_GIS_B_110 | Carrickmines_38 | T142_63MVA | 110 | 41.6 | 1 | 1293 | 64
2619 | SOMERSET_110 | SOMERSET_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1294 | 64
2622 | CLOON_110 | CLOON_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1295 | 0
2623 | DALTON_T141 | DALTON1_38 | T141_63_MVA | 110 | 41.6 | 1 | 1296 | 64
2624 | DALTON_110 | DALTON_38 | T142_31_5_MV | 110 | 41.6 | 1 | 1297 | 64
2625 | CARRICK ON SHANNON_110 | CARICKONS_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1298 | 0
2626 | CARRICK ON SHANNON_110 | CARICKONS_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1299 | 64
2628 | COWCROSS_110 | COWCROSS_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1300 | 64
2630 | CRANE_110 | CRANE_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1301 | 64
2631 | CHARLEVILLE_T141 | CHARLEVL1_38 | T141_63_MVA | 110 | 41.6 | 1 | 1302 | 64
2632 | DUNDALK_110 | DUNDALK1_38 | T141_63MVA | 110 | 41.6 | 0 | 1303 | 0
2633 | DUNDALK_110 | DUNDALK2_38 | T142_63MVA | 110 | 41.6 | 1 | 1304 | 64
2634 | DUNGARVAN_110 | DUNGARVAN_38 | T141_31_5MVA | 110 | 41.6 | 2 | 1305 | 0
2635 | DUNGARVAN_110 | DUNGARVAN_38 | T142_31_5MVA | 110 | 41.6 | 2 | 1306 | 16
2638 | DRUMLINE_110 | DRUMLINE_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1307 | 0
2640 | DUNMANWAY_110 | DUNMANWAY_38 | T141_63_MVA | 110 | 41.6 | 1 | 1308 | 0
2641 | DUNMANWAY_110 | DUNMANWAY_38 | T142_63_MVA | 110 | 41.6 | 1 | 1309 | 64
2643 | DRYBRDGE_110 | DRYBRIDGE_38 | T141_63MVA | 110 | 41.6 | 1 | 1310 | 0
2644 | DRYBRDGE_110 | DRYBRIDGE_38 | T142_63MVA | 110 | 41.6 | 1 | 1311 | 64
2647 | ENNIS_110 | ENNIS_38 | T141_31_5MVA | 110 | 41.6 | 2 | 1312 | 0
2648 | ENNIS_110 | ENNIS_38 | T142_31_5MVA | 110 | 41.6 | 2 | 1313 | 8
2650 | Finglas_T143_110 | FINGLAS_T143 | T143_63MVA_Finglas Blue | 110 | 41.6 | 1 | 1314 | 64
2651 | Finglas_T144_110 | FINGLAS_T144 | T144_63MVA_Finglas Blue | 110 | 41.6 | 0 | 1315 | 0
2652 | Finglas_T141_110 | FINGLAS_T141 | T141_63MVA_Finglas Mauve | 110 | 41.6 | 0 | 1316 | 0
2653 | Finglas_T142_110 | FINGLAS_T142 | T142_63MVA_Finglas Orange | 110 | 41.6 | 1 | 1317 | 64
2654 | FRANCIS ST_A 110 | FRANCIS ST_T142 | T142_63MVA_Francis Street_Red | 110 | 41.6 | 1 | 1318 | 64
2655 | BLAKE_110 | BLAKE_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1319 | 64
2659 | GALWAY_110 | GALWAY_38 | T141_63MVA | 110 | 41.6 | 1 | 1320 | 0
2660 | GALWAY_110 | GALWAY_38 | T142_63MVA | 110 | 41.6 | 1 | 1321 | 64
2661 | BALLYLICKEY_110 | BALLYLICKEY | T142_63MVA | 110 | 41.6 | 1 | 1322 | 64
2662 | GRANGE_110 | GRANGE_38 | T141_63MVA | 110 | 41.6 | 1 | 1323 | 0
2663 | GRANGE_110 | GRANGE_38 | T142_63MVA | 110 | 41.6 | 1 | 1324 | 64
2667 | GRIFFINRATH_110_1 | GRIFFINRATH_38 | T141_63MVA | 110 | 41.6 | 0 | 1325 | 0
2668 | GRIFFINRATH_110_2 | GRIFFINRATH_38 | T142_63MVA | 110 | 41.6 | 1 | 1326 | 64
2669 | INCHICORE_B1_110 | INCHCR_T141 | T141_63MVA_Inchicore_Red | 110 | 41.6 | 0 | 1327 | 0
2670 | INCHICORE_B1_110 | INCHICORE_T143 | T143_63MVA_Inchicore_Green | 110 | 41.6 | 1 | 1328 | 64
2672 | KILBARRY_110 | KILBARRY_38 | T142_63MVA | 110 | 41.6 | 1 | 1329 | 64
2673 | KILBARRY_110 | KILBARRY_38 | T143_63MVA | 110 | 41.6 | 1 | 1330 | 0
2674 | MEATH_HIL110 | MEATH_HILL38 | T141_63_MVA | 110 | 41.6 | 1 | 1331 | 0
2675 | MEATH_HIL110 | MEATH_HILL38 | T142_63_MVA | 110 | 41.6 | 1 | 1332 | 64
2676 | Knockearagh_110 | Knockearagh_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1333 | 0
2677 | Knockearagh_110 | Knockearagh_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1334 | 64
2678 | KILKENNY_110 | KILKENNY_38 | T141_63MVA | 110 | 41.6 | 1 | 1335 | 0
2679 | KILKENNY_110 | KILKENNY_38 | T142_63MVA | 110 | 41.6 | 1 | 1336 | 64
2683 | GRANGE CASTLE_110 | GRANGECASTLE | T141_63MVA | 110 | 41.6 | 1 | 1337 | 64
2687 | LETTERKENY_110 | LETERKENY_38 | T141_63MVA | 110 | 41.6 | 1 | 1338 | 0
2688 | LETTERKENY_110 | LETERKENY_38 | T142_63MVA | 110 | 41.6 | 1 | 1339 | 64
2691 | LIMERICK_110 | LIMERICK_381 | T141_63MVA | 110 | 41.6 | 0 | 1340 | 0
2692 | LIMERICK_110 | LIMERICK_382 | T142_63MVA | 110 | 41.6 | 1 | 1341 | 64
2693 | LISDRUM_110 | LISDRUM_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1342 | 0
2694 | LISDRUM_110 | LISDRUM_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1343 | 64
2695 | MCDERMOT_110 | MCDRMOT_T141 | T141_63MVA_MCDERMOTMauve | 110 | 41.6 | 1 | 1344 | 64
2696 | MCDERMOT_110 | MCDRMOT_T142 | T142_63MVA _MCDERMOT Orange | 110 | 41.6 | 0 | 1345 | 0
2697 | MACROOM_110 | MACROOM_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1346 | 64
2700 | MIDLETON_110 | MIDLETON_38 | T141_31_5MVA | 110 | 41.6 | 2 | 1347 | 20
2701 | GLASMORE T142_110 | GLASMORE_38 | T142_63_MVA | 110 | 41.6 | 1 | 1348 | 64
2703 | BOGGERAGH_110 | BOGGERAGH_38 | T142_63MVA | 110 | 41.6 | 1 | 1349 | 64
2705 | MILLTOWN_B_110 | MILLTOWN_T142 | T142_63MVA_Milltown_Green | 110 | 41.6 | 0 | 1350 | 0
2706 | MALLOW_110 | MALLOW_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1351 | 0
2707 | MALLOW_110 | MALLOW_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1352 | 64
2709 | MOY_110 | MOY_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1353 | 0
2712 | MULLINGAR_110 | MULLINGAR_38 | T141_31_5MVA | 110 | 41.6 | 2 | 1354 | 0
2713 | MULLINGAR_110 | MULLINGAR_38 | T142_31_5MVA | 110 | 41.6 | 2 | 1355 | 20
2715 | KILTEEL_110 | KILTEEL_38 | T141_31_5MVA | 110 | 41.6 | 2 | 1356 | 0
2716 | KILTEEL_110 | KILTEEL_38 | T142_31_5MVA | 110 | 41.6 | 2 | 1357 | 20
2717 | NAVAN_110 | NAVAN_38 | T142_63MVA | 110 | 41.6 | 1 | 1358 | 64
2718 | NAVAN_110 | NAVAN_38 | T141_63MVA | 110 | 41.6 | 1 | 1359 | 0
2719 | GLASMORE T141_110 | GLASMORE_38 | T141_63_MVA | 110 | 41.6 | 0 | 1360 | 0
2720 | NEWBRIDGE_110 | NWBRDGE1_38S | T141_31_5MVA | 110 | 41.6 | 0 | 1361 | 0
2721 | NEWBRIDGE_110 | NWBRIDGE_38S | T142_31_5MVA | 110 | 41.6 | 1 | 1362 | 64
2730 | PORTLAOIS_110 | PORTLAOIS_38 | T141_63_MVA | 110 | 41.6 | 1 | 1363 | 0
2731 | PORTLAOIS_110 | PORTLAOIS_38 | T142_63_MVA | 110 | 41.6 | 1 | 1364 | 64
2732 | TONROE_110 | TONROE_38 | T142_31_5MVA | 110 | 41.6 | 2 | 1365 | 20
2733 | TIPPERARY_110 | TIPPERARY_1 | T141_31_5MVA | 110 | 41.6 | 1 | 1366 | 64
2734 | GLENLARA_110 | GLENLARA_38 | T142_63_MVA | 110 | 41.6 | 1 | 1367 | 64
2735 | GLENLARA_T141 | GLENLARA_38B | T141_63MVA | 110 | 41.6 | 1 | 1368 | 64
2736 | RICHMOND_110 | RICHMOND_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1369 | 0
2737 | RICHMOND_110 | RICHMOND_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1370 | 64
2741 | SHANKILL_110 | SHANKILL_38 | T141_63MVA | 110 | 41.6 | 1 | 1371 | 0
2742 | SHANKILL_110 | SHANKILL_38 | T142_63MVA | 110 | 41.6 | 1 | 1372 | 64
2745 | SLIGO_110 | SLIGO_38 | T141_63MVA | 110 | 41.6 | 1 | 1373 | 0
2746 | SLIGO_110 | SLIGO_38 | T142_63MVA | 110 | 41.6 | 1 | 1374 | 64
2749 | THURLES_110 | THURLES_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1375 | 64
2750 | THURLES_110 | THURLES_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1376 | 0
2751 | TRIEN_T143 | TRIEN3_38 | T143_63MVA | 110 | 41.6 | 1 | 1377 | 64
2752 | TRIEN_110 | TRIEN_38 | T141_31_5_MV | 110 | 41.6 | 2 | 1378 | 0
2753 | TRIEN_110 | TRIEN_38 | T142_31_5_MV | 110 | 41.6 | 2 | 1379 | 20
2760 | TRALEE_110 | TRALEE_38 | T141_63MVA | 110 | 41.6 | 1 | 1380 | 0
2761 | TRALEE_110 | TRALEE_38 | T142_63MVA | 110 | 41.6 | 1 | 1381 | 64
2762 | TULLABRACK_110 | TULLABRACK_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1382 | 64
2763 | WATERFORD_110 | WATERFORD_38 | T141_63MVA | 110 | 41.6 | 1 | 1383 | 0
2764 | WATERFORD_110 | WATERFORD_38 | T142_63MVA | 110 | 41.6 | 1 | 1384 | 64
2767 | WEXFORD_110 | WEXFORD_38 | T141_63MVA | 110 | 41.6 | 1 | 1385 | 0
2773 | ARDNACRUSHA_110 | ARDNA_38_2 | T142_63MVA | 110 | 41.6 | 1 | 1386 | 64
2774 | ARDNACRUSHA_110 | ARDNA_38_1 | T141_63MVA | 110 | 41.6 | 0 | 1387 | 0
2790 | LANESBORO_110 | LANESBORO_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1388 | 64
2792 | NENAGH_110 | NENAGH_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1389 | 64
2803 | RINGSEND_R_110 | RINGSEND_T144 | T144_63MVA_Ringsend_Brown | 110 | 41.6 | 1 | 1390 | 64
2804 | RINGSEND_B_110 | RINGSEND_T141 | T141_63MVA_Ringsend_Blue | 110 | 41.6 | 0 | 1391 | 0
2810 | DOON_110 | DOON_38 | T142_31_5_MV | 110 | 41.6 | 1 | 1392 | 64
2811 | DOON_110 | DOON_38 | T141_31_5_MV | 110 | 41.6 | 1 | 1393 | 0
2812 | STRATFORD_110 | STRATFORD | T141_31_5MVA | 110 | 41.6 | 1 | 1394 | 64
2813 | ATHLONE_110 | ATHLONE_38 | T141_63MVA | 110 | 41.6 | 1 | 1395 | 0
2814 | ATHLONE_110 | ATHLONE_38 | T142_63MVA | 110 | 41.6 | 1 | 1396 | 64
2821 | BARYMORE_110 | BARRYMORE_38 | T141_31_5MVA | 110 | 41.6 | 2 | 1397 | 12
2824 | FRANCIS ST_B_110 | FRANCIS ST_T141 | T141_63MVA_Francis Street_Brown | 110 | 41.6 | 0 | 1398 | 0
2830 | BARNHELY_A_110 | BARNAHEALY_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1399 | 0
2831 | BARNHELY_A_110 | BARNAHEALY_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1400 | 64
2832 | THORNSBERRY_110 | THORNSBER_38 | T141_63MVA | 110 | 41.6 | 1 | 1401 | 0
2845 | INCHICORE_A1 110 | INCHICORE_T144 | T144_63MVA_Inchicore_Orange | 110 | 41.6 | 0 | 1402 | 0
2846 | INCHICORE_A1 110 | INCHCR_T145 | T145_63MVA_Inchicore_Orange | 110 | 41.6 | 1 | 1403 | 64
2853 | BOOLTIAGH_T141 | BOOLTGH_38_1 | T141_63MVA | 110 | 41.6 | 1 | 1404 | 64
2854 | BOOLTIAGH_T143 | BOOLTGH_38_2 | T143_63_MVA | 110 | 41.6 | 1 | 1405 | 64
2862 | BINBANE_T143 | BINBANE_38b | T143_63MVA | 110 | 41.6 | 1 | 1406 | 64
2863 | BINBANE_110 | BINBANE_38a | T141_63MVA | 110 | 41.6 | 1 | 1407 | 0
2864 | BINBANE_110 | BINBANE_38a | T142_63MVA | 110 | 41.6 | 1 | 1408 | 64
2876 | MILLTOWN_A_110 | MILLTOWN_T141 | T141_63MVA_Milltown_Blue | 110 | 41.6 | 1 | 1409 | 64
2905 | LISHEEN_110 | LISHEEN_38 | T142_63MVA | 110 | 41.6 | 1 | 1410 | 64
2909 | COOKSTOWN_GIS_110 | COOKSTOWN_38 | T141_63MVA | 110 | 41.6 | 1 | 1411 | 0
2910 | COOKSTOWN_GIS_110 | COOKSTOWN_38 | T142_63MVA | 110 | 41.6 | 1 | 1412 | 64
2915 | SALTHILL_110 | SALTHILL1_38 | T141_63MVA | 110 | 41.6 | 1 | 1413 | 64
2920 | CAUTEEN_T142 | CAUTEEN_2 | T142_63MVA | 110 | 41.6 | 1 | 1414 | 64
2921 | CAUTEEN_T144 | CAUTEEN_4 | T144_63_MVA | 110 | 41.6 | 1 | 1415 | 64
2924 | CARROWBEG_110 | CARROWBEG | T142_31_5MVA | 110 | 41.6 | 1 | 1416 | 64
2973 | SCREEB_110 | SCREEB | T142_31_5MVA | 110 | 41.6 | 1 | 1417 | 64
2999 | OUGHTRAGH_110 | OUGHTRAGH_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1418 | 64
3020 | DALLOW_110 | DALLOW_38 | T141_31_5_MV | 110 | 41.6 | 1 | 1419 | 64
3026 | TRILLICK_T142 | TRILLICK_38_T142 | T142_31_5MVA | 110 | 41.6 | 1 | 1420 | 64
3027 | TRILLICK_110 | TRILLICK_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1421 | 64
3029 | GARVAGH_110 | GARVAGH_38 | T141_63_MVA | 110 | 41.6 | 1 | 1422 | 64
3039 | REAMORE_T141 | REAMORE1_38 | T141_63MVA | 110 | 41.6 | 1 | 1423 | 64
3040 | REAMORE_T142 | REAMORE_38 | T142_63MVA | 110 | 41.6 | 1 | 1424 | 64
3100 | BALLYDINE_110 | BALLYDINE_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1425 | 64
3127 | ARDNAGAPPARY_110 | ARDNAGAPY_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1426 | 64
3141 | CORDAL_110 | CORDAL_33 | T132_120_MVA | 110 | 33 | 0 | 1427 | 0
3142 | CORDAL_110 | CORDAL_38 | T141_63_MVA | 110 | 41.6 | 1 | 1428 | 64
3152 | COOMATAGGART_110 | COOMATAGG_33 | T132_150_MVA | 110 | 33 | 0 | 1429 | 0
3153 | COOMATAGGART_110 | COOMATAGG_38 | T141_63_MVA | 110 | 41.6 | 1 | 1430 | 64
3160 | GLENREE_110 | GLENREE_38 | T142_63MVA | 110 | 41.6 | 1 | 1431 | 64
3162 | BELLACORRICK_110 | BELLACORI_38 | T141_63_MVA | 110 | 41.6 | 1 | 1432 | 64
3631 | CAHIR_110 | CAHIR_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1433 | 0
3632 | CAHIR_110 | CAHIR_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1434 | 64
3633 | CASTLEBAR_110 | CASTLBAR_38S | T142_31_5MVA | 110 | 41.6 | 1 | 1435 | 20
3638 | CLOON_110 | CLOON_38 | T142_31.5_MVA | 110 | 41.6 | 1 | 1436 | 64
3650 | DRUMLINE_110 | DRUMLINE_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1437 | 64
3655 | FASSAROE_W_110 | FASSAROE_38 | T141_63MVA | 110 | 41.6 | 0 | 1438 | 0
3656 | FASSAROE_E_110 | FASSAROE_38 | T142_63MVA | 110 | 41.6 | 1 | 1439 | 64
3662 | IKERRIN_110 | IKERRIN_38 | T141_31_5MVA | 110 | 41.6 | 2 | 1440 | 20
3680 | RATHKEALE_110 | RATHKEALE_38 | T141_30MVA | 110 | 41.6 | 1 | 1441 | 0
3681 | RATHKEALE_110 | RATHKEALE_38 | T142_30MVA | 110 | 41.6 | 1 | 1442 | 64
3683 | TRABEG_110 | TRABEG_38 | T141_31_5MVA | 110 | 41.6 | 2 | 1443 | 0
3684 | TRABEG_110 | TRABEG_38 | T142_31_5MVA | 110 | 41.6 | 2 | 1444 | 20
3687 | CATHALEENS FALL_110 | CATHFALLS_38 | T141_31_5MVA | 110 | 41.6 | 2 | 1445 | 12
3693 | BANDON_110 | BANDON_38 | T141_31_5MVA | 110 | 41.6 | 1 | 1446 | 0
3694 | THORNSBERRY_110 | THORNSBER_38 | T142_63MVA | 110 | 41.6 | 1 | 1447 | 64
3715 | Great Island_110 | GTISLND_38A2 | T141_63MVA | 110 | 41.6 | 2 | 1448 | 16
3724 | GORTAWEE_110 | GORTAWEE_38 | T142_63MVA | 110 | 41.6 | 1 | 1449 | 64
3931 | CHERRYWOOD_110 | CHERRYWD_38 | T141_63MVA | 110 | 41.6 | 1 | 1450 | 0
3932 | CHERRYWOOD_110 | CHERRYWD_38 | T142_63MVA | 110 | 41.6 | 1 | 1451 | 64
3975 | TAURBEG_WF | TAURBEG_20 | T1_30_MVA | 41.6 | 21.4 | 0 | 1452 | 0
4061 | RIVERS | RIVERS_10 | T41_Customer_30_MVA | 41.6 | 10.7 | 0 | 1453 | 0
4793 | Great Island_110 | GTISLND_38A1 | T142_63MVA | 110 | 41.6 | 0 | 1454 | 0
4795 | MOY_110 | MOY_38 | T142_31.5MVA | 110 | 41.6 | 1 | 1455 | 64
4797 | GLENREE_110 | GLENREE1_20 | T121_20MVA | 110 | 21.4 | 1 | 1456 | 64
4798 | BELLACORRICK_110 | BELLACORI_20 | T122_10MVA | 110 | 21.4 | 2 | 1457 | 20
4800 | RIVERS | RIVERS1_10 | T42_Customer_30_MVA | 41.6 | 10.7 | 0 | 1458 | 0
4801 | CHARLEVILLE__110 | CHARLEVILLE_38 | T142_31.5_MVA | 110 | 41.6 | 1 | 1459 | 64
4807 | WEXFORD_110 | WEXFORD_38 | T142_63MVA | 110 | 41.6 | 1 | 1460 | 64
4808 | WEXFORD_110 | WEXFORD2_20 | T122_20MVA | 110 | 21.4 | 1 | 1461 | 64
4810 | WEXFORD_110 | WEXFORD1_20 | T121_20MVA | 110 | 21.4 | 0 | 1462 | 0
4811 | CRANE_110 | CRANE_20 | T122_20MVA | 110 | 21.4 | 1 | 1463 | 64
4812 | GARVAGH_110 | GARVAGH_G_20 | T121_63_MVA | 110 | 21.4 | 0 | 1464 | 0
4819 | Tawnaghmore_A_110 | Tawnaghmore_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1465 | 64
4829 | BARNHELY_A_110 | BARNAHELY1_20 | T121_20MVA | 110 | 21.4 | 0 | 1466 | 0
4830 | BARNHELY_A_110 | BARNAHELY2_20 | T122_20MVA | 110 | 21.4 | 1 | 1467 | 64
4832 | BARNHELY_B_110 | BARNAHELY_20 | T124_20MVA | 110 | 21.4 | 1 | 1468 | 64
4835 | BANDON_110 | BANDON_38 | T142_31_5MVA | 110 | 41.6 | 1 | 1469 | 64
4836 | CAUTEEN_T141 | CAUTEEN_1 | T141_63MVA | 110 | 41.6 | 1 | 1470 | 64
4883 | KILTEEL_110 | KILTEEL_33 | T131_70_MVA | 110 | 33 | 0 | 1471 | 0
4888 | GALWAY_110 | GALWAY1_10 | T103 _20MVA | 110 | 10.7 | 0 | 1472 | 0
4889 | GALWAY_110 | GALWAY2_10 | T102_20MVA | 110 | 10.7 | 1 | 1473 | 64
5030 | BANDON_110 | BANDON2_10 | T101_20MVA | 110 | 10.7 | 0 | 1474 | 0
5208 | ARKLOW 110 | ARKLOW_10_1 | T101_20MVA | 110 | 10.7 | 0 | 1475 | 0
5209 | ARKLOW 110 | ARKLOW_10_2 | T102_20MVA | 110 | 10.7 | 1 | 1476 | 64
5305 | ENNIS_110 | ENNIS1_10 | T101_20MVA | 110 | 10.7 | 0 | 1477 | 0
5306 | ENNIS_110 | ENNIS_10 | T102_20MVA | 110 | 10.7 | 1 | 1478 | 64
5383 | GRANGE CASTLE_110 | GRANGECSL_10 | T121_20MVA | 110 | 21.4 | 0 | 1479 | 0
5384 | GRANGE CASTLE_110 | GRANGCSL2_10 | T122_20MVA | 110 | 21.4 | 1 | 1480 | 64
5426 | KILBARRY_110 | KILBARRY3_10 | T101_20MVA | 110 | 10.7 | 0 | 1481 | 0
5556 | MIDLETON_110 | MIDLTON_10_1 | T101_20MVA | 110 | 10.7 | 0 | 1482 | 0
5557 | MIDLETON_110 | MIDLTON_10_2 | T102_20MVA | 110 | 10.7 | 1 | 1483 | 64
5819 | BALLYRAGGET_110 | BALLYRAGGET | T141_31.5 MVA | 110 | 41.6 | 2 | 1484 | 8
5832 | COWCROSS_110 | COWCROSS2_10 | T102_20_MVA | 110 | 10.7 | 0 | 1485 | 0
7956 | BALLYMAKAILY | BALLYM_2 | BALLYM_GT1_135MVA | 110 | 15 | 0 | 1486 | 0
7957 | BALLYMAKAILY | BALLYM_1 | BALLYM_GT1_135MVA | 110 | 15 | 0 | 1487 | 0
7960 | ADAMSTOWN | ADAMSTN_2 | T122_20MVA | 110 | 21.4 | 1 | 1488 | 64
7961 | ADAMSTOWN | ADAMSTN_1 | T121_20MVA | 110 | 21.4 | 0 | 1489 | 0
7986 | CLUTTERLAND_110 | CLUTTERL1_20 | T121_63MVA | 110 | 21.4 | 0 | 1490 | 0
7989 | GALLANSTOWN_110 | GALANSTWN_33 | T131_160MVA | 110 | 33 | 0 | 1491 | 0
7993 | CLUTTERLAND_110 | CLUTTERL2_20 | T122_63MVA | 110 | 21.4 | 0 | 1492 | 0
8035 | North Quays | North Quays3 | T103_20MVA_Customer | 110 | 10.7 | 0 | 1493 | 0
8037 | BARNAKYLE | BARNAKYLE2 | T122_110MVA | 110 | 21.4 | 0 | 1494 | 0
8038 | BARNAKYLE | BARNAKYLE1 | T121_110MVA | 110 | 21.4 | 0 | 1495 | 0
8046 | YELLOWMEADOWS_A1 | YELLOWMDOW_1 | YELLOWMEADOW T121 | 110 | 21.4 | 0 | 1496 | 0
8047 | YELLOWMEADOWS_A2 | YELLOWMDOW_2 | YELLOWMEADOW T122 | 110 | 21.4 | 0 | 1497 | 0
8061 | COOLDERRIG 2 | COOLD2_20 | T122_50MVA | 110 | 21.4 | 0 | 1498 | 0
8062 | COOLDERRIG 1 | COOLD1-20 | T121_50MVA | 110 | 21.4 | 0 | 1499 | 0
8066 | KYLEMOR BESS | KYLEMOR_T131 | T131 IPP | 110 | 33 | 0 | 1500 | 0
8070 | CASTLEBAGOT_220 | CASTLEBAGOT_110 | T2101_250MVA | 220 | 110 | 0 | 1501 | 0
8071 | CASTLEBAGOT_220 | CASTLEBAGOT_110 | T2102_250MVA | 220 | 110 | 0 | 1502 | 0
8072 | CASTLEBAGOT_220 | CASTLEBAGOT_110 | T2103_250MVA | 220 | 110 | 0 | 1503 | 0
8073 | CASTLEBAGOT_220 | CASTLEBAGOT_110 | T2104_250MVA | 220 | 110 | 0 | 1504 | 0
8076 | CLOGHRAN_110 | CLOGHRAN3_20 | T123_35MVA | 110 | 21.4 | 0 | 1505 | 0
8078 | CLOGHRAN_110 | CLOGHRAN6_20 | T126_50MVA | 110 | 21.4 | 0 | 1506 | 0
8079 | CLOGHRAN_110 | CLOGHRAN4_20 | T124_50MVA | 110 | 21.4 | 0 | 1507 | 0
8125 | AIRTON110_A2 | AIRTON2_20 | T122_63_MVA | 110 | 21.4 | 0 | 1508 | 0
8126 | AIRTON110_A1 | AIRTON1_20 | T121_63_MVA | 110 | 21.4 | 0 | 1509 | 0
8129 | AIRTON110_A3 | AIRTON3_20 | T123_63MVA | 110 | 21.4 | 0 | 1510 | 0
8132 | CORKAGH | CORKAGH2 | T121_80MVA | 110 | 21.4 | 0 | 1511 | 0
8133 | MAYNTH_B_220 | MAYNTH_B_110 | T2104_250MVA | 220 | 110 | 0 | 1512 | 0
8134 | MAYNTH_B_220 | MAYNTH_B_110 | T2103_125MVA | 220 | 110 | 0 | 1513 | 0
8135 | MAYNTH_G_220 | MAYNTH_G_110 | T2101_125MVA | 220 | 110 | 0 | 1514 | 0
8136 | MAYNTH_G_220 | MAYNTH_G_110 | T2102_250MVA | 220 | 110 | 0 | 1515 | 0
8137 | FINGLAS | Finglas_T144_110 | T2101_250MVA | 220 | 110 | 0 | 1516 | 0
8138 | FINGLAS | FINGLAS_AISB | T2103_250MVA | 220 | 110 | 0 | 1517 | 0
8139 | CORDUFF1_220 | CORDUFF1_110 | T2101_250MVA | 220 | 110 | 0 | 1518 | 0
8140 | CORDUFF2_220 | CORDUFF2_110 | T2102_250MVA | 220 | 110 | 0 | 1519 | 0
8159 | CHERRYWOOD_110 | CHERRYWOOD2_10 | T102_20MVA | 110 | 10.7 | 1 | 1520 | 64
8160 | CHERRYWOOD_110 | CHERRYWOOD1_10 | T101_20MVA | 110 | 10.7 | 0 | 1521 | 0
8165 | POOLBEG A | POOLBEG_110R | TF3_250MVA | 220 | 110 | 0 | 1522 | 0
8166 | POOLBEG B | POOLBEG_110B | TF4_250MVA | 220 | 110 | 0 | 1523 | 0
8167 | INCHICOR_220 | INCHICORE_A1 110 | T2106_250MVA | 220 | 110 | 0 | 1524 | 0
8168 | INCHICOR_220 | INCHICORE_A1 110 | T2101_250MVA | 220 | 110 | 0 | 1525 | 0
8169 | INCHICOR_220 | INCHICORE_B1_110 | T2104_250MVA | 220 | 110 | 0 | 1526 | 0
8170 | INCHICOR_220 | INCHICORE_B1_110 | T2102_250MVA | 220 | 110 | 0 | 1527 | 0
8171 | FINGLAS | FINGLAS_AISA | T2104_250MVA | 220 | 110 | 0 | 1528 | 0
8172 | CRKMINES_GIS | CARRICKMINS_GIS_B_110 | T2104_250MVA | 220 | 110 | 0 | 1529 | 0
8173 | CRKMINES_GIS | CARRICKMINS_GIS_B_110 | T2103_250MVA | 220 | 110 | 0 | 1530 | 0
8174 | CRKMINES_GIS | CRKMNS_110_4 | T2101_250MVA | 220 | 110 | 0 | 1531 | 0
8175 | CRKMINES_AIS | CRKMNS_110_2 | T2102_250MVA | 220 | 110 | 0 | 1532 | 0
8176 | CORKAGH | CORKAGH3 | T123_80MVA | 110 | 21.4 | 0 | 1533 | 0
8177 | CORKAGH | CORKAGH1 | T121_80MVA | 110 | 21.4 | 0 | 1534 | 0
8178 | FORTUNESTOWN | FORTUNESTOWN2_10 | T102_20MVA | 110 | 10.7 | 1 | 1535 | 64
8179 | FORTUNESTOWN | FORTUNESTOWN1_10 | T101_20MVA | 110 | 10.7 | 0 | 1536 | 0
8180 | STEPHENSTOWN_110 | STEPHENS2_10 | T102_20MVA | 110 | 10.7 | 1 | 1537 | 64
8181 | STEPHENSTOWN_110 | STEPHENS_10 | T101_20MVA | 110 | 10.7 | 0 | 1538 | 0
8182 | CLOGHRAN_110 | CLOGHRAN2_20 | T122_35MVA | 110 | 21.4 | 0 | 1539 | 0
8183 | CLOGHRAN_110 | CLOGHRAN1_20 | T121_28MVA | 110 | 21.4 | 0 | 1540 | 0
8184 | BANCROFT | BANCROFT2_20 | T122_38MVA | 110 | 21.4 | 0 | 1541 | 0
8185 | BANCROFT | BANCROFT1_20 | T121_38MVA | 110 | 21.4 | 0 | 1542 | 0
8186 | NEWBURY | NEWBURY3_20 | T124_38MVA | 110 | 21.4 | 0 | 1543 | 0
8187 | NEWBURY | NEWBURY2_20 | T122_25MVA | 110 | 21.4 | 0 | 1544 | 0
8188 | NEWBURY | NEWBURY1_20 | T121_38MVA | 110 | 21.4 | 0 | 1545 | 0
8191 | TRINITY | TRINITY2_10 | T102_20MVA | 110 | 10.7 | 1 | 1546 | 64
8192 | TRINITY | TRINITY_10 | T101_20MVA | 110 | 10.7 | 0 | 1547 | 0
8193 | WHITEBANK_110 | WHITEBANK2_11 | CUST_12_5MVA | 110 | 10.7 | 0 | 1548 | 0
8195 | Wolfe Tone Street | WTS_10_2 | T102_20MVA | 110 | 10.7 | 1 | 1549 | 64
8196 | Wolfe Tone Street | WTS_10_1 | T101_20MVA | 110 | 10.7 | 0 | 1550 | 0
8198 | CITYWEST_110 | CITYWEST_2 | T102_20MVA | 110 | 10.7 | 1 | 1551 | 64
8199 | CITYWEST_110 | CITYWEST_1 | T101_20MVA | 110 | 10.7 | 0 | 1552 | 0
8200 | MACETOWN_110 | MACETOWN2_10 | T102_20MVA | 110 | 10.7 | 1 | 1553 | 64
8201 | MACETOWN_110 | MACETOWN_10 | T101_20MVA | 110 | 10.7 | 0 | 1554 | 0
8202 | PELLETSTOWN | PELLETSTN_2 | T102_20MVA | 110 | 10.7 | 1 | 1555 | 64
8203 | PELLETSTOWN | PELLETSTN_1 | T101_20MVA | 110 | 10.7 | 0 | 1556 | 0
8204 | CABRA_110 | CABRA2_10 | T102_20MVA | 110 | 10.7 | 1 | 1557 | 64
8205 | Heuston Square | Heuston Square_2 | T102_20MVA | 110 | 10.7 | 1 | 1558 | 64
8206 | Heuston Square | Heuston Square_1 | T101_20MVA | 110 | 10.7 | 0 | 1559 | 0
8207 | COOKSTOWN_GIS | COOKSTOWN2_10 | T102_20MVA | 110 | 10.7 | 1 | 1560 | 64
8208 | COOKSTOWN_GIS | COOKSTOWN1_10 | T101_20MVA | 110 | 10.7 | 0 | 1561 | 0
8211 | KILMAHUD | KILMAHUD_10 | T103_50MVA | 110 | 10.7 | 0 | 1562 | 0
8212 | KILMAHUD | KILMAHUD_2 | T102_50MVA | 110 | 10.7 | 0 | 1563 | 0
8213 | KILMAHUD | KILMAHUD_1 | T101_50MVA | 110 | 10.7 | 0 | 1564 | 0
8214 | DARDISTOWN | DARDISTN_2 | T102_31_5MVA | 110 | 10.7 | 0 | 1565 | 0
8215 | DARDISTOWN | DARDISTN_1 | T101_31_5MVA | 110 | 10.7 | 0 | 1566 | 0
8216 | POPPINTREE | POPPINTREE_2 | T102_20MVA | 110 | 10.7 | 1 | 1567 | 64
8217 | POPPINTREE | POPPINTREE_1 | T101_20MVA | 110 | 10.7 | 0 | 1568 | 0
8218 | BARODA_110 | BARODA2_10 | T102_31_5MVA | 110 | 10.7 | 0 | 1569 | 0
8219 | BARODA_110 | BARODA1_10 | T101_31_5MVA | 110 | 10.7 | 0 | 1570 | 0
8220 | Central Park | CENTRALPK2 | T102_20MVA | 110 | 10.7 | 1 | 1571 | 64
8221 | Central Park | CENTRALPK1 | T101_20MVA | 110 | 10.7 | 0 | 1572 | 0
8223 | MILTWN_3_110 | Milltown (dr)_4_10 | T101_20MVA | 110 | 10.7 | 0 | 1573 | 0
8224 | BALTRASNA | BALTRASNA_2 | T122_20MVA | 110 | 21.4 | 1 | 1574 | 64
8225 | BALTRASNA | BALTRASNA_1 | T121_20MVA | 110 | 21.4 | 0 | 1575 | 0
8226 | Pottery Road | POTTERYRD_2 | T102_20MVA | 110 | 10.7 | 1 | 1576 | 64
8227 | Pottery Road | POTTERYRD_1 | T101_20MVA | 110 | 10.7 | 0 | 1577 | 0
8228 | North Quays | North Quays2_10 | T102_20MVA | 110 | 10.7 | 1 | 1578 | 64
8229 | North Quays | North Quays_10 | T101_20MVA | 110 | 10.7 | 0 | 1579 | 0
8230 | Misery Hill | Misery Hill2_10 | T102_20MVA | 110 | 10.7 | 1 | 1580 | 64
8231 | Misery Hill | Misery Hill_10 | T101_20MVA | 110 | 10.7 | 0 | 1581 | 0
8232 | TANEY | TANEY2_10 | T102_20MVA | 110 | 10.7 | 1 | 1582 | 64
8233 | TANEY | TANEY1_10 | T101_20MVA | 110 | 10.7 | 0 | 1583 | 0
8247 | ARTANE | ARTANE2_10 | T102_20MVA | 110 | 10.7 | 1 | 1584 | 64
8248 | ARTANE | ARTANE1_10 | T101_20MVA | 110 | 10.7 | 0 | 1585 | 0
8251 | RINGSEND_B_110 | RINGSEND3_10 | T102_20MVA | 110 | 10.7 | 1 | 1586 | 64
8252 | RINGSEND_R_110 | RINGSE2_10 | T101_20MVA | 110 | 10.7 | 0 | 1587 | 0
8253 | MONREAD | MONREAD_1 | T101_20MVA | 110 | 10.7 | 0 | 1588 | 0
8254 | MONREAD | MONREAD_10 | T102_20MVA | 110 | 10.7 | 1 | 1589 | 64
8255 | College Park | COLLEGE_PARK3 | T103_20MVA | 110 | 10.7 | 1 | 1590 | 64
8256 | College Park | COLLEGE_PARK2 | T122_20MVA | 110 | 21.4 | 1 | 1591 | 64
8257 | College Park | COLLEGE_PARK1 | T121_20MVA | 110 | 21.4 | 0 | 1592 | 0
8262 | MILLTOWN_B_110 | Milltown (dr)_5_10 | T102_20MVA | 110 | 10.7 | 1 | 1593 | 64
8269 | GRANGECASTLE_2 | GRANGCSL4_20 | T124_20MVA | 110 | 21.4 | 1 | 1594 | 64
8273 | Harolds Cross_110 | HAROLDSX2_10 | T102_20MVA | 110 | 10.7 | 1 | 1595 | 64
8276 | KILMORE | KILMORE3_10 | T102_20MVA | 110 | 10.7 | 0 | 1596 | 0
8277 | KILMORE | KILMORE2_10 | T101_20MVA | 110 | 10.7 | 1 | 1597 | 64
8278 | KILMORE | KILMORE_10 | T103_20MVA | 110 | 10.7 | 0 | 1598 | 0
8286 | CABRA_110 | CABRA3_10 | T101_20MVA | 110 | 10.7 | 0 | 1599 | 0
8432 | FINGLAS | Finglas_T144_110 | FINGLAS_T2106 | 220 | 110 | 0 | 1600 | 0
8857 | TRABEG_110 | TRABEG2_10 | T102_20MVA | 110 | 10.7 | 1 | 1601 | 64
8858 | TRABEG_110 | TRABEG_10 | T101_20MVA | 110 | 10.7 | 0 | 1602 | 0
8943 | SNUGBOROUGH_110 | SNUGBOR_10_1 | T102_25_MVA | 110 | 10.7 | 0 | 1603 | 0
8945 | SNUGBOROUGH_110 | SNUGBOR_10_2 | T104_25_MVA | 110 | 10.7 | 0 | 1604 | 0
8948 | SNUGBOROUGH_110 | SNUGBOR_33_1 | T131_44_MVA | 110 | 33 | 0 | 1605 | 0
8950 | SNUGBOROUGH_110 | SNUGBOR_33_2 | T133_44_MVA | 110 | 33 | 0 | 1606 | 0
9046 | BANOGE_110 | BANOGE_20_1 | T121_20MVA | 110 | 21.4 | 0 | 1607 | 0
9048 | BANOGE_110 | BANOGE_20_2 | T122_20MVA | 110 | 21.4 | 1 | 1608 | 64
9064 | GRANGE CASTLE_110 | GRANGECASTLE | T142_63MVA | 110 | 41.6 | 1 | 1609 | 0
9078 | ATHY_110 | ATHY_X101 | T101_20MVA | 110 | 10.7 | 2 | 1610 | 12
9080 | ATHY_110 | ATHY_X102 | T102_20MVA | 110 | 10.7 | 0 | 1611 | 0
9099 | BALLYBEG_110 | BALLYBEG2_10 | T102_20MVA | 110 | 10.7 | 0 | 1612 | 0
9100 | BALLYBEG_110 | BALLYBEG1_10 | T101_20MVA | 110 | 10.7 | 1 | 1613 | 64
9125 | Castleview_110 | Castleview1_10 | T101_31.5_MVA | 110 | 10.7 | 1 | 1614 | 64
9126 | Castleview_110 | Castleview2_10 | T102_31.5_MVA | 110 | 10.7 | 0 | 1615 | 0
9128 | COOLROE_110 | COOLROE2_20 | T122_20_MVA | 110 | 21.4 | 0 | 1616 | 0
9129 | COOLROE_110 | COOLROE1_20 | T121_20_MVA | 110 | 21.4 | 1 | 1617 | 64
9141 | CORDUFF2_110 | CORDUF2_20 | T122_31.5_MVA | 110 | 21.4 | 0 | 1618 | 0
9142 | CORDUFF1_110 | CORDUFF_20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1619 | 64
9153 | DUNFIRTH_110 | DUNFIRTH_20 | T122_20MVA | 110 | 21.4 | 1 | 1620 | 8
9168 | KILLOTERAN_110 | KILLOTERAN1_10 | T101_20_MVA | 110 | 10.7 | 1 | 1621 | 64
9169 | KILLOTERAN_110 | KILLOTERAN2_10 | T102_20_MVA | 110 | 10.7 | 0 | 1622 | 0
9171 | Kilpaddoge_110 | Kilpaddoge_20 | T122_20_MVA | 110 | 21.4 | 1 | 1623 | 64
9184 | MARINA_110 | MARINA2_10 | T106_20_MVA | 110 | 10.7 | 0 | 1624 | 0
9185 | MARINA_110 | MARINA1_10 | T105_20_MVA | 110 | 10.7 | 2 | 1625 | 4
9208 | Mullagharlin_110 | Mullagharlin_20_2 | T122_31.5_MVA | 110 | 21.4 | 0 | 1626 | 0
9209 | Mullagharlin_110 | Mullagharlin_20_1 | T121_31.5_MVA | 110 | 21.4 | 1 | 1627 | 64
9211 | MULLINGAR_110 | MULLINGAR_1 | T101_20MVA | 110 | 10.7 | 1 | 1628 | 64
9212 | MULLINGAR_110 | MULLINGAR_2 | T102_20MVA | 110 | 10.7 | 0 | 1629 | 0
9220 | SALTHILL_110 | SALTHILL_1 | T101_31.5_MVA | 110 | 10.7 | 1 | 1630 | 64
9221 | SALTHILL_110 | SALTHILL_2 | T102_31.5_MVA | 110 | 10.7 | 0 | 1631 | 0
9234 | SINGLAND_110 | SINGLAND_2 | T102_20_MVA | 110 | 10.7 | 0 | 1632 | 0
9235 | SINGLAND_110 | SINGLAND_1 | T101_20_MVA | 110 | 10.7 | 1 | 1633 | 64
9281 | Hartnetts Cross | Hartnetts Cross T121_20 | T121_20MVA | 110 | 21.4 | 1 | 1634 | 64
9296 | TRABEG_110 | TRABEG_38 | T141_63_MVA | 110 | 41.6 | 2 | 1635 | 0
9297 | TRABEG_110 | TRABEG_38 | T142_63_MVA | 110 | 41.6 | 2 | 1636 | 44
9313 | Bracklone_110 | Bracklone1_20 | T121_20MVA | 110 | 21.4 | 0 | 1637 | 0
9314 | Bracklone_110 | Bracklone3_20 | T123_20MVA | 110 | 21.4 | 1 | 1638 | 56
9325 | Donore Road_110 | Donore Road_38 | T141_63_MVA | 110 | 41.6 | 1 | 1639 | 44
9326 | Donore Road_110 | Donore Road_38 | T142_63_MVA | 110 | 41.6 | 1 | 1640 | 0
9344 | BARODA_110 | Baroda_10 | T103_20MVA | 110 | 10.7 | 1 | 1641 | 44
9345 | BARODA_110 | Baroda_10 | T104_20MVA | 110 | 10.7 | 1 | 1642 | 0
9362 | Batter Lane_110 | Batter Lane_20 | T101_31.5_MVA | 110 | 21.4 | 1 | 1643 | 56
9363 | Batter Lane_110 | Batter Lane_20 | T102_31.5_MVA | 110 | 21.4 | 1 | 1644 | 0
9400 | LISHEEN_110 | Lisheen_33 | T131_40_MVA | 110 | 33 | 0 | 1645 | 0
9408 | Cloghboola_110 | Cloghboola_20 | T122_63MVA | 110 | 21.4 | 1 | 1646 | 64
9415 | Corderry_T121 | CORDERRY_2 | T121_20 MVA | 110 | 21.4 | 1 | 1647 | 64
9423 | Crory_110 | CRORY_20 | T121_63MVA | 110 | 21.4 | 1 | 1648 | 64
9431 | Garrow_T121 | GARROW_T121 | T121_20MVA | 110 | 21.4 | 1 | 1649 | 64
9447 | Liberty Street_110 | LIBERITY_10 | T101_20MVA | 110 | 10.7 | 1 | 1650 | 64
9455 | SORNEHILL_T122 | SORNEHILL_T122 | T122_31.5_MVA | 110 | 21.4 | 1 | 1651 | 64
9461 | Corderry_T122 | CORDERRY_1 | T122_63MVA | 110 | 21.4 | 1 | 1652 | 64
9463 | Garrow_T122 | GARROW_T122 | T122_100MVA | 110 | 21.4 | 0 | 1653 | 0
9464 | Liberty Street_110 | LIBERTY2_10 | T102_20MVA | 110 | 10.7 | 0 | 1654 | 0
10188 | Arigna_110 | ARIGNA_G1 | T121_15MVA | 110 | 21.4 | 1 | 1655 | 64
10206 | AHANE_1A_110 | AHANE_10 | T102_15MVA | 110 | 10.7 | 1 | 1656 | 64
12059 | MIDLETON_110 | MIDLETON_38 | T141_63_MVA | 110 | 41.6 | 2 | 1657 | 44
12061 | MIDLETON_110 | MIDLETON_38 | T142_63_MVA | 110 | 41.6 | 2 | 1658 | 0
12071 | TRIEN_110 | TRIEN_38 | T141_63_MVA | 110 | 41.6 | 2 | 1659 | 0
12073 | TRIEN_110 | TRIEN_38 | T142_63_MVA | 110 | 41.6 | 2 | 1660 | 44
12078 | ENNIS_110 | ENNIS_38 | T141_63_MVA | 110 | 41.6 | 2 | 1661 | 0
12079 | ENNIS_110 | ENNIS_38 | T142_63_MVA | 110 | 41.6 | 2 | 1662 | 56
12084 | MULLINGAR_110 | MULLINGAR_38 | T141_63_MVA | 110 | 41.6 | 2 | 1663 | 0
12085 | MULLINGAR_110 | MULLINGAR_38 | T142_63_MVA | 110 | 41.6 | 2 | 1664 | 44
12086 | DUNFIRTH_110 | DUNFIRTH_20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1665 | 0
12087 | DUNFIRTH_110 | Dunfirth2_20 | T122_31.5_MVA | 110 | 21.4 | 1 | 1666 | 56
12089 | BELLACORRICK_110 | BELLACORI_38 | T142_63_MVA | 110 | 41.6 | 1 | 1667 | 0
12094 | TONROE_110 | TONROE_38 | T141_31.5_MVA | 110 | 41.6 | 2 | 1668 | 0
12099 | BUTLERSTOWN_110 | BUTLERSTOWN__38 | T141_63_MVA | 110 | 41.6 | 2 | 1669 | 0
12100 | BUTLERSTOWN_110 | BUTLERSTOWN__38 | T142_63_MVA | 110 | 41.6 | 2 | 1670 | 52
12104 | EASTMONT_110 | EASTMONT_10 | T101_31.5_MVA | 110 | 10.7 | 1 | 1671 | 0
12105 | EASTMONT_110 | EASTMONT_10 | T102_31.5_MVA | 110 | 10.7 | 1 | 1672 | 44
12113 | FERMOY_110 | FERMOY_20 | T122_31.5_MVA | 110 | 21.4 | 1 | 1673 | 44
12114 | FERMOY_110 | FERMOY_20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1674 | 0
12131 | New Mayfield-Riverstown Station _110 | New Mayfield-Riverstown Station _20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1675 | 0
12132 | New Mayfield-Riverstown Station _110 | New Mayfield-Riverstown Station _20 | T122_31.5_MVA | 110 | 21.4 | 1 | 1676 | 44
12152 | Fosterstown_110 | Fosterstown_20 | T123_31.5_MVA | 110 | 21.4 | 1 | 1677 | 44
12153 | Fosterstown_110 | Fosterstown_20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1678 | 0
12192 | South East Carlow_110 | South East Carlow_20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1679 | 0
12193 | South East Carlow_110 | South East Carlow_20 | T122_31.5_MVA | 110 | 21.4 | 1 | 1680 | 44
12220 | SOUTH ATHY_110 | SOUTH ATHY_20 | T142_31.5_MVA | 110 | 21.4 | 0 | 1681 | 0
12221 | SOUTH ATHY_110 | SOUTH ATHY_20 | T141_31.5_MVA | 110 | 21.4 | 0 | 1682 | 0
12237 | North-East Cashel_110 | North-East Cashel_20 | T122_20_MVA | 110 | 21.4 | 1 | 1683 | 44
12238 | North-East Cashel_110 | North-East Cashel_20 | T121_20_MVA | 110 | 21.4 | 1 | 1684 | 0
12256 | Walterstown_110 | Walterstown_38 | T141_63_MVA | 110 | 41.6 | 1 | 1685 | 0
12257 | Walterstown_110 | Walterstown_38 | T142_63_MVA | 110 | 41.6 | 1 | 1686 | 44
12415 | POOLBEG3_220 | POOLBEG_33 | T2008_90MVA | 220 | 33 | 0 | 1687 | 0
12419 | IRISHTWN_220 | STH_WALL_33 | T2002_35MVA | 220 | 33 | 0 | 1688 | 0
12426 | MNYPT P | MONEYPNT 220 | T4202_500MVA | 400 | 220 | 0 | 1689 | 0
12428 | MNYPT D | MONEYPNT 220 | T4201_500MVA | 400 | 220 | 0 | 1690 | 0
12431 | OLDSTR 400 | OLDSTR 220 | T4202_500MVA | 400 | 220 | 0 | 1691 | 0
12432 | WOODLAND 400 | N3599 | T4204_500MVA | 400 | 220 | 0 | 1692 | 0
12433 | WOODLAND 400 | WOODLAND 220 | T4201_500MVA | 400 | 240 | 0 | 1693 | 0
12434 | WOODLAND 400 | WOODLAND_1 | T4202_500MVA | 400 | 220 | 0 | 1694 | 0
12435 | DUNSTOWN 400 | DUNSTOWN 220 | T4202_500MVA | 400 | 220 | 0 | 1695 | 0
12436 | DUNSTOWN 400 | DUNSTOWN 220 | T4201_500MVA | 400 | 240 | 0 | 1696 | 0
12440 | BRACETWN_220 | BRACETWN2_20 | T224_80MVA | 220 | 21.4 | 0 | 1697 | 0
12441 | BRACETWN_220 | BRACETWN1_20 | T222_80MVA | 220 | 21.4 | 0 | 1698 | 0
12442 | HADWELL_220 | AGHADA_02B | TA002_90MVA | 220 | 33 | 0 | 1699 | 0
12443 | HADWELL_220 | AGHADA_02A | TA001_90MVA | 220 | 33 | 0 | 1700 | 0
12444 | CLONEE | CLONEE3_20 | T221_63_MVA | 220 | 21.4 | 0 | 1701 | 0
12445 | CLONEE | CLONEE2_20 | T224_63_MVA | 220 | 21.4 | 0 | 1702 | 0
12446 | CLONEE | CLONEE1_20 | T222_63_MVA | 220 | 21.4 | 0 | 1703 | 0
12447 | CRUISERATH | CRUISERAT_20 | T223_110MVA | 220 | 21.4 | 0 | 1704 | 0
12448 | CRUISERATH | CRUISERAT_20 | T221_110MVA | 220 | 21.4 | 0 | 1705 | 0
12449 | SHBRIDGE 220 | SHBRIDGE 110 | T2102_125MVA | 220 | 110 | 0 | 1706 | 0
12450 | SHBRIDGE 220 | SHBRIDGE 110 | T2101_125MVA | 220 | 110 | 0 | 1707 | 0
12451 | CLONIFFN_220 | CLONIFEEN_33 | T232_110MVA | 220 | 33 | 0 | 1708 | 0
12452 | KELLYSTOWN | KELLYSTN35_3 | T232_132MVA | 220 | 34.5 | 0 | 1709 | 0
12453 | KELLYSTOWN | KELLYSTN35_2 | T233_132MVA | 220 | 34.5 | 0 | 1710 | 0
12454 | KELLYSTOWN | KELLYSTN35_1 | T237_132MVA | 220 | 34.5 | 0 | 1711 | 0
12455 | BELCAMP | BELCAMP 110 | T2103_250MVA | 220 | 110 | 0 | 1712 | 0
12457 | GTISLAND_220 | GTISLAND_110 | T2102_125MVA | 220 | 110 | 0 | 1713 | 0
12458 | GTISLAND_220 | GTISLAND_110 | T2101_125MVA | 220 | 110 | 0 | 1714 | 0
12462 | GORMAN_220 | GORMAN_110 | T2101_250MVA | 220 | 110 | 0 | 1715 | 0
12465 | KELLIS_220 | KELLIS_110 | T2102_125MVA | 220 | 110 | 0 | 1716 | 0
12466 | KELLIS_220 | KELLIS_110 | T2101_125MVA | 220 | 110 | 0 | 1717 | 0
12467 | LODGWOOD_220 | LODGWOOD | T2102_250MVA | 220 | 110 | 0 | 1718 | 0
12468 | BALLYNAHULLA | BALLYNAH_2 | T2102_250MVA | 220 | 110 | 0 | 1719 | 0
12469 | BALLYNAHULLA | BALLYNAH_1 | T2101_250MVA | 220 | 110 | 0 | 1720 | 0
12470 | BALLYVOUSKIL | BALLYVOU_2 | T2102_250MVA | 220 | 110 | 0 | 1721 | 0
12471 | BALLYVOUSKIL | BALLYVOU_1 | T2101_250MVA | 220 | 110 | 0 | 1722 | 0
12472 | KNOCKANURE | KNOCKAN_2 | T2102_250MVA | 220 | 110 | 0 | 1723 | 0
12473 | KNOCKANURE | KNOCKAN_1 | T2101_250MVA | 220 | 110 | 0 | 1724 | 0
12474 | KILPADDOGE | KILPADDOGE | T2102_250MVA | 220 | 110 | 0 | 1725 | 0
12475 | KILPADDOGE | KILPADDOGE | T2101_250MVA | 220 | 110 | 0 | 1726 | 0
12480 | KNOKRAHB 220 | KNOKRAHA 110 | T2101_250_MV | 220 | 110 | 0 | 1727 | 0
12481 | CULLENAGH | CULLNGH | T2101_250MVA | 220 | 110 | 0 | 1728 | 0
12484 | TARBERT 220 | TARBERT 110 | T2102_250MVA | 220 | 110 | 0 | 1729 | 0
12487 | CLASHAVOON | CLASHAVN | T2102_250MVA | 220 | 110 | 0 | 1730 | 0
12488 | CLASHAVOON | CLASHAVN | T2101_250MVA | 220 | 110 | 0 | 1731 | 0
12489 | RAFFEEN 220 | RAFFEEN 110 | T2102_250MVA | 220 | 110 | 0 | 1732 | 0
12490 | RAFFEEN 220 | RAFFEEN 110 | T2101_250MVA | 220 | 110 | 0 | 1733 | 0
12495 | LOUTH 220 | LOUTH 110 | T2104_250MVA | 220 | 110 | 0 | 1734 | 0
12496 | LOUTH 220 | LOUTH 110 | T2103_125MVA | 220 | 110 | 0 | 1735 | 0
12497 | LOUTH 220 | LOUTH 110 | T2102_125MVA | 220 | 110 | 0 | 1736 | 0
12498 | LOUTH 220 | LOUTH 110 | T2101_125MVA | 220 | 110 | 0 | 1737 | 0
12499 | SRANANAGH220 | SRANANAGH_1 | T2102_250MVA | 220 | 110 | 0 | 1738 | 0
12500 | KNOKRAHA 220 | KNOKRAHA 110 | T2102_250_MV | 220 | 110 | 0 | 1739 | 0
12501 | KILLONAN 220 | KILLONAN 110 | T2104_125MVA | 220 | 110 | 0 | 1740 | 0
12502 | KILLONAN 220 | KILLONAN 110 | T2103_250MVA | 220 | 110 | 0 | 1741 | 0
12503 | KILLONAN 220 | KILLONAN 110 | T2102_63MVA | 220 | 110 | 0 | 1742 | 0
12504 | KILLONAN 220 | KILLONAN 110 | T2101_63MVA | 220 | 110 | 0 | 1743 | 0
12509 | FLAGFORD 220 | FLAGFORD 110 | T2102_125MVA | 220 | 110 | 0 | 1744 | 0
12510 | FLAGFORD 220 | FLAGFORD 110 | T2101_125MVA | 220 | 110 | 0 | 1745 | 0
12521 | CASHLA 220 | CASHLA 110 | T2104_125MVA | 220 | 110 | 0 | 1746 | 0
12522 | CASHLA 220 | CASHLA 110 | T2102_250MVA | 220 | 110 | 0 | 1747 | 0
12523 | CASHLA 220 | CASHLA 110 | T2101_250MVA | 220 | 110 | 0 | 1748 | 0
12525 | TYNAGH_220 | TYNA_15.75kV | TYNAGH_220 - TYNA_15.75kV - TYNAGH_15kV - 1 | 220 | 15.75 | 0 | 1749 | 0
12530 | AGHADA 220 | AGHADA 110 | T2102_125MVA | 220 | 110 | 0 | 1750 | 0
12532 | TURLHILL | TRLHL_G3_TH3 | T20034_175_M | 220 | 10.7 | 0 | 1751 | 0
12533 | TURLHILL | TRLHL_G1_TH1 | T20012_175_M | 220 | 10.7 | 0 | 1752 | 0
12535 | ARKLOW 220 | ARKLOW 110 | T2102_125MVA | 220 | 110 | 0 | 1753 | 0
12536 | MONEYPNT 220 | MONEYPNT 110 | T2102_250MVA | 220 | 110 | 0 | 1754 | 0
12537 | MULREAVY | MULREAVY_33 | T131_120MVA | 110 | 33 | 0 | 1755 | 0
12540 | CROAGHONAGH | CROAGHONA_33 | T131_110MVA | 110 | 33 | 0 | 1756 | 0
12543 | DERRYCARNEY_110 | DERRYCAR2_33 | T134_40_MVA | 110 | 33 | 0 | 1757 | 0
12544 | DERRYCARNEY_110 | DERRYCAR1_33 | T132_110MVA | 110 | 33 | 0 | 1758 | 0
12545 | KILCUMBER | KILCUMBER_33 | T131_110MVA | 110 | 33 | 0 | 1759 | 0
12548 | ROSSPILE | ROSSPILE_33 | T131_120MVA | 110 | 33 | 0 | 1760 | 0
12550 | MOUNT LUCAS | MOUNT LUCAS_20 | GT1_90MVA | 110 | 21.4 | 0 | 1761 | 0
12553 | BLUNDELSTOWN | BLUNDELS_33 | T131_70MVA | 110 | 33 | 0 | 1762 | 0
12852 | Pembroke_110 | Pembroke_10 | T101_31.5_MVA | 110 | 10.7 | 1 | 1763 | 0
12853 | Pembroke_110 | Pembroke_10 | T102_31.5_MVA | 110 | 10.7 | 1 | 1764 | 44
12865 | BELLACORRICK_110 | BELLACORI_20 | T121_10_MVA | 110 | 21.4 | 2 | 1765 | 0
12870 | KILTEEL_110 | KILTEEL_38 | T141_63_MVA | 110 | 41.6 | 2 | 1766 | 0
12871 | KILTEEL_110 | KILTEEL_38 | T142_63_MVA | 110 | 41.6 | 2 | 1767 | 44
12880 | IKERRIN_110 | IKERRIN_38 | T142_31.5_MVA | 110 | 41.6 | 2 | 1768 | 0
12891 | Killinick_110 | killinick_20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1769 | 0
12892 | Killinick_110 | killinick_20 | T122_31.5_MVA | 110 | 21.4 | 1 | 1770 | 44
12893 | CASTLEBAR_110 | CASTLEBAR_38 | T141_63_MVA | 110 | 41.6 | 1 | 1771 | 0
12894 | CASTLEBAR_110 | CASTLEBAR_38 | T142_63_MVA | 110 | 41.6 | 1 | 1772 | 0
12906 | Wilton_110 | Wilton_38 | T141_63_MVA | 110 | 41.6 | 1 | 1773 | 0
12907 | Wilton_110 | Wilton_38 | T142_63_MVA | 110 | 41.6 | 1 | 1774 | 44
12943 | New 110/MV station at Birdhill_110 | New 110/MV station at Birdhill_20 | T122_31.5_MVA | 110 | 21.4 | 1 | 1775 | 44
12944 | New 110/MV station at Birdhill_110 | New 110/MV station at Birdhill_20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1776 | 0
12972 | POPPINTREE | POPPINTREE2_3 | T121_31.5_MVA | 110 | 21.4 | 1 | 1777 | 44
12981 | BLUNDELSTOWN | Blundelstown_38 | T141_63_MVA | 110 | 41.6 | 1 | 1778 | 0
12982 | BLUNDELSTOWN | Blundelstown_38 | T142_63_MVA | 110 | 41.6 | 1 | 1779 | 44
13003 | KILL HILL_110 | KILL HILL_20 | T121_20_MVA | 110 | 21.4 | 0 | 1780 | 0
13004 | KILL HILL_110 | KILL HILL_20 | T122_20_MVA | 110 | 21.4 | 0 | 1781 | 0
13018 | Killacloyne_110 | Killacloyne_20 | T121_20_MVA | 110 | 21.4 | 1 | 1782 | 44
13019 | Killacloyne_110 | Killacloyne_20 | T122_20_MVA | 110 | 21.4 | 1 | 1783 | 0
13033 | NAVAN_110 | NAVAN_20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1784 | 0
13034 | NAVAN_110 | NAVAN_20 | T122_31.5_MVA | 110 | 21.4 | 1 | 1785 | 44
13045 | North City Junction_110 | North City Junction_20 | T122_31.5_MVA | 110 | 21.4 | 1 | 1786 | 0
13046 | North City Junction_110 | North City Junction_20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1787 | 44
13055 | YELLOWMEADOWS_A1 | Yellowmeadows_20 | T123_31.5_MVA | 110 | 21.4 | 1 | 1788 | 0
13056 | YELLOWMEADOWS_A1 | Yellowmeadows_20 | T124_31.5_MVA | 110 | 21.4 | 1 | 1789 | 44
13064 | DUNSINK_110 | DUNSINK_20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1790 | 0
13065 | DUNSINK_110 | DUNSINK_20 | T122_31.5_MVA | 110 | 21.4 | 1 | 1791 | 44
13079 | MCDERMOT_110 | McDermott_20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1792 | 0
13080 | MCDERMOT_110 | McDermott_20 | T122_31.5_MVA | 110 | 21.4 | 1 | 1793 | 44
13088 | West Portlaoise_110 | West Portlaoise_38 | T141_31.5_MVA | 110 | 41.6 | 1 | 1794 | 0
13089 | West Portlaoise_110 | West Portlaoise_38 | T142_31.5_MVA | 110 | 41.6 | 1 | 1795 | 44
13101 | Ballycummin_110 | Ballycummin_38 | T142_63_MVA | 110 | 41.6 | 1 | 1796 | 44
13102 | Ballycummin_110 | Ballycummin_38 | T141_63_MVA | 110 | 41.6 | 1 | 1797 | 0
13112 | East Athlone_110 | East Athlone_38 | T141_63_MVA | 110 | 41.6 | 1 | 1798 | 0
13113 | East Athlone_110 | East Athlone_38 | T142_63_MVA | 110 | 41.6 | 1 | 1799 | 44
13115 | East Galway_110 | East Galway_38 | T141_63_MVA | 110 | 41.6 | 1 | 1800 | 0
13116 | East Galway_110 | East Galway_38 | T142_63_MVA | 110 | 41.6 | 1 | 1801 | 44
13136 | NEWBRIDGE EAST_110 | NEWBRIDGE EAST_38 | T141_63_MVA | 110 | 41.6 | 1 | 1802 | 0
13137 | NEWBRIDGE EAST_110 | NEWBRIDGE EAST_38 | T142_63_MVA | 110 | 41.6 | 1 | 1803 | 44
13144 | BELMAYNE_110 | BELMAYNE_38 | T141_63_MVA | 110 | 41.6 | 1 | 1804 | 0
13145 | BELMAYNE_110 | BELMAYNE_38 | T142_63_MVA | 110 | 41.6 | 1 | 1805 | 44
13165 | RINAWADE_110 | RINAWADE_38 | T141_31.5_MVA | 110 | 41.6 | 1 | 1806 | 0
13166 | RINAWADE_110 | RINAWADE_38 | T142_31.5_MVA | 110 | 41.6 | 1 | 1807 | 44
13174 | KILNAP_110 | KILNAP_20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1808 | 0
13175 | KILNAP_110 | KILNAP_20 | T122_31.5_MVA | 110 | 21.4 | 1 | 1809 | 52
13195 | Steevens Lane | Steevens Lane_10 | T121_31.5_MVA | 110 | 10.7 | 1 | 1810 | 0
13197 | Steevens Lane | Steevens Lane_10 | T122_31.5_MVA | 110 | 10.7 | 1 | 1811 | 48
13198 | Nutley Lane | Nutley Lane_10 | T122_31.5_MVA | 110 | 10.7 | 1 | 1812 | 44
13199 | Nutley Lane | Nutley Lane_10 | T121_31.5_MVA | 110 | 10.7 | 1 | 1813 | 0
13218 | COURTLOUGH_110 | COURTLOUGH_38 | T141_63_MVA | 110 | 41.6 | 1 | 1814 | 0
13219 | COURTLOUGH_110 | COURTLOUGH_38 | T142_63_MVA | 110 | 41.6 | 1 | 1815 | 44
13260 | DROMBEG_110 | DROMBEG_38 | T142_31.5_MVA | 110 | 41.6 | 1 | 1816 | 64
13280 | MONAGHAN__110 | MONAGHAN__20 | T121_31.5_MVA | 110 | 21.4 | 1 | 1817 | 0
13281 | MONAGHAN__110 | MONAGHAN__20 | T123_31.5_MVA | 110 | 21.4 | 1 | 1818 | 44
13284 | MARINA_110 | MARINA2_10 | T106_31.5_MVA | 110 | 10.7 | 0 | 1819 | 0
13285 | MARINA_110 | MARINA1_10 | T105_31.5_MVA | 110 | 10.7 | 2 | 1820 | 60
13286 | MARINA_110 | MARINA_38 | T141_63_MVA | 110 | 41.6 | 1 | 1821 | 0
13287 | MARINA_110 | MARINA_38 | T142_63_MVA | 110 | 41.6 | 1 | 1822 | 60
13290 | BELLACORRICK_110 | Bellacorrick_38 | T143_63_MVA | 110 | 41.6 | 1 | 1823 | 48
13293 | CATHALEENS FALL_110 | CATHFALLS_38 | T141_63_MVA | 110 | 41.6 | 2 | 1824 | 52
13299 | DERRYIRON | DERRYIRON_38 | T141_63_MVA | 110 | 41.6 | 1 | 1825 | 52
13300 | DUNFIRTH_110 | DUNFIRTH_20 | T122_31.5_MVA | 110 | 21.4 | 1 | 1826 | 0
13303 | BALLYRAGGET_110 | BALLYRAGGET | T141_63_MVA | 110 | 41.6 | 2 | 1827 | 0
13305 | BALLYRAGGET_110 | BALLYRAGGET | T142_63_MVA | 110 | 41.6 | 2 | 1828 | 56
13318 | ARKLOW_T143 | ARKLOW_2_38 | T143_63_MVA | 110 | 41.6 | 1 | 1829 | 56
13321 | IKERRIN_110 | IKERRIN_38 | T141_31.5_MVA | 110 | 41.6 | 2 | 1830 | 44
13322 | BELLACORRICK_110 | BELLACORI_38 | T141_63_MVA | 110 | 41.6 | 1 | 1831 | 0
13324 | BELLACORRICK_110 | BELLACORI_20 | T122_10_MVA | 110 | 21.4 | 2 | 1832 | 44
13326 | TONROE_110 | TONROE_38 | T142_31.5_MVA | 110 | 41.6 | 2 | 1833 | 44
13328 | Great Island_110 | GTISLND_38A2 | T141_63_MVA | 110 | 41.6 | 2 | 1834 | 48
13329 | Great Island_110 | GTISLND_38A2 | T142_63_MVA | 110 | 41.6 | 2 | 1835 | 0
13330 | CAUTEEN_T143 | CAUTEEN_3_38 | T143_63_MVA | 110 | 41.6 | 1 | 1836 | 48
13334 | Castleview_T103 | Castleview_3_10 | T103_31.5_MVA | 110 | 10.7 | 1 | 1837 | 52
13336 | BARYMORE_110 | BARRYMORE_38 | T141_63_MVA | 110 | 41.6 | 2 | 1838 | 52
13338 | DUNGARVAN_110 | DUNGARVAN_38 | T141_63_MVA | 110 | 41.6 | 2 | 1839 | 0
13339 | DUNGARVAN_110 | DUNGARVAN_38 | T142_63_MVA | 110 | 41.6 | 2 | 1840 | 48
13341 | Crory_T122 | Crory_2_20 | T122_31,5_MVA | 110 | 21.4 | 1 | 1841 | 60
13342 | BALTINGLASS | BALTINGL1_20 | T421_10MVA | 41.6 | 21.4 | 0 | 1842 | 0
13343 | BALTINGLASS | BALTINGL2_20 | T422_10MVA BALTINGLASS | 41.6 | 21.4 | 2 | 1843 | 60
13344 | West Portlaoise_110 | West Portlaoise_1_20 | T121_31.5_MVA | 110 | 21.4 | 0 | 1844 | 0
13345 | West Portlaoise_110 | West Portlaoise_2_20 | T122_31.5_MVA | 110 | 21.4 | 1 | 1845 | 44
13346 | ATHY_110 | ATHY_X101 | T121_31.5_MVA | 110 | 21.4 | 2 | 1846 | 52
13347 | ATHY_110 | ATHY_X102 | T122_31.5_MVA | 110 | 21.4 | 0 | 1847 | 0
13348 | BLAKE_38 | BLAKE1_10 | T41_15_MVA | 41.6 | 10.7 | 1 | 1848 | 0
13349 | BLAKE_38 | BLAKE2_10 | T42_15_MVA | 41.6 | 10.7 | 1 | 1849 | 44
13350 | BISHOPSTOWN | BISHOPS1_10 | T41_15_MVA BISHOPSTOWN | 41.6 | 10.7 | 0 | 1850 | 0
13351 | BISHOPSTOWN | BISHOPS2_10 | T42_15_MVA BISHOPSTOWN | 41.6 | 10.7 | 2 | 1851 | 44