MV/LV Substation TE***898Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.323 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41214 | 0 |  | --> | C16 ex COES ROAD | Coes Road: T41∥T42 | Dundalk |  | 54.0032 | -6.3916
MV/LV Substation TE***904 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52kW. | --> | C13 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6554 | -8.094
MV/LV Substation TE***908 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.34 | 3.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40948 | 0 |  | --> | C18 ex CASTLEREA | Castlerea: T41∥T42 | Carrick On Shannon |  | 53.7658 | -8.4757
MV/LV Substation TE***910X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C15 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.7872 | -8.9234
MV/LV Substation TE***919Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =122kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.2071 | 0 |  | --> | C14 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.2248 | -7.0062
MV/LV Substation TE***920Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =103kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0114 | 0.20294 | 0 |  | --> | C14 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.2232 | -7.0054
MV/LV Substation TE***941X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =338kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =399.8kW. | --> | C26 ex PORTLAOISE | Portlaoise: T42 | Portlaoise |  | 53.0263 | -7.3114
MV/LV Substation TE***942 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.149 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0 | 0 | Constrained,otherwise capacity available =204kW. | --> | C13 ex LEE BRIDGE | Lee Bridge: T41 | Macroom |  | 51.8386 | -8.9894
MV/LV Substation TE***942X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =162kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20599 | 0 |  | --> | C13 ex SPIDDAL | Spiddal: T42 | Screeb |  | 53.2469 | -9.2826
MV/LV Substation TE***942X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C20 ex CLOONLOUGH | Cloonlough: T41∥T42 | Barrymore |  | 52.2637 | -8.2689
MV/LV Substation TE***949X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.279 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0019 | 0.4169 | 0 |  | --> | C12 ex CARRIGLAWN | Carriglawn: T41∥T42 | Wexford |  | 52.3416 | -6.4656
MV/LV Substation TE***955 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 5.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.059367 | 0 |  | --> | E17 ex MOY | Moy: T421∥T422 | Moy |  | 54.1098 | -9.1665
MV/LV Substation TE***962 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C14 ex GREYSTONES | Greystones: T42 | Fassaroe |  | 53.1555 | -6.0968
MV/LV Substation TE***966 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 3.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C17 ex CASTLEBLAYNEY | Castleblayney: T41 | Dundalk |  | 54.1273 | -6.8574
MV/LV Substation TE***969X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex DENNEHYS CROSS | Dennehys Cross: T42 | Trabeg |  | 51.8802 | -8.5087
MV/LV Substation TE***972X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.165 | 5.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20552 | 0 |  | --> | C13 ex PURCELLS INCH | Purcells Inch: T42 | Kilkenny |  | 52.6444 | -7.2138
MV/LV Substation TE***988X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | C20 ex TEMPLEMORE | Templemore: T42 | Ikerrin |  | 52.8231 | -7.844
MV/LV Substation TE***989Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10842 | 0 |  | --> | C21 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7573 | -6.2758
MV/LV Substation TH***001 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =345kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E13 ex DALTON | Dalton: T421∥T422 | Dalton |  | 53.7197 | -8.9983
MV/LV Substation TH***001 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.305 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.40992 | 0 |  | --> | C16 ex BALBRIGGAN | Balbriggan: T42 | Glasmore |  | 53.6084 | -6.1836
MV/LV Substation TH***001 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.142 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.43924 | 0 |  | --> | C20 ex CAHIR | Cahir: T42 | Cahir |  | 52.3761 | -7.9253
MV/LV Substation TH***001 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.203 | 3 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =425.3kW. | --> | C19 ex SWINFORD | Swinford: T41∥T42 | Castlebar |  | 53.9433 | -8.9498
MV/LV Substation TH***001 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =179kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0019 | 0.5 | 0 |  | --> | C21 ex MALAHIDE | Malahide: T41 | Glasmore |  | 53.4512 | -6.1525
MV/LV Substation TH***001 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =125kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.43268 | 0 |  | --> | C15 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8529 | -8.2956
MV/LV Substation TH***001Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.139 | 10.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.0228 | 0.18553 | 0 |  | --> | C23 ex PELLETSTOWN | Pelletstown: T101 | Finglas |  | 53.383 | -6.3668
MV/LV Substation TH***002 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 |  | --> | 0.19 | 0 | 0 | 0 | 0.0114 | 0 | 0 | Constrained,otherwise capacity available =218.5kW. | --> | C14 ex LEE BRIDGE | Lee Bridge: T42 | Macroom |  | 51.905 | -8.9643
MV/LV Substation TH***002 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =234kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.4217 | 0 |  | --> | C13 ex CORBALLY | Corbally: T41∥T42 | Ardnacrusha |  | 52.669 | -8.6232
MV/LV Substation TH***002 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.161 | 8.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0209 | 0.18414 | 0 |  | --> | C12 ex MONREAD | Monread: T102 | Monread |  | 53.2219 | -6.659
MV/LV Substation TH***002 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00855 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C15 ex KILTIMAGH | Kiltimagh: T41 | Castlebar |  | 53.8481 | -9.0025
MV/LV Substation TH***002 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.225 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.42206 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry: T42 | Tonroe |  | 54.0538 | -8.7303
MV/LV Substation TH***002Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.315 | 3.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.01615 | 0.39638 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge: T41 | Griffinrath |  | 53.3468 | -6.5386
MV/LV Substation TH***003 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.084 | 1.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.01235 | 0.20473 | 0 |  | --> | C13 ex ROSCOMMON | Roscommon: T41 | Lanesboro |  | 53.6232 | -8.1934
MV/LV Substation TH***003X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.04825 | 0 |  | --> | C16 ex RAHANS | Rahans: T41 | Moy |  | 54.106 | -9.1527
MV/LV Substation TH***003Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =161kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0133 | 0 | 0 | Constrained,otherwise capacity available =192.1kW. | --> | C20 ex COOLCARRON | Coolcarron: T41 | Barrymore |  | 52.131 | -8.2889
MV/LV Substation TH***003Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =70kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0019 | 0.10269 | 0 |  | --> | C17 ex CLONES | Clones: T41∥T42 | Shankill |  | 54.2186 | -7.1034
MV/LV Substation TH***004 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.282 | 3.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0266 | 0.39044 | 0 |  | --> | C14 ex SANDYFORD | Sandyford: T42 | Carrickmines |  | 53.2774 | -6.2468
MV/LV Substation TH***004 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20176 | 0 |  | --> | E15 ex TULLOW | Tullow: T421 | Carlow |  | 52.7985 | -6.7415
MV/LV Substation TH***004 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex DINGLE | Dingle: T421 | Oughtragh |  | 52.1432 | -10.2686
MV/LV Substation TH***004 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0.038 | 0.5 | 0 |  | --> | C19 ex LOUGHSHINNY | Loughshinny: T41 | Glasmore |  | 53.5809 | -6.1082
MV/LV Substation TH***004 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =72kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10438 | 0 |  | --> | E11 ex BALLINROBE | Ballinrobe: T421∥T422 | Dalton |  | 53.6217 | -9.2135
MV/LV Substation TH***004Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.268 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.00665 | 0.41358 | 0 |  | --> | C14 ex KELLS | Kells: T41∥T42 | Navan |  | 53.7324 | -6.8721
MV/LV Substation TH***005 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.213 | 3.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0323 | 0.39484 | 0 |  | --> | C14 ex SANDYFORD | Sandyford: T42 | Carrickmines |  | 53.2753 | -6.2467
MV/LV Substation TH***005 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.399 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400.2kW. | --> | E11 ex MACROOM | Macroom: T422 | Macroom |  | 51.8977 | -8.8627
MV/LV Substation TH***005 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.048 | 0 | Constrained,otherwise capacity available =155kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20307 | 0 |  | --> | C15 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 52.9377 | -9.296
MV/LV Substation TH***005 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.141 | 1.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20922 | 0 |  | --> | C18 ex CARRICKMACROSS | Carrickmacross: T42 | Meath Hill |  | 53.9736 | -6.7198
MV/LV Substation TH***005Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =134kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01805 | 0.19129 | 0 |  | --> | C18 ex MOUNTGORRY | Mountgorry: T42 | Grange (dr) |  | 53.4509 | -6.1829
MV/LV Substation TH***006 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.295 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0.40346 | 0 |  | --> | C19 ex SANDYFORD | Sandyford: T41 | Carrickmines |  | 53.2739 | -6.2511
MV/LV Substation TH***006 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =355kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0228 | 0.38314 | 0 |  | --> | C17 ex LOUGHREA | Loughrea: T41∥T42 | Somerset |  | 53.2017 | -8.5572
MV/LV Substation TH***006 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.334 | 3.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =410.4kW. | --> | C16 ex BALLYSHANNON | Ballyshannon: T41∥T42 | Cathaleens Fall |  | 54.5019 | -8.1961
MV/LV Substation TH***007 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.001 | 2.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.22642 | 0 |  | --> | C17 ex VIRGINIA | Virginia: T41∥T42 | Meath Hill |  | 53.8344 | -7.0788
MV/LV Substation TH***007 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C18 ex RAMSTOWN | Ramstown: T41∥T42 | Crane |  | 52.6725 | -6.296
MV/LV Substation TH***008 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.212 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42898 | 0 |  | --> | C14 ex INCHICORE NORTH | Inchicore North: T41 | Inchicore 110kv |  | 53.343 | -6.3387
MV/LV Substation TH***008 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.176 | 3.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2038 | 0 |  | --> | C22 ex CASTLEREA | Castlerea: T41∥T42 | Carrick On Shannon |  | 53.7703 | -8.5014
MV/LV Substation TH***008 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.259 | 14.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.41094 | 0 |  | --> | C24 ex STEPHENSTOWN | Stephenstown: T102 | Finglas |  | 53.6055 | -6.1727
MV/LV Substation TH***009 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.072 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.21347 | 0 |  | --> | C20 ex CASTLEBLAYNEY | Castleblayney: T42 | Dundalk |  | 54.1172 | -6.7354
MV/LV Substation TH***010 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.14 | 2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.20338 | 0 |  | --> | C16 ex CAPPAMORE | Cappamore: T41∥T42 | Ardnacrusha |  | 52.6044 | -8.2449
MV/LV Substation TH***010 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.307 | 3.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4146 | 0 |  | --> | C13 ex CASTLEBLAYNEY | Castleblayney: T41 | Dundalk |  | 54.1208 | -6.7488
MV/LV Substation TH***010Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =313kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02375 | 0.38868 | 0 |  | --> | C11 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1499 | -7.0534
MV/LV Substation TH***011 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =155kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0 | 0 | Constrained,otherwise capacity available =205.1kW. | --> | C17 ex ROSCREA | Roscrea: T41 | Ikerrin |  | 52.9445 | -7.7907
MV/LV Substation TH***011 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E13 ex TULLOW | Tullow: T421 | Carlow |  | 52.7307 | -6.6895
MV/LV Substation TH***011Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.171 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20459 | 0 |  | --> | E18 ex LONGFORD | Longford: T422 | Richmond |  | 53.7353 | -7.7757
MV/LV Substation TH***011Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =297kVA. | --> | 0.38 | 0 | 0 | 0 | 0.15675 | 0.25114 | 0 |  | --> | C11 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1501 | -7.0519
MV/LV Substation TH***012 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.144 | 6.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =208.8kW. | --> | E11 ex RATHKEALE | Rathkeale: T421∥T422 | Rathkeale |  | 52.6016 | -8.9729
MV/LV Substation TH***013 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.154 | 9.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.4325 | 0 |  | --> | C13 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.7986 | -9.5252
MV/LV Substation TH***013 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =346kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.39454 | 0 |  | --> | E13 ex DALTON | Dalton: T421∥T422 | Dalton |  | 53.7235 | -8.9979
MV/LV Substation TH***015 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.234 | 7 |  | --> | 0.38 | 0 | 0 | 0 | 0.00665 | 0.4187 | 0 |  | --> | C12 ex ARDGEEHA | Ardgeeha: T41∥T42 | Doon |  | 52.3606 | -7.6988
MV/LV Substation TH***015 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.132 | 3.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.0152 | 0 | 0 | Constrained,otherwise capacity available =194.6kW. | --> | C13 ex TURLOUGH ROAD | Turlough Road: T41∥T42 | Castlebar |  | 53.8635 | -9.289
MV/LV Substation TH***015Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05142 | 0 |  | --> | C22 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.3361 | -6.5382
MV/LV Substation TH***015Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex BALLINACURRA | Ballinacurra: T42 | Limerick |  | 52.6574 | -8.6272
MV/LV Substation TH***016 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.066 | 9.9 |  | --> | 0.095 | 0 | 0 | 0 | 0.00855 | 0.096295 | 0 |  | --> | C12 ex CONVOY | Convoy: T41∥T42 | Letterkenny |  | 54.8623 | -7.6751
MV/LV Substation TH***016Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 150 kVA :Pole Substation | 0.15 | --> | 0.15 | 0 | 0 | Constrained,otherwise capacity available =115kVA. | --> | 0.1425 | 0 | 0 | 0 | 0.00475 | 0.1505 | 0 |  | --> | C11 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.6592 | -7.8301
MV/LV Substation TH***017 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =164kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.43004 | 0 |  | --> | E18 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.3404 | -7.0566
MV/LV Substation TH***017 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.353 | 4.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40746 | 0 |  | --> | C13 ex MONEENAGEISHA | Moneenageisha: T41 | Galway 110kv |  | 53.2747 | -9.0448
MV/LV Substation TH***018 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =86kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =212.4kW. | --> | C14 ex BELLFIELD | Bellfield: T41∥T42 | Crane |  | 52.5004 | -6.5571
MV/LV Substation TH***018X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 1.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10484 | 0 |  | --> | C12 ex ABBEYFEALE | Abbeyfeale: T42 | Trien |  | 52.3738 | -9.3096
MV/LV Substation TH***018X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | E19 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.4978 | -7.1296
MV/LV Substation TH***019 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =258kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.4181 | 0 |  | --> | C13 ex TUAM SOUTH | Tuam South: T42 | Cloon |  | 53.5161 | -8.8521
MV/LV Substation TH***019Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.312 | 25.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.02375 | 0.38884 | 0 |  | --> | C19 ex ARKLOW | Arklow: T101∥T102 | Arklow |  | 52.807 | -6.1442
MV/LV Substation TH***019Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 4.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05219 | 0 |  | --> | E21 ex ATHENRY | Athenry: T423 | Galway 110kv |  | 53.3714 | -8.7038
MV/LV Substation TH***019Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =312kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.40584 | 0 |  | --> | E15 ex DULEEK | Duleek: T421∥T422 | Drybridge |  | 53.6601 | -6.4096
MV/LV Substation TH***020Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =21kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.054432 | 0 |  | --> | C18 ex BLAKE | Blake: T41∥T42 | Blake |  | 53.2712 | -6.8202
MV/LV Substation TH***021 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.28 | 0.3 | Constrained,otherwise capacity available =323kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41214 | 0 |  | --> | C19 ex BREWERY ROAD | Brewery Road: T41 | Carrickmines |  | 53.2736 | -6.1987
MV/LV Substation TH***021X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.35 | 4.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40792 | 0 |  | --> | E20 ex ENNISCRONE | Enniscrone: T421∥T422 | Moy |  | 54.2127 | -9.0857
MV/LV Substation TH***023X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05325 | 0 |  | --> | E11 ex BALLYHALE | Ballyhale: T421 | Kilkenny |  | 52.5219 | -7.1316
MV/LV Substation TH***023Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =335kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41026 | 0 |  | --> | C23 ex ATHLONE | Athlone: T41 | Athlone |  | 53.4205 | -7.9413
MV/LV Substation TH***024X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C19 ex KINGSCOURT | Kingscourt: T41 | Meath Hill |  | 53.8001 | -6.7277
MV/LV Substation TH***025X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052345 | 0 |  | --> | E16 ex BALLYCROSSAUN | Ballycrossaun: T421∥T422 | Somerset |  | 53.0901 | -8.1863
MV/LV Substation TH***026 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.267 | 3.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.01995 | 0.39972 | 0 |  | --> | C12 ex BALLINASLOE | Ballinasloe: T41∥T42 | Somerset |  | 53.3262 | -8.1991
MV/LV Substation TH***026Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.01425 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C15 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0495 | -7.3239
MV/LV Substation TH***027 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.152 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.01805 | 0 | 0 | Constrained,otherwise capacity available =188.5kW. | --> | C19 ex TURLOUGH ROAD | Turlough Road: T43 | Castlebar |  | 53.8677 | -9.2925
MV/LV Substation TH***027 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.169 | 9.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.1949 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.7968 | -9.5248
MV/LV Substation TH***027X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C19 ex MILFORD (NR) | Milford (nr): T41∥T42 | Letterkenny |  | 55.0336 | -7.6463
MV/LV Substation TH***027Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | C14 ex BALLYMAHON | Ballymahon: T41∥T42 | Athlone |  | 53.5832 | -7.6555
MV/LV Substation TH***028 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.325 | 11.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.39682 | 0 |  | --> | C32 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2839 | -9.0798
MV/LV Substation TH***028 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.393 | 0.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.02185 | 0.5 | 0 |  | --> | C13 ex SMEARLA | Smearla: T41 | Trien |  | 52.4487 | -9.483
MV/LV Substation TH***028 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.238 | 1.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.39433 | 0 | Constrained,otherwise capacity available =409.1kW. | --> | C15 ex LOUGHTAGALLA | Loughtagalla: T41∥T42 | Thurles |  | 52.6767 | -7.8118
MV/LV Substation TH***029 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =267kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0266 | 0.39272 | 0 |  | --> | C12 ex MORRISTOWN | Morristown: T41∥T42 | Newbridge |  | 53.1859 | -6.7962
MV/LV Substation TH***029Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.267 | 3.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.057 | 0.36072 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge: T41 | Griffinrath |  | 53.3446 | -6.5386
MV/LV Substation TH***031Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0076 | 0.5 | 0 |  | --> | C23 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4183 | -6.4744
MV/LV Substation TH***031Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.297 | 4.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.0285 | 0.38614 | 0 |  | --> | C16 ex LOUGHSHINNY | Loughshinny: T42 | Glasmore |  | 53.5786 | -6.1221
MV/LV Substation TH***032 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.341 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.40634 | 0 |  | --> | C23 ex SRAH | Srah: T43 | Thornsberry |  | 53.28 | -7.4867
MV/LV Substation TH***033X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C18 ex SHERCOCK | Shercock: T41∥T42 | Meath Hill |  | 53.9989 | -6.8935
MV/LV Substation TH***034 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.152 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20754 | 0 |  | --> | C15 ex LOUGHTAGALLA | Loughtagalla: T41∥T42 | Thurles |  | 52.6761 | -7.8102
MV/LV Substation TH***035X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =302kVA. | --> | 0.38 | 0 | 0 | 0 | 0.038 | 0.37538 | 0 |  | --> | C16 ex ATHENRY | Athenry: T41∥T42 | Galway 110kv |  | 53.3019 | -8.7574
MV/LV Substation TH***037 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.04 | 0 | Constrained,otherwise capacity available =356kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40698 | 0 |  | --> | C11 ex GRAIGUENAMANAGH | Graiguenamanagh: T41∥T42 | Kilkenny |  | 52.5388 | -6.9538
MV/LV Substation TH***037 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =142kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20907 | 0 |  | --> | C16 ex CLONES | Clones: T41∥T42 | Shankill |  | 54.1799 | -7.2334
MV/LV Substation TH***038Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.346 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40854 | 0 |  | --> | C17 ex MANOR STREET | Manor Street: T41 | Waterford |  | 52.2598 | -7.1071
MV/LV Substation TH***039 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.040477 | 0 |  | --> | C16 ex ATHENRY | Athenry: T41∥T42 | Galway 110kv |  | 53.2975 | -8.745
MV/LV Substation TH***039Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =150kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.19784 | 0 |  | --> | E17 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4481 | -6.2362
MV/LV Substation TH***040 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 0.1 |  | --> | 0.095 | 0 | 0 | 0 | 0.0076 | 0 | 0 | Constrained,otherwise capacity available =94.1kW. | --> | C16 ex RATHDRUM | Rathdrum: T42 | Arklow |  | 52.9335 | -6.2335
MV/LV Substation TH***040Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C15 ex LITTLE MILLS | Little Mills: T41 | Dundalk |  | 53.9728 | -6.3914
MV/LV Substation TH***041Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.337 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.40396 | 0 |  | --> | C16 ex GILLOGUE | Gillogue: T41∥T42 | Ardnacrusha |  | 52.6809 | -8.6009
MV/LV Substation TH***041Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C15 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3282 | -6.4841
MV/LV Substation TH***042X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C21 ex LITTLE BRAY | Little Bray: T41 | Fassaroe |  | 53.2081 | -6.1809
MV/LV Substation TH***043 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =250kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0 | 0 | Constrained,otherwise capacity available =409.3kW. | --> | C19 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.0913 | -7.6289
MV/LV Substation TH***044 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.334 | 4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =410.4kW. | --> | E17 ex CHARLEVILLE | Charleville: T422 | Charleville |  | 52.3584 | -8.6857
MV/LV Substation TH***045X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E12 ex KILCULLEN | Kilcullen: T424 | Stratford |  | 53.099 | -6.8154
MV/LV Substation TH***046 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.2 | 4.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C12 ex BALLYRAINE | Ballyraine: T41∥T42 | Letterkenny |  | 54.9588 | -7.7039
MV/LV Substation TH***048X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 6.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0152 | 0.5 | 0 |  | --> | C18 ex CARRICKMINES | Carrickmines: T42 | Carrickmines |  | 53.2546 | -6.2082
MV/LV Substation TH***049 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =132kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.44068 | 0 |  | --> | C13 ex CORBALLY | Corbally: T41∥T42 | Ardnacrusha |  | 52.6701 | -8.6322
MV/LV Substation TH***049X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.159 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.19545 | 0 |  | --> | C18 ex KILCOLGAN | Kilcolgan: T42 | Galway 110kv |  | 53.2311 | -8.8907
MV/LV Substation TH***050 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.369 | 25.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40494 | 0 |  | --> | C17 ex ARKLOW | Arklow: T101∥T102 | Arklow |  | 52.7965 | -6.1453
MV/LV Substation TH***050X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.4kW. | --> | E15 ex CASTLETOWNBERE | Castletownbere: T421 | Ballylicky |  | 51.6502 | -9.9171
MV/LV Substation TH***051Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =320kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =412.6kW. | --> | C15 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0505 | -7.3214
MV/LV Substation TH***052X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C16 ex BALLINACURRA | Ballinacurra: T42 | Limerick |  | 52.6335 | -8.6413
MV/LV Substation TH***053 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.17 | 9.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20474 | 0 |  | --> | C12 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.7953 | -9.5247
MV/LV Substation TH***053Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =166kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0 | 0 | Constrained,otherwise capacity available =194.4kW. | --> | C14 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.0905 | -7.607
MV/LV Substation TH***054 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =331kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01995 | 0 | 0 | Constrained,otherwise capacity available =389.9kW. | --> | C13 ex KNOCKAPHUNTA | Knockaphunta: T41∥T42 | Castlebar |  | 53.8476 | -9.2978
MV/LV Substation TH***054Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =115kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =203.1kW. | --> | C11 ex BELLFIELD | Bellfield: T41∥T42 | Crane |  | 52.5049 | -6.5828
MV/LV Substation TH***054Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =99kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0285 | 0.18553 | 0 |  | --> | C17 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1601 | -6.8946
MV/LV Substation TH***055 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.277 | 4.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.4072 | 0 |  | --> | C13 ex OAKFIELD | Oakfield: T41 | Sligo |  | 54.2696 | -8.4936
MV/LV Substation TH***056 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.26 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =411.8kW. | --> | E15 ex CASTLETOWNBERE | Castletownbere: T421 | Ballylicky |  | 51.6507 | -9.9103
MV/LV Substation TH***058 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =325kVA. | --> | 0.38 | 0 | 0 | 0 | 0.04655 | 0 | 0 | Constrained,otherwise capacity available =362.8kW. | --> | C23 ex PORTLAOISE | Portlaoise: T41 | Portlaoise |  | 53.0343 | -7.2905
MV/LV Substation TH***058 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.7kW. | --> | C12 ex LEE BRIDGE | Lee Bridge: T42 | Macroom |  | 51.896 | -8.968
MV/LV Substation TH***058Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.286 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0399 | 0.37584 | 0 |  | --> | C22 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.3348 | -6.5389
MV/LV Substation TH***058Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =137kVA. | --> | 0.19 | 0 | 0 | 0 | 0.02755 | 0.18083 | 0 |  | --> | E17 ex DULEEK | Duleek: T421∥T422 | Drybridge |  | 53.6531 | -6.4346
MV/LV Substation TH***062 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.475 | 0.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex SMEARLA | Smearla: T41 | Trien |  | 52.4447 | -9.4847
MV/LV Substation TH***063 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C24 ex MONFIN | Monfin: T41∥T42 | Wexford |  | 52.4918 | -6.5609
MV/LV Substation TH***063 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.125 | 0.1 | Constrained,otherwise capacity available =221kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.42464 | 0 |  | --> | C14 ex MULGANNON | Mulgannon: T42 | Wexford |  | 52.3312 | -6.4589
MV/LV Substation TH***063Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.323 | 1.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0228 | 0.38814 | 0 |  | --> | C19 ex JOHNSTOWN | Johnstown: T41 | Kilteel |  | 53.2272 | -6.645
MV/LV Substation TH***063Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.296 | 2.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.4103 | 0 |  | --> | C11 ex MOUNTGORRY | Mountgorry: T41 | Grange (dr) |  | 53.4563 | -6.2197
MV/LV Substation TH***064 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E20 ex GARRANACANTY | Garranacanty: T422 | Tipperary |  | 52.4849 | -8.0218
MV/LV Substation TH***064X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =396kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40064 | 0 |  | --> | C12 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.9288 | -7.7291
MV/LV Substation TH***065 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 4.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | E13 ex BALLYRAGGET | Ballyragget: T421∥T422 | Ballyragget |  | 52.7917 | -7.3326
MV/LV Substation TH***066 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.266 | 9.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0323 | 0.38688 | 0 |  | --> | C20 ex ARTANE | Artane: T102 | Finglas |  | 53.3787 | -6.2174
MV/LV Substation TH***067 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.061 | 4 |  | --> | 0.095 | 0 | 0 | 0 | 0.01425 | 0 | 0 | Constrained,otherwise capacity available =91kW. | --> | E14 ex CHARLEVILLE | Charleville: T422 | Charleville |  | 52.3547 | -8.6951
MV/LV Substation TH***067Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =214kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4287 | 0 |  | --> | C17 ex MORRISTOWN | Morristown: T41∥T42 | Newbridge |  | 53.1771 | -6.8005
MV/LV Substation TH***068 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.306 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.40876 | 0 |  | --> | C13 ex SMEARLA | Smearla: T41 | Trien |  | 52.4514 | -9.4764
MV/LV Substation TH***068Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.29 | 3.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41722 | 0 |  | --> | C22 ex COOLOCK | Coolock: T42 | Finglas |  | 53.3887 | -6.1791
MV/LV Substation TH***069Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.278 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.02565 | 0.39206 | 0 |  | --> | C18 ex MALAHIDE | Malahide: T42 | Glasmore |  | 53.449 | -6.1456
MV/LV Substation TH***072X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex CAHERDAVIN | Caherdavin: T41 | Ardnacrusha |  | 52.6735 | -8.6432
MV/LV Substation TH***073X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.182 | 1.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20286 | 0 |  | --> | C17 ex BALLYTIVNAN | Ballytivnan: T41 | Sligo |  | 54.3091 | -8.554
MV/LV Substation TH***073X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 5.3 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C29 ex WOLFE TONE STREET | Wolfe Tone Street: T101 | Finglas |  | 53.351 | -6.2596
MV/LV Substation TH***074 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.172 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20043 | 0 |  | --> | C15 ex COES ROAD | Coes Road: T41∥T42 | Dundalk |  | 54.0045 | -6.3643
MV/LV Substation TH***076 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.078 | 6 |  | --> | 0.095 | 0 | 0 | 0 | 0.01045 | 0.09246 | 0 |  | --> | C14 ex MALLOW | Mallow: T42 | Mallow |  | 52.1432 | -8.6514
MV/LV Substation TH***076 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =354kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex MORRISTOWN | Morristown: T41∥T42 | Newbridge |  | 53.177 | -6.8058
MV/LV Substation TH***077Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.495 | 1.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.038 | 0.5 | 0 |  | --> | C19 ex SALLINS | Sallins: T41 | Griffinrath |  | 53.2897 | -6.7591
MV/LV Substation TH***077Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.256 | 5.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.02755 | 0 | 0 | Constrained,otherwise capacity available =393.4kW. | --> | C11 ex BANDON | Bandon: T101 | Bandon |  | 51.7542 | -8.7368
MV/LV Substation TH***078Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.157 | 0.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =206.8kW. | --> | C17 ex ATHBOY | Athboy: T42 | Navan |  | 53.714 | -7.0169
MV/LV Substation TH***078Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.093 | 3.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0437 | 0.17041 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge: T41 | Griffinrath |  | 53.3468 | -6.5363
MV/LV Substation TH***079Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.346 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =408.5kW. | --> | C21 ex LEE BRIDGE | Lee Bridge: T41 | Macroom |  | 51.9443 | -9.1597
MV/LV Substation TH***080Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.146 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.02375 | 0.18346 | 0 |  | --> | C21 ex MARSHES | Marshes: T41 | Dundalk |  | 53.9613 | -6.3693
MV/LV Substation TH***080Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.11 | 0.1 | Constrained,otherwise capacity available =136kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20498 | 0 |  | --> | C15 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.5082 | -8.8685
MV/LV Substation TH***083 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.468 | 3.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0228 | 0.5 | 0 |  | --> | C23 ex MOUNT MERRION | Mount Merrion: T41 | Carrickmines |  | 53.2901 | -6.2096
MV/LV Substation TH***084Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.4 | 5.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BALLINCOLLIG | Ballincollig: T41 | Kilbarry |  | 51.8872 | -8.5912
MV/LV Substation TH***088X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex TUAM SOUTH | Tuam South: T42 | Cloon |  | 53.5163 | -8.8503
MV/LV Substation TH***088Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.35 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.39992 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.8327 | -6.9035
MV/LV Substation TH***090Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =63kVA. | --> | 0.095 | 0 | 0 | 0 | 0.01995 | 0.08475 | 0 |  | --> | C18 ex LITTLE MILLS | Little Mills: T41 | Dundalk |  | 53.9266 | -6.4056
MV/LV Substation TH***092 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.301 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.40654 | 0 |  | --> | C11 ex MANOR STREET | Manor Street: T41 | Waterford |  | 52.2476 | -7.1081
MV/LV Substation TH***092X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.101 | 1.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =205.2kW. | --> | E17 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1334 | -7.4351
MV/LV Substation TH***093Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.137 | 11.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.0076 | 0.20183 | 0 |  | --> | C14 ex SINGLAND | Singland: T102 | Singland |  | 52.5903 | -8.5474
MV/LV Substation TH***094 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.336 | 11.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.01615 | 0.39312 | 0 |  | --> | C24 ex SALTHILL | Salthill: T102 | Salthill |  | 53.264 | -9.0867
MV/LV Substation TH***095X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C13 ex CHARLESTOWN | Charlestown: T41 | Tonroe |  | 53.9278 | -8.8614
MV/LV Substation TH***095Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.11 | 0.1 | Constrained,otherwise capacity available =273kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.40982 | 0 |  | --> | C23 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.5268 | -8.8535
MV/LV Substation TH***095Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.313 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.41068 | 0 |  | --> | C22 ex HOWTH JUNCTION | Howth Junction: T42 | Grange (dr) |  | 53.3887 | -6.1521
MV/LV Substation TH***096X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CHARLESTOWN | Charlestown: T41 | Tonroe |  | 53.9251 | -8.8574
MV/LV Substation TH***097X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.361 | 8.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.4022 | 0 |  | --> | C14 ex GORTLEE | Gortlee: T41∥T42 | Letterkenny |  | 54.9548 | -7.7523
MV/LV Substation TH***098Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.112 | 3.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.01615 | 0.1966 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge: T41 | Griffinrath |  | 53.345 | -6.5357
MV/LV Substation TH***098Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E20 ex LONGFORD | Longford: T422 | Richmond |  | 53.7413 | -7.8055
MV/LV Substation TH***099X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 3.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.04632 | 0 |  | --> | C20 ex OAKFIELD | Oakfield: T42 | Sligo |  | 54.3001 | -8.5802
MV/LV Substation TH***100X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.362 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.40004 | 0 |  | --> | C16 ex RAHANS | Rahans: T41 | Moy |  | 54.1075 | -9.1478
MV/LV Substation TH***100X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.166 | 3.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20537 | 0 |  | --> | C22 ex CASTLEREA | Castlerea: T41∥T42 | Carrick On Shannon |  | 53.8362 | -8.3808
MV/LV Substation TH***102 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.322 | 5.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C17 ex CHURCHTOWN | Churchtown: T41 | Rathkeale |  | 52.4507 | -9.0613
MV/LV Substation TH***102X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 11.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0534 | 0 |  | --> | C28 ex SALTHILL | Salthill: T102 | Salthill |  | 53.254 | -9.1608
MV/LV Substation TH***102X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CENTRAL PARK | Central Park: T102 | Carrickmines |  | 53.2774 | -6.2104
MV/LV Substation TH***102Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.177 | 10.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.19865 | 0 |  | --> | C23 ex PELLETSTOWN | Pelletstown: T101 | Finglas |  | 53.3697 | -6.3887
MV/LV Substation TH***103 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.294 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.04085 | 0.3736 | 0 |  | --> | C13 ex BRAY | Bray: T41 | Fassaroe |  | 53.1956 | -6.1173
MV/LV Substation TH***103Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.173 | 6.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.00665 | 0.19727 | 0 |  | --> | C13 ex CASHEL | Cashel: T41 | Cahir |  | 52.5175 | -7.8769
MV/LV Substation TH***104 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.175 | 6.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =204kW. | --> | E18 ex SPRINGS | Springs: T421∥T422 | Dungarvan |  | 52.0457 | -7.6582
MV/LV Substation TH***105Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.385 | 6.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4024 | 0 |  | --> | C13 ex CASHEL | Cashel: T41 | Cahir |  | 52.5168 | -7.8765
MV/LV Substation TH***106 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.326 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41166 | 0 |  | --> | C12 ex MOUNT MISERY | Mount Misery: T41 | Waterford |  | 52.2689 | -7.1045
MV/LV Substation TH***106 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.002 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1145 | 0 |  | --> | C15 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.8155 | -8.9634
MV/LV Substation TH***106Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.158 | 2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20661 | 0 |  | --> | C16 ex GRANGE (SR) | Grange (sr): T41∥T42 | Butlerstown |  | 52.2478 | -7.0847
MV/LV Substation TH***108X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C13 ex CHARLESTOWN | Charlestown: T41 | Tonroe |  | 53.9215 | -8.8494
MV/LV Substation TH***108Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =112kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0361 | 0.1756 | 0 |  | --> | C15 ex MALAHIDE | Malahide: T41 | Glasmore |  | 53.4324 | -6.1336
MV/LV Substation TH***108Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =317kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0 | 0 | Constrained,otherwise capacity available =398.1kW. | --> | C16 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.038 | -7.3211
MV/LV Substation TH***108Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E62 ex ATHY | Athy: T102 | Athy |  | 52.9992 | -6.954
MV/LV Substation TH***109Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =350kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40792 | 0 |  | --> | C12 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1613 | -6.9077
MV/LV Substation TH***111X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 12.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex TANEY | Taney: T101 | Carrickmines |  | 53.2863 | -6.2345
MV/LV Substation TH***112X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.362 | 12.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40604 | 0 |  | --> | C13 ex TANEY | Taney: T101 | Carrickmines |  | 53.2871 | -6.2361
MV/LV Substation TH***113X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 12.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex TANEY | Taney: T101 | Carrickmines |  | 53.2858 | -6.2357
MV/LV Substation TH***115X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.437 | 1.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex ABBEYFEALE | Abbeyfeale: T42 | Trien |  | 52.3849 | -9.3021
MV/LV Substation TH***115Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.096 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.0418 | 0.17197 | 0 |  | --> | C22 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.3341 | -6.536
MV/LV Substation TH***116 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.265 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.02945 | 0.39004 | 0 |  | --> | C12 ex DODDER ROAD | Dodder Road: T42 | Milltown (dr) |  | 53.3041 | -6.2599
MV/LV Substation TH***116X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.499 | 2.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0.01045 | 0.5 | 0 |  | --> | E20 ex STRANORLAR | Stranorlar: T422 | Letterkenny |  | 54.7931 | -7.7706
MV/LV Substation TH***117Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.287 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0247 | 0.39168 | 0 |  | --> | C22 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.876 | -8.5286
MV/LV Substation TH***118 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 3.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052647 | 0 |  | --> | C14 ex MCDONAGH | Mcdonagh: T42 | Kilkenny |  | 52.6463 | -7.2242
MV/LV Substation TH***118Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =141kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.19922 | 0 |  | --> | C19 ex LOUGHSHINNY | Loughshinny: T41 | Glasmore |  | 53.5787 | -6.1126
MV/LV Substation TH***119X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.108 | 0.1 | Constrained,otherwise capacity available =158kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20161 | 0 |  | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen: T41∥T42 | Tonroe |  | 53.907 | -8.5836
MV/LV Substation TH***121Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0114 | 0.5 | 0 |  | --> | C18 ex BALLYMAHON | Ballymahon: T41∥T42 | Athlone |  | 53.5591 | -7.7717
MV/LV Substation TH***122 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 4.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.9kW. | --> | E14 ex MOVILLE | Moville: T421∥T422 | Trillick |  | 55.1853 | -7.0547
MV/LV Substation TH***122Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.24 | 6.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0 | 0 | Constrained,otherwise capacity available =412.8kW. | --> | E12 ex RATHKEALE | Rathkeale: T421∥T422 | Rathkeale |  | 52.4731 | -8.8614
MV/LV Substation TH***123X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.18 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20318 | 0 |  | --> | E21 ex STRANORLAR | Stranorlar: T421 | Letterkenny |  | 54.7942 | -7.7831
MV/LV Substation TH***123Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | C16 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0887 | -7.3696
MV/LV Substation TH***123Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =127kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21135 | 0 |  | --> | C17 ex LUCAN EAST | Lucan East: T41∥T42 | Grange Castle |  | 53.3557 | -6.4521
MV/LV Substation TH***124 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.277 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.4052 | 0 |  | --> | C16 ex TYCOR | Tycor: T41∥T42 | Waterford |  | 52.2505 | -7.1422
MV/LV Substation TH***127X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.122 | 1.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.02185 | 0.1891 | 0 |  | --> | C17 ex TRABEG | Trabeg: T102 | Trabeg |  | 51.8676 | -8.4648
MV/LV Substation TH***127Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C14 ex CLONAKILTY | Clonakilty: T41∥T42 | Dunmanway |  | 51.5994 | -8.8723
MV/LV Substation TH***128Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =333kVA. | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.39058 | 0 |  | --> | C14 ex CLONAKILTY | Clonakilty: T41∥T42 | Dunmanway |  | 51.6165 | -8.9103
MV/LV Substation TH***128Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.087 | 8.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0475 | 0.16729 | 0 |  | --> | E18 ex BALTRASNA | Baltrasna: T122 | Baltrasna |  | 53.5014 | -6.4595
MV/LV Substation TH***129X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.164 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20568 | 0 |  | --> | C18 ex TUBBERCURRY | Tubbercurry: T42 | Tonroe |  | 54.0537 | -8.7116
MV/LV Substation TH***130 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard: T41 | Cookstown |  | 53.2933 | -6.3747
MV/LV Substation TH***131 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =330kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.40504 | 0 |  | --> | C15 ex LOUGHSHINNY | Loughshinny: T41 | Glasmore |  | 53.5229 | -6.0894
MV/LV Substation TH***131 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E12 ex OLDCASTLE | Oldcastle: T422 | Mullingar |  | 53.7252 | -7.0932
MV/LV Substation TH***131X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.276 | 3.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41936 | 0 |  | --> | C21 ex MOUNT MERRION | Mount Merrion: T41 | Carrickmines |  | 53.2997 | -6.2044
MV/LV Substation TH***131X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.125 | 0.1 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex MULGANNON | Mulgannon: T42 | Wexford |  | 52.3322 | -6.4584
MV/LV Substation TH***131Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =242kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0456 | 0.3765 | 0 |  | --> | E11 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4911 | -6.1352
MV/LV Substation TH***131Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.073 | 3.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.21033 | 0 |  | --> | C18 ex GRAIGUE | Graigue: T42 | Carlow |  | 52.8436 | -6.9476
MV/LV Substation TH***132Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =314kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0266 | 0.38552 | 0 |  | --> | C21 ex DOUGLAS | Douglas: T42 | Trabeg |  | 51.8755 | -8.3924
MV/LV Substation TH***133 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.126 | 7.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.0285 | 0.1815 | 0 |  | --> | C11 ex GARRYCASTLE | Garrycastle: T41 | Athlone |  | 53.4203 | -7.9081
MV/LV Substation TH***135 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.264 | 3.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.05605 | 0.36218 | 0 |  | --> | C14 ex SANDYFORD | Sandyford: T42 | Carrickmines |  | 53.2729 | -6.246
MV/LV Substation TH***135X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =349kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02185 | 0.38508 | 0 |  | --> | C17 ex CARRIGALINE | Carrigaline: T41∥T42 | Barnahely |  | 51.8148 | -8.375
MV/LV Substation TH***135Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.22 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.4118 | 0 |  | --> | C12 ex MONEYCOOLEY | Moneycooley: T42 | Griffinrath |  | 53.3489 | -6.5507
MV/LV Substation TH***135Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.364 | 8.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40572 | 0 |  | --> | C21 ex MULLINGAR | Mullingar: T101 | Mullingar |  | 53.526 | -7.3549
MV/LV Substation TH***135Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.022 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.0513 | 0.17254 | 0 |  | --> | C21 ex MARSHES | Marshes: T41 | Dundalk |  | 53.9601 | -6.3683
MV/LV Substation TH***135Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.281 | 0.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4186 | 0 |  | --> | C21 ex MONEYCOOLEY | Moneycooley: T41 | Griffinrath |  | 53.3803 | -6.5921
MV/LV Substation TH***137Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 4.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.1kW. | --> | E13 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.2748 | -7.0723
MV/LV Substation TH***138Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.385 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4024 | 0 |  | --> | C11 ex GRAIGUE | Graigue: T41 | Carlow |  | 52.8311 | -6.9246
MV/LV Substation TH***138Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =108kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0228 | 0.1902 | 0 |  | --> | C13 ex BALGADDY | Balgaddy: T41 | Grange Castle |  | 53.3389 | -6.4469
MV/LV Substation TH***139X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex BAILIEBORO | Bailieboro: T41∥T42 | Meath Hill |  | 53.9156 | -6.9691
MV/LV Substation TH***139Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C11 ex SMEARLA | Smearla: T41 | Trien |  | 52.4431 | -9.4826
MV/LV Substation TH***140X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.306 | 3.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.40276 | 0 |  | --> | C15 ex BOYLE | Boyle: T41∥T42 | Carrick On Shannon |  | 53.9745 | -8.2815
MV/LV Substation TH***141Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =180kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.19318 | 0 |  | --> | C35 ex CASTLEVIEW | Castleview: T101 | Castleview |  | 51.8972 | -8.3461
MV/LV Substation TH***142X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0019 | 0.5 | 0 |  | --> | C13 ex LOUGHLINSTOWN | Loughlinstown: T41 | Carrickmines |  | 53.2575 | -6.1141
MV/LV Substation TH***142X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex ROCHES STREET | Roches Street: T41 | Limerick |  | 52.662 | -8.6308
MV/LV Substation TH***144Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.298 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.02945 | 0.385 | 0 |  | --> | C24 ex TINAHASK | Tinahask: T41∥T42 | Arklow |  | 52.7857 | -6.166
MV/LV Substation TH***145X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.108 | 0.1 | Constrained,otherwise capacity available =330kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41104 | 0 |  | --> | C11 ex BALLAGHADERREEN | Ballaghaderreen: T41∥T42 | Tonroe |  | 53.8993 | -8.5731
MV/LV Substation TH***146X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.01 | 3.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.056007 | 0 |  | --> | C18 ex SHERCOCK | Shercock: T41∥T42 | Meath Hill |  | 53.998 | -6.8908
MV/LV Substation TH***147Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex ROCHES STREET | Roches Street: T42 | Limerick |  | 52.6633 | -8.6287
MV/LV Substation TH***148Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.311 | 7.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.403 | 0 |  | --> | E41 ex KINSALE | Kinsale: T423 | Bandon |  | 51.7022 | -8.5293
MV/LV Substation TH***150 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =55kVA. | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =101.9kW. | --> | E13 ex ABBEYLEIX | Abbeyleix: T422 | Portlaoise |  | 52.9103 | -7.3347
MV/LV Substation TH***150X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =106kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.20849 | 0 |  | --> | E15 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.5035 | -6.4005
MV/LV Substation TH***151Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 1.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10095 | 0 |  | --> | C22 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.3361 | -6.5434
MV/LV Substation TH***151Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | E12 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 53.0177 | -7.1504
MV/LV Substation TH***153 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =157kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =437.1kW. | --> | C12 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.0904 | -7.6197
MV/LV Substation TH***157X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.055 | 2.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =106.9kW. | --> | E17 ex BALLYMACARRY | Ballymacarry: T421 | Trillick |  | 55.0829 | -7.4565
MV/LV Substation TH***158 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =159kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20145 | 0 |  | --> | C12 ex CRANMORE | Cranmore: T41∥T42 | Sligo |  | 54.259 | -8.4626
MV/LV Substation TH***159 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex MANOR STREET | Manor Street: T41 | Waterford |  | 52.2591 | -7.1067
MV/LV Substation TH***159X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 2.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =104.4kW. | --> | E17 ex LISDRUM | Lisdrum: T422 | Lisdrum |  | 54.2158 | -7.0429
MV/LV Substation TH***163 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.032 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.11031 | 0 |  | --> | E19 ex LAWLESSTOWN | Lawlesstown: T421 | Doon |  | 52.4688 | -7.6905
MV/LV Substation TH***163Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05142 | 0 |  | --> | C14 ex CASHEL | Cashel: T42 | Cahir |  | 52.5682 | -7.8918
MV/LV Substation TH***166 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.14 | 8.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.019 | 0.18938 | 0 |  | --> | C17 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9472 | -6.0246
MV/LV Substation TH***166Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =166kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20137 | 0 |  | --> | C18 ex HEADFORD | Headford: T42 | Cloon |  | 53.4699 | -9.0982
MV/LV Substation TH***167X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =177kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | C19 ex MILFORD (NR) | Milford (nr): T41∥T42 | Letterkenny |  | 55.0944 | -7.5425
MV/LV Substation TH***168X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex CASTLEREA | Castlerea: T41∥T42 | Carrick On Shannon |  | 53.7692 | -8.4959
MV/LV Substation TH***169 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.145 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0 | 0 | Constrained,otherwise capacity available =205.6kW. | --> | C11 ex LEE BRIDGE | Lee Bridge: T41 | Macroom |  | 51.9046 | -8.9465
MV/LV Substation TH***169X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 3.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.046345 | 0 |  | --> | C15 ex BOYLE | Boyle: T41∥T42 | Carrick On Shannon |  | 53.9814 | -8.2921
MV/LV Substation TH***169X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =27kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05355 | 0 |  | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9554 | -8.0884
MV/LV Substation TH***170Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =286kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.40684 | 0 |  | --> | C22 ex MIDLETON | Midleton: T102 | Midleton |  | 51.9043 | -8.1696
MV/LV Substation TH***171 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.387 | 5.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex POTTERY ROAD | Pottery Road: T101 | Carrickmines |  | 53.2764 | -6.139
MV/LV Substation TH***171X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.145 | 3.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.01995 | 0.18761 | 0 |  | --> | C20 ex MARSHES | Marshes: T42 | Dundalk |  | 53.9679 | -6.3696
MV/LV Substation TH***172Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =178kVA. | --> | 0.19 | 0 | 0 | 0 | 0.019 | 0.18349 | 0 |  | --> | C16 ex BALLINACURRA | Ballinacurra: T42 | Limerick |  | 52.632 | -8.6372
MV/LV Substation TH***175X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.179 | 1.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =203.3kW. | --> | E14 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1454 | -7.4535
MV/LV Substation TH***175Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.307 | 3.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4146 | 0 |  | --> | C19 ex ERRIGAL | Errigal: T41 | Shankill |  | 54.0734 | -7.0797
MV/LV Substation TH***175Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex BALLINACURRA | Ballinacurra: T41 | Limerick |  | 52.66 | -8.637
MV/LV Substation TH***177X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C23 ex SRAH | Srah: T43 | Thornsberry |  | 53.2954 | -7.4712
MV/LV Substation TH***177X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 2.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052345 | 0 |  | --> | C17 ex MOUNTGORRY | Mountgorry: T41 | Grange (dr) |  | 53.4543 | -6.1718
MV/LV Substation TH***177Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.167 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20521 | 0 |  | --> | C17 ex ROOSKY | Roosky: T41 | Richmond |  | 53.7744 | -8.1163
MV/LV Substation TH***178Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.196 | 3.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20064 | 0 |  | --> | C16 ex TRAMORE | Tramore: T42 | Butlerstown |  | 52.164 | -7.144
MV/LV Substation TH***179Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C26 ex MONEYCOOLEY | Moneycooley: T44 | Griffinrath |  | 53.3787 | -6.6251
MV/LV Substation TH***179Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C12 ex BANDON | Bandon: T101 | Bandon |  | 51.7466 | -8.7374
MV/LV Substation TH***179Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.357 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40682 | 0 |  | --> | E20 ex LONGFORD | Longford: T422 | Richmond |  | 53.7416 | -7.8037
MV/LV Substation TH***181Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.312 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0247 | 0.38784 | 0 |  | --> | C25 ex TRAMORE | Tramore: T41 | Butlerstown |  | 52.156 | -7.163
MV/LV Substation TH***184X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELFIELD | Belfield: T41 | Blackrock |  | 53.3145 | -6.2079
MV/LV Substation TH***184Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =419kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.00665 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C18 ex RAMSTOWN | Ramstown: T41∥T42 | Crane |  | 52.6742 | -6.2958
MV/LV Substation TH***185X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELFIELD | Belfield: T41 | Blackrock |  | 53.3145 | -6.2079
MV/LV Substation TH***186 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | C18 ex BALLYMOTE | Ballymote: T41 | Sligo |  | 54.0866 | -8.5086
MV/LV Substation TH***186X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.1 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELFIELD | Belfield: T41 | Blackrock |  | 53.313 | -6.2071
MV/LV Substation TH***186X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =381kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.38904 | 0 |  | --> | C13 ex SPIDDAL | Spiddal: T42 | Screeb |  | 53.2488 | -9.2166
MV/LV Substation TH***186Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =110kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2139 | 0 |  | --> | C11 ex MORRISTOWN | Morristown: T41∥T42 | Newbridge |  | 53.1715 | -6.8159
MV/LV Substation TH***187X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.374 | 0.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =404.1kW. | --> | C18 ex ATHBOY | Athboy: T42 | Navan |  | 53.6208 | -6.9203
MV/LV Substation TH***187Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C11 ex CARRIGALINE | Carrigaline: T41∥T42 | Barnahely |  | 51.8282 | -8.3495
MV/LV Substation TH***189 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =177kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | C11 ex BALLINACURRA | Ballinacurra: T41 | Limerick |  | 52.6596 | -8.6387
MV/LV Substation TH***191Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =112kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01615 | 0.1966 | 0 |  | --> | C23 ex MACETOWN | Macetown: T101 | Macetown |  | 53.423 | -6.4742
MV/LV Substation TH***192 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C15 ex MALAHIDE | Malahide: T41 | Glasmore |  | 53.4154 | -6.1274
MV/LV Substation TH***192X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex CASTLEREA | Castlerea: T41∥T42 | Carrick On Shannon |  | 53.7699 | -8.4958
MV/LV Substation TH***195 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =266kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00665 | 0.41388 | 0 |  | --> | C11 ex MORRISTOWN | Morristown: T41∥T42 | Newbridge |  | 53.1745 | -6.8129
MV/LV Substation TH***195Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =132kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20659 | 0 |  | --> | C11 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.6701 | -7.8061
MV/LV Substation TH***196 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.161 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20614 | 0 |  | --> | C15 ex SCARTEEN | Scarteen: T41∥T42 | Mallow |  | 52.1137 | -8.663
MV/LV Substation TH***197X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.282 | 6.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.41544 | 0 |  | --> | C18 ex CARRICKMINES | Carrickmines: T42 | Carrickmines |  | 53.2561 | -6.2184
MV/LV Substation TH***199 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.268 | 1.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex FAIRHILL | Fairhill: T42 | Kilbarry |  | 51.9015 | -8.4676
MV/LV Substation TH***200X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.291 | 3.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.03895 | 0.37606 | 0 |  | --> | C20 ex MARSHES | Marshes: T42 | Dundalk |  | 53.9688 | -6.3649
MV/LV Substation TH***202X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =330kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.39904 | 0 |  | --> | E16 ex PATRICKSWELL | Patrickswell: T421∥T422 | Limerick |  | 52.5578 | -8.7904
MV/LV Substation TH***202Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C16 ex CLONES | Clones: T41∥T42 | Shankill |  | 54.1789 | -7.234
MV/LV Substation TH***202Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =300kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.40968 | 0 |  | --> | C21 ex MALAHIDE | Malahide: T41 | Glasmore |  | 53.4511 | -6.1525
MV/LV Substation TH***203Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =316kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0323 | 0.37922 | 0 |  | --> | C15 ex LOUGHSHINNY | Loughshinny: T41 | Glasmore |  | 53.5341 | -6.0934
MV/LV Substation TH***204X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.127 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.07125 | 0.13635 | 0 |  | --> | C11 ex ROSSGEIR | Rossgeir: T41∥T42 | Letterkenny |  | 54.8173 | -7.5123
MV/LV Substation TH***207 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.15 | 8.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0247 | 0.18184 | 0 |  | --> | C17 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.971 | -6.0263
MV/LV Substation TH***207Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CLONAKILTY | Clonakilty: T41∥T42 | Dunmanway |  | 51.6216 | -8.8832
MV/LV Substation TH***208 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.188 | 8.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0133 | 0.18791 | 0 |  | --> | C25 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9831 | -6.0598
MV/LV Substation TH***208 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.117 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.44282 | 0 |  | --> | C13 ex INCHICORE NORTH | Inchicore North: T41 | Inchicore 110kv |  | 53.3408 | -6.3476
MV/LV Substation TH***208X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.365 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40556 | 0 |  | --> | C16 ex LITTLE BRAY | Little Bray: T42 | Fassaroe |  | 53.2391 | -6.1314
MV/LV Substation TH***208X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.258 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0247 | 0.3961 | 0 |  | --> | C15 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5642 | -6.8017
MV/LV Substation TH***209 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =112kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.2036 | 0 |  | --> | C16 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6648 | -7.2626
MV/LV Substation TH***209 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =88kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101.9kW. | --> | C16 ex TOOMEVARA | Toomevara: T42 | Nenagh |  | 52.8567 | -7.946
MV/LV Substation TH***209X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.423 | 4.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BALLYRICKARD | Ballyrickard: T41∥T42 | Tralee |  | 52.2677 | -9.7073
MV/LV Substation TH***210 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =159kVA. | --> | 0.19 | 0 | 0 | 0 | 0.02755 | 0.17745 | 0 |  | --> | C39 ex CASTLEVIEW | Castleview: T101 | Castleview |  | 51.9033 | -8.3506
MV/LV Substation TH***211Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =174kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20412 | 0 |  | --> | C17 ex RATHMULLAN | Rathmullan: T41 | Drybridge |  | 53.7156 | -6.3717
MV/LV Substation TH***212Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =260kVA. | --> | 0.38 | 0 | 0 | 0 | 0.04655 | 0.3728 | 0 |  | --> | C13 ex DOCK ROAD | Dock Road: T41∥T42 | Limerick |  | 52.6297 | -8.6664
MV/LV Substation TH***212Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.13 | 7.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.02375 | 0 | 0 | Constrained,otherwise capacity available =185.9kW. | --> | E11 ex DUNFIRTH | Dunfirth: T122 | Dunfirth |  | 53.4001 | -6.8595
MV/LV Substation TH***214X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.146 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20846 | 0 |  | --> | C12 ex KILSARAN | Kilsaran: T42 | Drybridge |  | 53.8834 | -6.3452
MV/LV Substation TH***218X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.336 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41012 | 0 |  | --> | C16 ex DUNLEER | Dunleer: T41∥T42 | Drybridge |  | 53.8329 | -6.3935
MV/LV Substation TH***225 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =362kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40604 | 0 |  | --> | E18 ex BIRDHILL | Birdhill: T422 | Ardnacrusha |  | 52.7194 | -8.4992
MV/LV Substation TH***226Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.334 | 4.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41042 | 0 |  | --> | C17 ex GLEBE | Glebe: T41∥T42 | Richmond |  | 53.7187 | -7.7908
MV/LV Substation TH***227X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.114 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.01425 | 0 | 0 | Constrained,otherwise capacity available =198.3kW. | --> | E23 ex ATHBOY | Athboy: T423 | Navan |  | 53.5342 | -6.9585
MV/LV Substation TH***228X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.136 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0.04845 | 0.15898 | 0 |  | --> | C11 ex MANOR STREET | Manor Street: T41 | Waterford |  | 52.2524 | -7.0698
MV/LV Substation TH***228X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.067 | 4.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10515 | 0 |  | --> | C20 ex CASTLEBLAYNEY | Castleblayney: T42 | Dundalk |  | 54.1155 | -6.7459
MV/LV Substation TH***231Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.188 | 2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20191 | 0 |  | --> | C12 ex GRANGE (SR) | Grange (sr): T41∥T42 | Butlerstown |  | 52.2412 | -7.1137
MV/LV Substation TH***231Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C13 ex MULLINGAR | Mullingar: T101 | Mullingar |  | 53.5732 | -7.3258
MV/LV Substation TH***232X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.286 | 4.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41784 | 0 |  | --> | C13 ex MONEENAGEISHA | Moneenageisha: T41 | Galway 110kv |  | 53.2798 | -9.0372
MV/LV Substation TH***235X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.059 | 1.5 |  | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.10135 | 0 |  | --> | C24 ex CAHIR | Cahir: T42 | Cahir |  | 52.4407 | -7.8815
MV/LV Substation TH***235Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | E12 ex KILCULLEN | Kilcullen: T424 | Stratford |  | 53.0905 | -6.8069
MV/LV Substation TH***236X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.176 | 4.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.1988 | 0 |  | --> | E20 ex ENNISCRONE | Enniscrone: T421∥T422 | Moy |  | 54.2129 | -9.0802
MV/LV Substation TH***236X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex DUN LAOGHAIRE | Dun Laoghaire: T42 | Blackrock |  | 53.2944 | -6.1406
MV/LV Substation TH***236X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.179 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0.20133 | 0 |  | --> | C12 ex DUNLEER | Dunleer: T41∥T42 | Drybridge |  | 53.7939 | -6.2401
MV/LV Substation TH***237 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.167 | 4.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0 | 0 | Constrained,otherwise capacity available =194.2kW. | --> | E12 ex MOVILLE | Moville: T421∥T422 | Trillick |  | 55.2055 | -6.9919
MV/LV Substation TH***239 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | E33 ex TRIM | Trim: T421 | Navan |  | 53.4706 | -6.7491
MV/LV Substation TH***241X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 3.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C19 ex CAUSEWAY | Causeway: T41∥T42 | Tralee |  | 52.4008 | -9.8023
MV/LV Substation TH***242X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.101 | 2 |  | --> | 0.19 | 0 | 0 | 0 | 0.03325 | 0.18024 | 0 |  | --> | C12 ex GRANGE (SR) | Grange (sr): T41∥T42 | Butlerstown |  | 52.243 | -7.1006
MV/LV Substation TH***243X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.134 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.01805 | 0.19129 | 0 |  | --> | C12 ex DUNLEER | Dunleer: T41∥T42 | Drybridge |  | 53.7891 | -6.2454
MV/LV Substation TH***244X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex HOWTH JUNCTION | Howth Junction: T41 | Grange (dr) |  | 53.3762 | -6.1663
MV/LV Substation TH***245X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.169 | 3.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =204.9kW. | --> | E14 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 51.955 | -7.8561
MV/LV Substation TH***245Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =134kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21029 | 0 |  | --> | C14 ex NAAS | Naas: T42 | Newbridge |  | 53.2182 | -6.666
MV/LV Substation TH***251 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.124 | 2 |  | --> | 0.19 | 0 | 0 | 0 | 0.019 | 0.1918 | 0 |  | --> | C16 ex CAPPAMORE | Cappamore: T41∥T42 | Ardnacrusha |  | 52.5827 | -8.1631
MV/LV Substation TH***254X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | E19 ex KILCOCK | Kilcock: T421 | Griffinrath |  | 53.3888 | -6.7003
MV/LV Substation TH***255X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.382 | 7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex WATLING STREET | Watling Street: T41 | Francis Street |  | 53.3458 | -6.2837
MV/LV Substation TH***255Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =231kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42616 | 0 |  | --> | C21 ex MALAHIDE | Malahide: T41 | Glasmore |  | 53.4518 | -6.1531
MV/LV Substation TH***257Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052647 | 0 |  | --> | C17 ex ROOSKY | Roosky: T41 | Richmond |  | 53.7747 | -8.0945
MV/LV Substation TH***258Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =132kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0228 | 0 | 0 | Constrained,otherwise capacity available =186.6kW. | --> | C15 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0421 | -7.2871
MV/LV Substation TH***258Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.15 | 0.2 | Constrained,otherwise capacity available =165kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20552 | 0 |  | --> | C11 ex COOLMINE | Coolmine: T41 | Finglas |  | 53.3769 | -6.3925
MV/LV Substation TH***259 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 3.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10268 | 0 |  | --> | C19 ex CASTLEBLAYNEY | Castleblayney: T41 | Dundalk |  | 54.1129 | -6.7535
MV/LV Substation TH***261 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.11 | 0.1 | Constrained,otherwise capacity available =159kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20645 | 0 |  | --> | C15 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.5146 | -8.8657
MV/LV Substation TH***261 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =30kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0531 | 0 |  | --> | C21 ex LITTLE BRAY | Little Bray: T41 | Fassaroe |  | 53.2193 | -6.1465
MV/LV Substation TH***262 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C15 ex KILTIMAGH | Kiltimagh: T41 | Castlebar |  | 53.8468 | -8.9982
MV/LV Substation TH***262X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.303 | 5.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41522 | 0 |  | --> | E12 ex CLARA | Clara: T422 | Thornsberry |  | 53.3629 | -7.4971
MV/LV Substation TH***262X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 5.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C18 ex ARDNAREE | Ardnaree: T42 | Moy |  | 54.103 | -9.1433
MV/LV Substation TH***262Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =194kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0076 | 0.19296 | 0 |  | --> | E11 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.533 | -6.5811
MV/LV Substation TH***263 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.391 | 3.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C20 ex OAKFIELD | Oakfield: T42 | Sligo |  | 54.2712 | -8.6076
MV/LV Substation TH***263Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C15 ex MOUNTGORRY | Mountgorry: T41 | Grange (dr) |  | 53.4624 | -6.2171
MV/LV Substation TH***263Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =190kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.1916 | 0 |  | --> | E11 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.537 | -6.5837
MV/LV Substation TH***264Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =28kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =53.4kW. | --> | E15 ex BEALISTOWN | Bealistown: T421 | Great Island |  | 52.269 | -6.7536
MV/LV Substation TH***268Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.34 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.39748 | 0 |  | --> | E15 ex BALLYCONNELL | Ballyconnell: T421∥T422 | Gortawee |  | 54.0898 | -7.4612
MV/LV Substation TH***271 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.39433 | 0 | Constrained,otherwise capacity available =500kW. | --> | C14 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.6747 | -7.821
MV/LV Substation TH***271X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0133 | 0.5 | 0 |  | --> | C12 ex CAHERDAVIN | Caherdavin: T42 | Ardnacrusha |  | 52.6621 | -8.6545
MV/LV Substation TH***271Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =332kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.39174 | 0 |  | --> | C17 ex BALLYGAR | Ballygar: T41 | Athlone |  | 53.487 | -8.5624
MV/LV Substation TH***273 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.189 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20176 | 0 |  | --> | C11 ex CHARLESTOWN | Charlestown: T41 | Tonroe |  | 53.9573 | -8.8084
MV/LV Substation TH***273Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.331 | 0.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4109 | 0 |  | --> | C20 ex RATHMULLAN | Rathmullan: T42 | Drybridge |  | 53.7052 | -6.374
MV/LV Substation TH***275X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.099 | 6.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0228 | 0.19153 | 0 |  | --> | C22 ex PELLETSTOWN | Pelletstown: T102 | Finglas |  | 53.3764 | -6.372
MV/LV Substation TH***275Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =372kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40446 | 0 |  | --> | C15 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7186 | -6.3329
MV/LV Substation TH***275Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.168 | 0.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.0361 | 0 | 0 | Constrained,otherwise capacity available =167.1kW. | --> | E16 ex KILMACTHOMAS | Kilmacthomas: T421∥T422 | Dungarvan |  | 52.1342 | -7.4589
MV/LV Substation TH***277X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052345 | 0 |  | --> | C16 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9347 | -8.1093
MV/LV Substation TH***279X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.133 | 4.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.02565 | 0.18344 | 0 |  | --> | C17 ex CASTLEKNOCK | Castleknock: T41∥T42 | Finglas |  | 53.3771 | -6.3761
MV/LV Substation TH***279Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.173 | 2.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =199.3kW. | --> | C19 ex NEWCASTLEWEST | Newcastlewest: T41∥T42 | Rathkeale |  | 52.4169 | -9.0844
MV/LV Substation TH***280 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.132 | 4.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21059 | 0 |  | --> | C15 ex MAYFIELD | Mayfield: T41 | Kilbarry |  | 51.9186 | -8.4177
MV/LV Substation TH***280X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.178 | 7.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20349 | 0 |  | --> | C13 ex GARRYCASTLE | Garrycastle: T41 | Athlone |  | 53.4283 | -7.93
MV/LV Substation TH***282Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.169 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2049 | 0 |  | --> | C11 ex SMEARLA | Smearla: T41 | Trien |  | 52.4419 | -9.4854
MV/LV Substation TH***284 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =57kVA. | --> | 0.095 | 0 | 0 | 0 | 0.019 | 0.08665 | 0 |  | --> | E11 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.3396 | -7.0785
MV/LV Substation TH***284X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.315 | 8.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41338 | 0 |  | --> | C14 ex GORTLEE | Gortlee: T41∥T42 | Letterkenny |  | 54.9635 | -7.7611
MV/LV Substation TH***285Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C13 ex BANDON | Bandon: T101 | Bandon |  | 51.7497 | -8.7479
MV/LV Substation TH***286 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C12 ex CHARLESTOWN | Charlestown: T41 | Tonroe |  | 54.0005 | -8.777
MV/LV Substation TH***287Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =493kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0076 | 0.5 | 0 |  | --> | C11 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1412 | -7.0566
MV/LV Substation TH***289Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =80kVA. | --> | 0.19 | 0 | 0 | 0 | 0.08645 | 0.12731 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.6977 | -6.257
MV/LV Substation TH***289Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =354kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4073 | 0 |  | --> | E18 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.5116 | -7.1418
MV/LV Substation TH***290X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.349 | 5.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.40308 | 0 |  | --> | C11 ex KILFLYNN | Kilflynn: T41∥T42 | Tralee |  | 52.3498 | -9.6863
MV/LV Substation TH***290Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.403 | 1.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin: T42 | Inchicore 110kv |  | 53.3242 | -6.3941
MV/LV Substation TH***291 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.9kW. | --> | E17 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1398 | -7.4344
MV/LV Substation TH***291X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.124 | 6.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.01995 | 0.1908 | 0 |  | --> | C22 ex PELLETSTOWN | Pelletstown: T102 | Finglas |  | 53.376 | -6.3762
MV/LV Substation TH***293X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C12 ex ABBEYFEALE | Abbeyfeale: T42 | Trien |  | 52.3701 | -9.3028
MV/LV Substation TH***293Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin: T42 | Inchicore 110kv |  | 53.3241 | -6.3941
MV/LV Substation TH***294X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.336 | 4.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41012 | 0 |  | --> | C11 ex HOWTH JUNCTION | Howth Junction: T41 | Grange (dr) |  | 53.3756 | -6.1635
MV/LV Substation TH***294Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =94kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101kW. | --> | C13 ex CLOYNE | Cloyne: T41 | Midleton |  | 51.8298 | -8.0164
MV/LV Substation TH***296X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | E20 ex ROSCREA | Roscrea: T42 | Ikerrin |  | 52.9272 | -7.7419
MV/LV Substation TH***296Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 3.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20176 | 0 |  | --> | E16 ex ASHBOURNE | Ashbourne: T422 | Finglas |  | 53.5177 | -6.4081
MV/LV Substation TH***297X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.014 | 0 | Constrained,otherwise capacity available =293kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0513 | 0.36276 | 0 |  | --> | C21 ex CASTLETROY | Castletroy: T41∥T42 | Ardnacrusha |  | 52.6594 | -8.555
MV/LV Substation TH***298X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.095 | 0.1 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.01045 | 0.5 | 0 |  | --> | C21 ex CASTLEISLAND | Castleisland: T41∥T42 | Tralee |  | 52.226 | -9.4677
MV/LV Substation TH***299Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.36 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.39736 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.8311 | -6.9023
MV/LV Substation TH***300Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.288 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41752 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.8303 | -6.9019
MV/LV Substation TH***301X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 6.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex CARRICKMINES | Carrickmines: T42 | Carrickmines |  | 53.2611 | -6.2238
MV/LV Substation TH***305 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | C13 ex SWINFORD | Swinford: T41∥T42 | Castlebar |  | 53.8911 | -9.101
MV/LV Substation TH***307 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =257kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0418 | 0.37824 | 0 |  | --> | C15 ex LITTLE BRAY | Little Bray: T41 | Fassaroe |  | 53.214 | -6.1096
MV/LV Substation TH***308Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =115kVA. | --> | 0.19 | 0 | 0 | 0 | 0.04085 | 0.17015 | 0 |  | --> | C15 ex MALAHIDE | Malahide: T41 | Glasmore |  | 53.4217 | -6.1307
MV/LV Substation TH***309 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =172kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20443 | 0 |  | --> | E47 ex CLAREGALWAY | Claregalway: T421 | Galway 110kv |  | 53.436 | -8.7473
MV/LV Substation TH***309Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =114kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2133 | 0 |  | --> | C22 ex MIDLETON | Midleton: T102 | Midleton |  | 51.9014 | -8.163
MV/LV Substation TH***311 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052345 | 0 |  | --> | C15 ex SAGGART | Saggart: T41∥T42 | Grange Castle |  | 53.2746 | -6.4409
MV/LV Substation TH***311X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9453 | -8.0945
MV/LV Substation TH***311Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex GRAIGUE | Graigue: T42 | Carlow |  | 52.837 | -6.9315
MV/LV Substation TH***312Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.154 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.019 | 0 | 0 | Constrained,otherwise capacity available =187.2kW. | --> | C11 ex LEE BRIDGE | Lee Bridge: T41 | Macroom |  | 51.91 | -8.9782
MV/LV Substation TH***315Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 6.7 |  | --> | 0.095 | 0 | 0 | 0 | 0.0038 | 0 | 0 | Constrained,otherwise capacity available =97.6kW. | --> | E17 ex SPRINGS | Springs: T421∥T422 | Dungarvan |  | 52.0951 | -7.6388
MV/LV Substation TH***316Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex GRANGE (DR) | Grange (dr): T41 | Grange (dr) |  | 53.3977 | -6.1803
MV/LV Substation TH***316Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =77kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10361 | 0 |  | --> | C21 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7625 | -6.2622
MV/LV Substation TH***317X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.061 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10605 | 0 |  | --> | E11 ex BALLYHALE | Ballyhale: T421 | Kilkenny |  | 52.5236 | -7.1327
MV/LV Substation TH***317Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20176 | 0 |  | --> | C12 ex BALBRIGGAN | Balbriggan: T42 | Glasmore |  | 53.5911 | -6.1879
MV/LV Substation TH***320 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 5.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BALLINCOLLIG | Ballincollig: T41 | Kilbarry |  | 51.8837 | -8.5918
MV/LV Substation TH***320Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.373 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.3993 | 0 |  | --> | C13 ex SMEARLA | Smearla: T41 | Trien |  | 52.4552 | -9.4697
MV/LV Substation TH***322X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.168 | 6.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.19606 | 0 |  | --> | C14 ex CARRICKMINES | Carrickmines: T42 | Carrickmines |  | 53.2602 | -6.2153
MV/LV Substation TH***324 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.021 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.054432 | 0 |  | --> | E16 ex BALLYCROSSAUN | Ballycrossaun: T421∥T422 | Somerset |  | 53.0888 | -8.1891
MV/LV Substation TH***325X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 12.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex TANEY | Taney: T101 | Carrickmines |  | 53.2795 | -6.2125
MV/LV Substation TH***326X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.059 | 0.6 |  | --> | 0.095 | 0 | 0 | 0 | 0.0171 | 0.08835 | 0 |  | --> | E31 ex TRIM | Trim: T421 | Navan |  | 53.5734 | -6.9075
MV/LV Substation TH***326X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 12.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex TANEY | Taney: T101 | Carrickmines |  | 53.2794 | -6.2125
MV/LV Substation TH***328 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =333kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =410.6kW. | --> | C14 ex DRUMBEAR | Drumbear: T41∥T42 | Lisdrum |  | 54.249 | -6.9676
MV/LV Substation TH***329 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.248 | 3.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0437 | 0.3776 | 0 |  | --> | C19 ex MOUNT MERRION | Mount Merrion: T41 | Carrickmines |  | 53.2997 | -6.2082
MV/LV Substation TH***331 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 1.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10315 | 0 |  | --> | E12 ex CONG | Cong: T421∥T422 | Cloon |  | 53.5269 | -9.3799
MV/LV Substation TH***332 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =342kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.39433 | 0 | Constrained,otherwise capacity available =409.2kW. | --> | C14 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.6732 | -7.8211
MV/LV Substation TH***332X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.351 | 6.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0.39476 | 0 |  | --> | C18 ex AGHAGAD | Aghagad: T41∥T42 | Sligo |  | 54.3939 | -8.5265
MV/LV Substation TH***335X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 8.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0209 | 0.5 | 0 |  | --> | C13 ex GORTLEE | Gortlee: T41∥T42 | Letterkenny |  | 54.9729 | -7.7251
MV/LV Substation TH***335Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =282kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0.40544 | 0 |  | --> | C20 ex RAHEEN | Raheen: T42 | Limerick |  | 52.6276 | -8.6455
MV/LV Substation TH***338X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.077 | 3.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10361 | 0 |  | --> | C19 ex CAUSEWAY | Causeway: T41∥T42 | Tralee |  | 52.3924 | -9.8424
MV/LV Substation TH***338X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.25 | 6.8 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex CARRICKMINES | Carrickmines: T42 | Carrickmines |  | 53.2508 | -6.1833
MV/LV Substation TH***340X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CENTRAL PARK | Central Park: T102 | Carrickmines |  | 53.2774 | -6.2102
MV/LV Substation TH***341X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.145 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0.04275 | 0.16361 | 0 |  | --> | C15 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5516 | -6.8021
MV/LV Substation TH***341Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.5058 | -6.2047
MV/LV Substation TH***342 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 53.0018 | -6.6351
MV/LV Substation TH***344Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.44613 | 0 | Constrained,otherwise capacity available =500kW. | --> | C18 ex BALLYCOOLIN | Ballycoolin: T42 | Finglas |  | 53.4026 | -6.3683
MV/LV Substation TH***345 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =291kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =407.1kW. | --> | C13 ex CLOYNE | Cloyne: T41 | Midleton |  | 51.8295 | -8.0132
MV/LV Substation TH***345Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.172 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20443 | 0 |  | --> | C16 ex BALBRIGGAN | Balbriggan: T42 | Glasmore |  | 53.6104 | -6.1799
MV/LV Substation TH***347 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =149kVA. | --> | 0.19 | 0 | 0 | 0 | 0.03325 | 0.173 | 0 |  | --> | C21 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7659 | -6.2611
MV/LV Substation TH***347X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central: T45 | Inchicore 110kv |  | 53.3378 | -6.3201
MV/LV Substation TH***351X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.18 | 2.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20318 | 0 |  | --> | C16 ex MALAHIDE | Malahide: T42 | Glasmore |  | 53.4397 | -6.1243
MV/LV Substation TH***352 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 3.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.8kW. | --> | C12 ex TELAYDON | Telaydon: T42 | Lisdrum |  | 54.2675 | -6.959
MV/LV Substation TH***354X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =169kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.1959 | 0 |  | --> | C19 ex MALAHIDE | Malahide: T41 | Glasmore |  | 53.4535 | -6.1629
MV/LV Substation TH***355X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =29kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.04825 | 0 |  | --> | E24 ex BIRR | Birr: T422 | Dallow |  | 53.1389 | -7.8079
MV/LV Substation TH***357Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0076 | 0.04295 | 0 |  | --> | E17 ex DULEEK | Duleek: T421∥T422 | Drybridge |  | 53.6322 | -6.4814
MV/LV Substation TH***358X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.492 | 8.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex RINGSEND | Ringsend: T102 | Poolbeg |  | 53.3446 | -6.2285
MV/LV Substation TH***358Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.01045 | 0.5 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge: T41 | Griffinrath |  | 53.3412 | -6.5364
MV/LV Substation TH***358Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =329kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.4022 | 0 |  | --> | E17 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4459 | -6.2444
MV/LV Substation TH***359Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =286kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.41384 | 0 |  | --> | E17 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4458 | -6.2428
MV/LV Substation TH***360 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.477 | 4.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0247 | 0.5 | 0 |  | --> | C22 ex HOWTH JUNCTION | Howth Junction: T42 | Grange (dr) |  | 53.3878 | -6.1541
MV/LV Substation TH***361X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.093 | 6.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0133 | 0.20241 | 0 |  | --> | C22 ex PELLETSTOWN | Pelletstown: T102 | Finglas |  | 53.3788 | -6.371
MV/LV Substation TH***362X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6.8 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex HAROLDS CROSS | Harolds Cross: T102 | Poolbeg |  | 53.333 | -6.2623
MV/LV Substation TH***363Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex WATERFORD | Waterford: T41 | Waterford |  | 52.2636 | -7.1205
MV/LV Substation TH***365 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 4 |  | --> | 0.095 | 0 | 0 | 0 | 0.01045 | 0.10709 | 0 |  | --> | C12 ex ROSS CARBERY | Ross Carbery: T41∥T42 | Dunmanway |  | 51.5776 | -9.0273
MV/LV Substation TH***365X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.347 | 4.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.02565 | 0.3814 | 0 |  | --> | C21 ex BALLYRAINE | Ballyraine: T41∥T42 | Letterkenny |  | 54.963 | -7.6901
MV/LV Substation TH***365X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 1.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101.4kW. | --> | C14 ex BALLYBAY | Ballybay: T41∥T42 | Lisdrum |  | 54.1277 | -6.9072
MV/LV Substation TH***368X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.205 | 5.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.41102 | 0 |  | --> | C22 ex GALWAY 110KV | Galway 110kv: T102 | Galway 110kv |  | 53.2892 | -9.0002
MV/LV Substation TH***369Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C23 ex TINAHASK | Tinahask: T41∥T42 | Arklow |  | 52.7942 | -6.2326
MV/LV Substation TH***370X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =166kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0076 | 0.19737 | 0 |  | --> | C12 ex TUAM SOUTH | Tuam South: T42 | Cloon |  | 53.5196 | -8.843
MV/LV Substation TH***370Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.197 | 2.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20048 | 0 |  | --> | E11 ex CLONROCHE | Clonroche: T421∥T422 | Wexford |  | 52.4096 | -6.71
MV/LV Substation TH***372 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.305 | 3.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41492 | 0 |  | --> | C11 ex DEANSGRANGE | Deansgrange: T41 | Carrickmines |  | 53.2757 | -6.1587
MV/LV Substation TH***373X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.12 | 4.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0228 | 0.1884 | 0 |  | --> | C17 ex CASTLEKNOCK | Castleknock: T41∥T42 | Finglas |  | 53.3759 | -6.3794
MV/LV Substation TH***377X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.326 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41166 | 0 |  | --> | C11 ex TRIMMS LANE | Trimms Lane: T41 | Salthill |  | 53.2602 | -9.074
MV/LV Substation TH***378X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.168 | 3.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0304 | 0.40346 | 0 |  | --> | C22 ex COOLOCK | Coolock: T42 | Finglas |  | 53.3917 | -6.1749
MV/LV Substation TH***383Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.378 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.39352 | 0 |  | --> | C17 ex VIRGINIA | Virginia: T41∥T42 | Meath Hill |  | 53.8341 | -7.082
MV/LV Substation TH***383Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.173 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0 | 0 | Constrained,otherwise capacity available =202.3kW. | --> | C11 ex LEE BRIDGE | Lee Bridge: T41 | Macroom |  | 51.9122 | -8.965
MV/LV Substation TH***384 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.331 | 4.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4109 | 0 |  | --> | C13 ex MONEENAGEISHA | Moneenageisha: T41 | Galway 110kv |  | 53.2784 | -9.0415
MV/LV Substation TH***387 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E11 ex BALLYHALE | Ballyhale: T421 | Kilkenny |  | 52.5215 | -7.1295
MV/LV Substation TH***387Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.325 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41182 | 0 |  | --> | C18 ex BALLYMAHON | Ballymahon: T41∥T42 | Athlone |  | 53.5584 | -7.7734
MV/LV Substation TH***388Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 9.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex MIDLETON | Midleton: T101 | Midleton |  | 51.9154 | -8.1743
MV/LV Substation TH***388Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.185 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0.20039 | 0 |  | --> | C17 ex ROOSKY | Roosky: T41 | Richmond |  | 53.8333 | -7.916
MV/LV Substation TH***389 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.419 | 2.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.02375 | 0.5 | 0 |  | --> | C17 ex WHITEHALL | Whitehall: T41 | Finglas |  | 53.3788 | -6.2622
MV/LV Substation TH***391X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E18 ex MOY | Moy: T421∥T422 | Moy |  | 54.115 | -9.1519
MV/LV Substation TH***393 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =322kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =412.3kW. | --> | C14 ex FERMOY NORTH | Fermoy North: T41∥T42 | Barrymore |  | 52.1863 | -8.3562
MV/LV Substation TH***393Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =175kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.19796 | 0 |  | --> | E13 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4738 | -6.2336
MV/LV Substation TH***394 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =341kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.39434 | 0 |  | --> | C17 ex BALLYGAR | Ballygar: T41 | Athlone |  | 53.489 | -8.5704
MV/LV Substation TH***394Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =292kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0.40392 | 0 |  | --> | E13 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.472 | -6.2313
MV/LV Substation TH***396 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.352 | 11.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.4016 | 0 |  | --> | C36 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2874 | -9.0864
MV/LV Substation TH***397Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.28 | 5.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41376 | 0 |  | --> | C12 ex KILBARRY | Kilbarry: T43 | Kilbarry |  | 51.921 | -8.4646
MV/LV Substation TH***398X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.177 | 4.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.01425 | 0.18865 | 0 |  | --> | E16 ex MOHILL | Mohill: T421∥T422 | Carrick On Shannon |  | 53.9296 | -8.0025
MV/LV Substation TH***399Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 4.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | E16 ex BALLYRAGGET | Ballyragget: T421∥T422 | Ballyragget |  | 52.8316 | -7.3469
MV/LV Substation TH***4013 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =34kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052495 | 0 |  | --> | E11 ex KILCOLGAN | Kilcolgan: T421 | Galway 110kv |  | 53.2012 | -8.8686
MV/LV Substation TH***4024 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.047265 | 0 |  | --> | E18 ex CLONMINCH | Clonminch: T422 | Thornsberry |  | 53.2738 | -7.6094
MV/LV Substation TH***4028 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.361 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.3972 | 0 |  | --> | C11 ex GREYSTONES | Greystones: T41 | Fassaroe |  | 53.1352 | -6.0906
MV/LV Substation TH***403 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.1 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.39433 | 0 | Constrained,otherwise capacity available =500kW. | --> | C15 ex LOUGHTAGALLA | Loughtagalla: T41∥T42 | Thurles |  | 52.675 | -7.8102
MV/LV Substation TH***4030 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.179 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20333 | 0 |  | --> | C11 ex BALLYARD | Ballyard: T41∥T42 | Tralee |  | 52.2621 | -9.7112
MV/LV Substation TH***403X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =134kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21029 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis: T41∥T42 | Dalton |  | 53.7615 | -8.7754
MV/LV Substation TH***403X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.018 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0019 | 0.052867 | 0 |  | --> | C15 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3374 | -6.4866
MV/LV Substation TH***4046 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =95kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | E11 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.4632 | -6.3521
MV/LV Substation TH***4047 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.449 | 3.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge: T41 | Griffinrath |  | 53.3384 | -6.5335
MV/LV Substation TH***4047 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.186 | 2.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20223 | 0 |  | --> | C16 ex LITTLE BRAY | Little Bray: T42 | Fassaroe |  | 53.2364 | -6.1237
MV/LV Substation TH***404X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052495 | 0 |  | --> | E11 ex BALLYHALE | Ballyhale: T421 | Kilkenny |  | 52.5172 | -7.1812
MV/LV Substation TH***4052 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 4.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C14 ex BRAY | Bray: T42 | Fassaroe |  | 53.1908 | -6.1325
MV/LV Substation TH***4053 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.381 | 4.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0057 | 0.5 | 0 |  | --> | C28 ex KILMORE | Kilmore: T102 | Finglas |  | 53.4071 | -6.1776
MV/LV Substation TH***4054 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex KILMORE | Kilmore: T102 | Finglas |  | 53.407 | -6.1745
MV/LV Substation TH***4054 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.3kW. | --> | C11 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6807 | -8.2192
MV/LV Substation TH***4059 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C20 ex KILMARTIN | Kilmartin: T41 | Arklow |  | 53.0686 | -6.2248
MV/LV Substation TH***4059 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E62 ex ATHY | Athy: T102 | Athy |  | 53.0251 | -6.9131
MV/LV Substation TH***405Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.163 | 3.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =205.8kW. | --> | E20 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 51.9337 | -8.0553
MV/LV Substation TH***4061 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =175kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20396 | 0 |  | --> | E16 ex PATRICKSWELL | Patrickswell: T421∥T422 | Limerick |  | 52.5636 | -8.7997
MV/LV Substation TH***4067 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central: T45 | Inchicore 110kv |  | 53.337 | -6.3157
MV/LV Substation TH***4070 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C24 ex GORESBRIDGE | Goresbridge: T41∥T42 | Kilkenny |  | 52.6294 | -7.0584
MV/LV Substation TH***4083 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C12 ex SKIBBEREEN | Skibbereen: T41∥T42 | Dunmanway |  | 51.5504 | -9.2617
MV/LV Substation TH***4087 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex SALLYNOGGIN ROAD | Sallynoggin Road: T42 | Cherrywood |  | 53.2799 | -6.1463
MV/LV Substation TH***4090 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =295kVA. | --> | 0.38 | 0 | 0 | 0 | 0.03135 | 0.38346 | 0 |  | --> | E17 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.448 | -6.2526
MV/LV Substation TH***4095 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex ARTANE | Artane: T101 | Finglas |  | 53.3841 | -6.2358
MV/LV Substation TH***4097 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C18 ex KILLESHANDRA | Killeshandra: T41∥T42 | Gortawee |  | 53.9972 | -7.5839
MV/LV Substation TH***4105 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 1.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C13 ex DUNDRUM | Dundrum: T41 | Blackrock |  | 53.292 | -6.2421
MV/LV Substation TH***4109 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.397 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40048 | 0 |  | --> | C20 ex SUTTON | Sutton: T42 | Grange (dr) |  | 53.3755 | -6.0591
MV/LV Substation TH***4109 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C11 ex KILRUSH | Kilrush: T41∥T42 | Tullabrack |  | 52.6374 | -9.2485
MV/LV Substation TH***4110 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 7.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C21 ex ATHY | Athy: T101 | Athy |  | 52.9742 | -7.0703
MV/LV Substation TH***4113 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =157kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00665 | 0 | 0 | Constrained,otherwise capacity available =199.8kW. | --> | C13 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6396 | -8.1103
MV/LV Substation TH***4115 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =439kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex GRANGE (DR) | Grange (dr): T41 | Grange (dr) |  | 53.4082 | -6.1617
MV/LV Substation TH***412 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 1.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52kW. | --> | E17 ex CREESLOUGH | Creeslough: T421 | Ardnagappary |  | 55.1798 | -7.972
MV/LV Substation TH***412X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =233kVA. | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0 | 0 | Constrained,otherwise capacity available =405.9kW. | --> | C16 ex RATHDOWNEY | Rathdowney: T42 | Ikerrin |  | 52.855 | -7.5836
MV/LV Substation TH***412X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 8.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex GORTLEE | Gortlee: T41∥T42 | Letterkenny |  | 54.9476 | -7.766
MV/LV Substation TH***412Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.353 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40746 | 0 |  | --> | C12 ex MONEYCOOLEY | Moneycooley: T42 | Griffinrath |  | 53.3529 | -6.5479
MV/LV Substation TH***4130 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E16 ex BALLYRAGGET | Ballyragget: T421∥T422 | Ballyragget |  | 52.8503 | -7.391
MV/LV Substation TH***4137 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.245 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.41006 | 0 |  | --> | C19 ex SALLINS | Sallins: T41 | Griffinrath |  | 53.2878 | -6.7553
MV/LV Substation TH***4139 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0.00855 | 0.5 | 0 |  | --> | C19 ex TRINITY | Trinity: T101 | Poolbeg |  | 53.3411 | -6.2443
MV/LV Substation TH***4141 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown: T102 | Inchicore 110kv |  | 53.2838 | -6.4193
MV/LV Substation TH***4142 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown: T102 | Inchicore 110kv |  | 53.2835 | -6.4209
MV/LV Substation TH***4146 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest: T101 | Inchicore 110kv |  | 53.2849 | -6.4273
MV/LV Substation TH***4147 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.334 | 11.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0.07315 | 0.5 | 0 |  | --> | C22 ex BALLYBEG | Ballybeg: T102 | Carrickmines |  | 52.9778 | -6.0544
MV/LV Substation TH***4148 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C26 ex CITYWEST | Citywest: T102 | Inchicore 110kv |  | 53.2885 | -6.419
MV/LV Substation TH***4148 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =329kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =411.2kW. | --> | C17 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.098 | -7.625
MV/LV Substation TH***4149 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C26 ex CITYWEST | Citywest: T102 | Inchicore 110kv |  | 53.2892 | -6.4183
MV/LV Substation TH***4151 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex MOUNT MERRION | Mount Merrion: T41 | Carrickmines |  | 53.2915 | -6.2073
MV/LV Substation TH***4152 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 3.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C15 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.4379 | -10.0764
MV/LV Substation TH***4154 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E17 ex BAGENALSTOWN | Bagenalstown: T421∥T422 | Carlow |  | 52.7554 | -7.0733
MV/LV Substation TH***416 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =355kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40714 | 0 |  | --> | C16 ex SHANNON | Shannon: T42 | Drumline |  | 52.7011 | -8.9021
MV/LV Substation TH***416 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 7 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.048647 | 0 |  | --> | C14 ex ARDGEEHA | Ardgeeha: T41∥T42 | Doon |  | 52.3832 | -7.6973
MV/LV Substation TH***4162 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MOUNT MERRION | Mount Merrion: T42 | Carrickmines |  | 53.2967 | -6.2117
MV/LV Substation TH***4163 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.414 | 8.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0304 | 0.5 | 0 |  | --> | C19 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 53.0158 | -6.114
MV/LV Substation TH***4164 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 8.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.06555 | 0.5 | 0 |  | --> | C19 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 53.0166 | -6.1166
MV/LV Substation TH***4168 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =307kVA. | --> | 0.38 | 0 | 0 | 0 | 0.14535 | 0.2616 | 0 |  | --> | C24 ex MACETOWN | Macetown: T102 | Macetown |  | 53.5013 | -6.5337
MV/LV Substation TH***4168 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =142kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.069851 | 0 | Constrained,otherwise capacity available =209.1kW. | --> | E12 ex BIRR | Birr: T422 | Dallow |  | 53.1059 | -7.717
MV/LV Substation TH***4170 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =369kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.39994 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.5214 | -6.1668
MV/LV Substation TH***4171 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3.1 |  | --> | 0.95 | 0 | 0 | 0 | 0.038 | 0.5 | 0 |  | --> | C21 ex MONKSTOWN | Monkstown: T41 | Blackrock |  | 53.289 | -6.1768
MV/LV Substation TH***4177 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =192kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.19628 | 0 |  | --> | E11 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.5277 | -6.5868
MV/LV Substation TH***4179 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.09 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0247 | 0.19085 | 0 |  | --> | E14 ex KILCOCK | Kilcock: T422 | Griffinrath |  | 53.4067 | -6.6686
MV/LV Substation TH***4180 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E19 ex KILCOCK | Kilcock: T421 | Griffinrath |  | 53.3902 | -6.7022
MV/LV Substation TH***4180 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex DEANSGRANGE | Deansgrange: T41 | Carrickmines |  | 53.2754 | -6.1585
MV/LV Substation TH***4180 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex MISERY HILL | Misery Hill: T102 | Poolbeg |  | 53.3443 | -6.2326
MV/LV Substation TH***4183 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | E20 ex GARRANACANTY | Garranacanty: T422 | Tipperary |  | 52.4921 | -8.0246
MV/LV Substation TH***4185 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.6 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex SALLYNOGGIN ROAD | Sallynoggin Road: T41 | Cherrywood |  | 53.2811 | -6.1025
MV/LV Substation TH***4185 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0038 | 0.5 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines: T41 | Carrickmines |  | 53.2407 | -6.1971
MV/LV Substation TH***4193 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.239 | 5.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.41896 | 0 |  | --> | C22 ex CLOON | Cloon: T42 | Cloon |  | 53.5122 | -8.8516
MV/LV Substation TH***4194 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.003 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05698 | 0 |  | --> | E12 ex KILCOCK | Kilcock: T422 | Griffinrath |  | 53.4529 | -6.5976
MV/LV Substation TH***4195 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.303 | 3.8 |  | --> | 0.95 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C28 ex LIBERTY STREET | Liberty Street: T102 | Liberty Street |  | 51.8981 | -8.4746
MV/LV Substation TH***419Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.188 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20191 | 0 |  | --> | C21 ex MANOR STREET | Manor Street: T41 | Waterford |  | 52.2534 | -7.1135
MV/LV Substation TH***419Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.168 | 2.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.00665 | 0.19806 | 0 |  | --> | C12 ex CARRIGLAWN | Carriglawn: T41∥T42 | Wexford |  | 52.3781 | -6.449
MV/LV Substation TH***420 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 8.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | C17 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9281 | -6.0411
MV/LV Substation TH***4201 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E13 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.2845 | -7.104
MV/LV Substation TH***4202 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =375kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =404kW. | --> | C11 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.0949 | -7.6085
MV/LV Substation TH***4203 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.321 | 8.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.40744 | 0 |  | --> | C12 ex MONREAD | Monread: T102 | Monread |  | 53.2292 | -6.6617
MV/LV Substation TH***4205 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.348 | 0.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.40324 | 0 |  | --> | E33 ex TRIM | Trim: T421 | Navan |  | 53.4879 | -6.806
MV/LV Substation TH***4221 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4153 | -6.4599
MV/LV Substation TH***4224 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.12 | 0.1 | Constrained,otherwise capacity available =395kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4008 | 0 |  | --> | C16 ex CREGG ROAD | Cregg Road: T41∥T42 | Ballydine |  | 52.3485 | -7.3871
MV/LV Substation TH***4228 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =334kVA. | --> | 0.38 | 0 | 0 | 0 | 0.1197 | 0.28442 | 0 |  | --> | C17 ex NAAS | Naas: T41 | Newbridge |  | 53.211 | -6.6749
MV/LV Substation TH***422Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex LIFFEY VALLEY | Liffey Valley: T42 | Inchicore 110kv |  | 53.3505 | -6.4104
MV/LV Substation TH***4230 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =345kVA. | --> | 0.38 | 0 | 0 | 0 | 0.11495 | 0.2877 | 0 |  | --> | C24 ex MACETOWN | Macetown: T102 | Macetown |  | 53.5032 | -6.5352
MV/LV Substation TH***4231 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 0.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C17 ex CAMDEN ROW | Camden Row: T41 | Francis Street |  | 53.3423 | -6.2803
MV/LV Substation TH***4235 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex CITYWEST | Citywest: T102 | Inchicore 110kv |  | 53.2899 | -6.4164
MV/LV Substation TH***4236 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C21 ex NENAGH | Nenagh: T41 | Nenagh |  | 52.8555 | -8.2073
MV/LV Substation TH***4236 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex CITYWEST | Citywest: T102 | Inchicore 110kv |  | 53.291 | -6.4113
MV/LV Substation TH***4238 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =358kVA. | --> | 0.38 | 0 | 0 | 0 | 0.076 | 0.32666 | 0 |  | --> | C11 ex NAAS | Naas: T41 | Newbridge |  | 53.2068 | -6.6484
MV/LV Substation TH***4238 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =336kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.40612 | 0 |  | --> | C15 ex BLAKE | Blake: T41∥T42 | Blake |  | 53.2869 | -6.8639
MV/LV Substation TH***424 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.368 | 3.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4051 | 0 |  | --> | C19 ex RECESS | Recess: T41 | Galway 110kv |  | 53.3939 | -9.9209
MV/LV Substation TH***4242 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex NORTH QUAYS | North Quays: T102 | Poolbeg |  | 53.3492 | -6.2295
MV/LV Substation TH***4243 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex NORTH QUAYS | North Quays: T102 | Poolbeg |  | 53.349 | -6.2295
MV/LV Substation TH***4249 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =386kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40224 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.4897 | -6.2933
MV/LV Substation TH***424X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 4.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10377 | 0 |  | --> | E15 ex JENKINSTOWN | Jenkinstown: T421∥T422 | Dundalk |  | 54.0457 | -6.363
MV/LV Substation TH***4260 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =32kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.8kW. | --> | E12 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 53.014 | -7.1508
MV/LV Substation TH***4260 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.1995 | 0.43298 | 0 |  | --> | C24 ex MACETOWN | Macetown: T102 | Macetown |  | 53.5037 | -6.5326
MV/LV Substation TH***4261 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0.0475 | 0.5 | 0 |  | --> | C24 ex MACETOWN | Macetown: T102 | Macetown |  | 53.5035 | -6.5286
MV/LV Substation TH***4265 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C15 ex SEMPERIT | Semperit: T41 | Grange Castle |  | 53.3348 | -6.3598
MV/LV Substation TH***426X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.15 | 4.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.0247 | 0.18184 | 0 |  | --> | C11 ex RINGASKIDDY 110KV | Ringaskiddy 110kv: T42 | Barnahely |  | 51.8668 | -8.3397
MV/LV Substation TH***4270 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =385kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.3864 | 0 |  | --> | C16 ex KILLACLOYNE | Killacloyne: T41∥T42 | Midleton |  | 51.9165 | -8.3351
MV/LV Substation TH***4270 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E19 ex KILCOCK | Kilcock: T421 | Griffinrath |  | 53.3898 | -6.7033
MV/LV Substation TH***4271 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.482 | 0.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.01425 | 0.5 | 0 |  | --> | C12 ex SRAH | Srah: T41∥T42 | Thornsberry |  | 53.2916 | -7.5002
MV/LV Substation TH***428 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 1.3 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10408 | 0 |  | --> | C17 ex ROSCOMMON | Roscommon: T41 | Lanesboro |  | 53.6142 | -8.2917
MV/LV Substation TH***4289 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E11 ex CLONROCHE | Clonroche: T421∥T422 | Wexford |  | 52.4056 | -6.7072
MV/LV Substation TH***429 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 4.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10174 | 0 |  | --> | C19 ex RINGASKIDDY 110KV | Ringaskiddy 110kv: T42 | Barnahely |  | 51.8681 | -8.3331
MV/LV Substation TH***4297 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6.6 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex LIBERTY STREET | Liberty Street: T101 | Liberty Street |  | 51.8961 | -8.4777
MV/LV Substation TH***4299 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex LEIXLIP | Leixlip: T41 | Griffinrath |  | 53.3659 | -6.4977
MV/LV Substation TH***430 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =155kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.19607 | 0 |  | --> | C17 ex SKIBBEREEN | Skibbereen: T41∥T42 | Dunmanway |  | 51.5581 | -9.1318
MV/LV Substation TH***4303 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =334kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41042 | 0 |  | --> | C18 ex NAAS | Naas: T42 | Newbridge |  | 53.1947 | -6.6669
MV/LV Substation TH***430Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 4.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10206 | 0 |  | --> | C19 ex BAILIEBORO | Bailieboro: T41∥T42 | Meath Hill |  | 53.887 | -7.0509
MV/LV Substation TH***4311 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 7.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E11 ex DUNFIRTH | Dunfirth: T122 | Dunfirth |  | 53.3967 | -6.8779
MV/LV Substation TH***4313 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =157kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E19 ex ADAMSTOWN | Adamstown: T121 | Inchicore 110kv |  | 53.3365 | -6.4678
MV/LV Substation TH***4314 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E19 ex ADAMSTOWN | Adamstown: T121 | Inchicore 110kv |  | 53.3366 | -6.4678
MV/LV Substation TH***4315 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E19 ex ADAMSTOWN | Adamstown: T121 | Inchicore 110kv |  | 53.3379 | -6.4707
MV/LV Substation TH***4316 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E19 ex ADAMSTOWN | Adamstown: T121 | Inchicore 110kv |  | 53.3371 | -6.4701
MV/LV Substation TH***4322 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.395 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.3808 | 0 |  | --> | C18 ex MALAHIDE | Malahide: T42 | Glasmore |  | 53.4438 | -6.1478
MV/LV Substation TH***4324 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0.12445 | 0.5 | 0 |  | --> | C16 ex JOHNSTOWN | Johnstown: T42 | Kilteel |  | 53.2411 | -6.5999
MV/LV Substation TH***432X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =154kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01235 | 0.19423 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis: T41∥T42 | Dalton |  | 53.7598 | -8.775
MV/LV Substation TH***4330 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex GLASNEVIN | Glasnevin: T41 | Finglas |  | 53.3678 | -6.2701
MV/LV Substation TH***4335 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E19 ex ADAMSTOWN | Adamstown: T121 | Inchicore 110kv |  | 53.3371 | -6.4673
MV/LV Substation TH***4339 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C26 ex GRANGE CASTLE | Grange Castle: T102 | Inchicore 110kv |  | 53.2927 | -6.4823
MV/LV Substation TH***433X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05739 | 0 |  | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen: T41∥T42 | Tonroe |  | 53.9042 | -8.5902
MV/LV Substation TH***434 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.313 | 4.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.40768 | 0 |  | --> | C19 ex RINGASKIDDY 110KV | Ringaskiddy 110kv: T42 | Barnahely |  | 51.87 | -8.3352
MV/LV Substation TH***4341 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex DUNDALK | Dundalk: T42 | Dundalk |  | 54.0059 | -6.4095
MV/LV Substation TH***4346 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400kW. | --> | C14 ex PORTLAOISE | Portlaoise: T42 | Portlaoise |  | 53.0485 | -7.2615
MV/LV Substation TH***4347 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | E14 ex EMYVALE | Emyvale: T422 | Lisdrum |  | 54.3423 | -6.9499
MV/LV Substation TH***4353 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex MACETOWN | Macetown: T102 | Macetown |  | 53.5039 | -6.532
MV/LV Substation TH***4354 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.03515 | 0.5 | 0 |  | --> | C24 ex MACETOWN | Macetown: T102 | Macetown |  | 53.5064 | -6.5327
MV/LV Substation TH***4357 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =387kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40208 | 0 |  | --> | E17 ex BALTRASNA | Baltrasna: T121 | Baltrasna |  | 53.5135 | -6.5423
MV/LV Substation TH***4358 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E19 ex ADAMSTOWN | Adamstown: T121 | Inchicore 110kv |  | 53.3368 | -6.4716
MV/LV Substation TH***436 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052345 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton: T422 | Sligo |  | 54.2999 | -8.1651
MV/LV Substation TH***4365 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 9.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C13 ex MIDLETON | Midleton: T101 | Midleton |  | 51.929 | -8.1748
MV/LV Substation TH***436X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.6 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex HEADFORD ROAD | Headford Road: T42 | Galway 110kv |  | 53.2786 | -9.0487
MV/LV Substation TH***4384 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex MACETOWN | Macetown: T102 | Macetown |  | 53.507 | -6.5298
MV/LV Substation TH***4385 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex MACETOWN | Macetown: T102 | Macetown |  | 53.5059 | -6.5307
MV/LV Substation TH***439X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C15 ex SAGGART | Saggart: T41∥T42 | Grange Castle |  | 53.2679 | -6.3828
MV/LV Substation TH***439Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex HOWTH JUNCTION | Howth Junction: T41 | Grange (dr) |  | 53.3764 | -6.1666
MV/LV Substation TH***4407 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C19 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0358 | -7.306
MV/LV Substation TH***4408 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400kW. | --> | C19 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0355 | -7.3057
MV/LV Substation TH***4409 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400kW. | --> | C19 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0347 | -7.3062
MV/LV Substation TH***441 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10111 | 0 |  | --> | E11 ex BALLYHALE | Ballyhale: T421 | Kilkenny |  | 52.5201 | -7.1347
MV/LV Substation TH***441X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 12.9 |  | --> | 0.95 | 0 | 0 | 0 | 0.01045 | 0.5 | 0 |  | --> | C19 ex HEUSTON SQUARE | Heuston Square: T101 | Inchicore 110kv |  | 53.3442 | -6.2837
MV/LV Substation TH***4420 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C23 ex ATHLONE | Athlone: T41 | Athlone |  | 53.423 | -7.9402
MV/LV Substation TH***4437 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex DRUMCONDRA | Drumcondra: T41 | Mcdermott |  | 53.3592 | -6.2563
MV/LV Substation TH***445Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.147 | 3.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.00665 | 0.2013 | 0 |  | --> | C19 ex CELBRIDGE | Celbridge: T41 | Griffinrath |  | 53.314 | -6.6114
MV/LV Substation TH***447X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 5.3 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex WOLFE TONE STREET | Wolfe Tone Street: T101 | Finglas |  | 53.3494 | -6.2795
MV/LV Substation TH***447X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =146kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20846 | 0 |  | --> | C15 ex LUCAN EAST | Lucan East: T41∥T42 | Grange Castle |  | 53.3503 | -6.4394
MV/LV Substation TH***448Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.123 | 0.1 | Constrained,otherwise capacity available =314kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01995 | 0 | 0 | Constrained,otherwise capacity available =392.5kW. | --> | C16 ex RATHDRUM | Rathdrum: T42 | Arklow |  | 52.9354 | -6.2354
MV/LV Substation TH***449 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 5.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | C13 ex BANDON | Bandon: T101 | Bandon |  | 51.7486 | -8.76
MV/LV Substation TH***450 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 8.3 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10284 | 0 |  | --> | C23 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.924 | -6.1159
MV/LV Substation TH***450Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.354 | 8.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.4023 | 0 |  | --> | C21 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9874 | -6.0726
MV/LV Substation TH***450Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.316 | 12.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.40422 | 0 |  | --> | C23 ex MONREAD | Monread: T101 | Monread |  | 53.2359 | -6.728
MV/LV Substation TH***4515 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex TRINITY | Trinity: T102 | Poolbeg |  | 53.3405 | -6.2406
MV/LV Substation TH***451X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =56kVA. | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.1018 | 0 |  | --> | E11 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4908 | -6.1004
MV/LV Substation TH***4539 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex MARROWBONE LANE | Marrowbone Lane: T42 | Inchicore 110kv |  | 53.3412 | -6.2887
MV/LV Substation TH***4540 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex MARROWBONE LANE | Marrowbone Lane: T42 | Inchicore 110kv |  | 53.3421 | -6.2878
MV/LV Substation TH***4541 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex MARROWBONE LANE | Marrowbone Lane: T42 | Inchicore 110kv |  | 53.3413 | -6.2891
MV/LV Substation TH***4543 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.244 | 6.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex PELLETSTOWN | Pelletstown: T102 | Finglas |  | 53.3764 | -6.3097
MV/LV Substation TH***4544 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex PELLETSTOWN | Pelletstown: T102 | Finglas |  | 53.376 | -6.309
MV/LV Substation TH***4546 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex PELLETSTOWN | Pelletstown: T102 | Finglas |  | 53.3754 | -6.3083
MV/LV Substation TH***4547 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex PELLETSTOWN | Pelletstown: T102 | Finglas |  | 53.3755 | -6.3091
MV/LV Substation TH***454Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =70kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0247 | 0.19376 | 0 |  | --> | C17 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1598 | -6.8916
MV/LV Substation TH***455Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.299 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0513 | 0.36184 | 0 |  | --> | C20 ex SUTTON | Sutton: T42 | Grange (dr) |  | 53.3749 | -6.0547
MV/LV Substation TH***456 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.128 | 1.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.04465 | 0.1642 | 0 |  | --> | C17 ex BALLYTIVNAN | Ballytivnan: T41 | Sligo |  | 54.3059 | -8.5563
MV/LV Substation TH***4561 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =191kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex TRINITY | Trinity: T102 | Poolbeg |  | 53.3405 | -6.2405
MV/LV Substation TH***456Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.209 | 0.2 | Constrained,otherwise capacity available =251kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.40916 | 0 |  | --> | C17 ex BISHOPSTOWN | Bishopstown: T41 | Kilbarry |  | 51.8846 | -8.5784
MV/LV Substation TH***461X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =242kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01615 | 0.4075 | 0 |  | --> | C21 ex DOUGLAS | Douglas: T42 | Trabeg |  | 51.8733 | -8.3945
MV/LV Substation TH***466X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.182 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.19686 | 0 |  | --> | E11 ex BALLYHALE | Ballyhale: T421 | Kilkenny |  | 52.5242 | -7.1802
MV/LV Substation TH***467 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.054 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1071 | 0 |  | --> | C17 ex DUNLEER | Dunleer: T41∥T42 | Drybridge |  | 53.8813 | -6.3413
MV/LV Substation TH***471Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =374kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40414 | 0 |  | --> | E13 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9147 | -6.8403
MV/LV Substation TH***472Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.325 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.39682 | 0 |  | --> | C17 ex GILLOGUE | Gillogue: T41∥T42 | Ardnacrusha |  | 52.7218 | -8.5574
MV/LV Substation TH***476Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.328 | 3.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.40036 | 0 |  | --> | C20 ex MARSHES | Marshes: T42 | Dundalk |  | 53.9813 | -6.3728
MV/LV Substation TH***479 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 4.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052647 | 0 |  | --> | E15 ex JENKINSTOWN | Jenkinstown: T421∥T422 | Dundalk |  | 54.0439 | -6.3653
MV/LV Substation TH***482Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.383 | 1.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40272 | 0 |  | --> | C18 ex ROSEHILL | Rosehill: T42 | Kilkenny |  | 52.6532 | -7.256
MV/LV Substation TH***484Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 8.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C25 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9936 | -6.0491
MV/LV Substation TH***485 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =171kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.19359 | 0 |  | --> | C15 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8447 | -8.3135
MV/LV Substation TH***486X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0.00285 | 0.5 | 0 |  | --> | C16 ex MISERY HILL | Misery Hill: T102 | Poolbeg |  | 53.3408 | -6.2279
MV/LV Substation TH***487 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 4.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05295 | 0 |  | --> | E21 ex CLARA | Clara: T421 | Thornsberry |  | 53.397 | -7.6721
MV/LV Substation TH***487X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =32kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =47.8kW. | --> | E11 ex CASTLELYONS | Castlelyons: T421∥T422 | Barrymore |  | 52.0927 | -8.2452
MV/LV Substation TH***488 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0.5 | 3.2 |  | --> | 0.95 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C27 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.488 | -10.0233
MV/LV Substation TH***490Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =143kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =208.9kW. | --> | C14 ex PORTLAOISE | Portlaoise: T42 | Portlaoise |  | 53.0508 | -7.2773
MV/LV Substation TH***491Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =146kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00665 | 0 | 0 | Constrained,otherwise capacity available =201.5kW. | --> | C14 ex PORTLAOISE | Portlaoise: T42 | Portlaoise |  | 53.053 | -7.2779
MV/LV Substation TH***493Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.179 | 0.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20333 | 0 |  | --> | C14 ex SWORDS | Swords: T42 | Glasmore |  | 53.4629 | -6.2398
MV/LV Substation TH***496 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.025 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053845 | 0 |  | --> | E20 ex GARRANACANTY | Garranacanty: T422 | Tipperary |  | 52.4929 | -8.0262
MV/LV Substation TH***497 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =69kVA. | --> | 0.095 | 0 | 0 | 0 | 0.00855 | 0.069851 | 0 | Constrained,otherwise capacity available =95.8kW. | --> | C15 ex BANAGHER | Banagher: T42 | Dallow |  | 53.184 | -7.9802
MV/LV Substation TH***498 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | E20 ex ROSCREA | Roscrea: T42 | Ikerrin |  | 52.9309 | -7.7617
MV/LV Substation TH***498Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 5.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10284 | 0 |  | --> | E18 ex CRANE | Crane: T122 | Crane |  | 52.448 | -6.3487
MV/LV Substation TH***501Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =318kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =412.9kW. | --> | C14 ex LEE BRIDGE | Lee Bridge: T42 | Macroom |  | 51.9038 | -8.9614
MV/LV Substation TH***503X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.356 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40698 | 0 |  | --> | E11 ex BALLYHALE | Ballyhale: T421 | Kilkenny |  | 52.5224 | -7.1549
MV/LV Substation TH***509Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.9kW. | --> | C13 ex CURRAGLASS | Curraglass: T41 | Barrymore |  | 52.0871 | -8.0031
MV/LV Substation TH***511Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =326kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41166 | 0 |  | --> | C15 ex MALAHIDE | Malahide: T41 | Glasmore |  | 53.4185 | -6.1456
MV/LV Substation TH***512 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | E13 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.7957 | -6.4442
MV/LV Substation TH***526X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.403 | 0.4 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex GLOUCESTER PLACE | Gloucester Place: T42 | Mcdermott |  | 53.3526 | -6.2518
MV/LV Substation TH***527X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.403 | 0.4 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C12 ex GLOUCESTER PLACE | Gloucester Place: T42 | Mcdermott |  | 53.3522 | -6.251
MV/LV Substation TH***528X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.391 | 1.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin: T42 | Inchicore 110kv |  | 53.3245 | -6.3956
MV/LV Substation TH***532Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 6.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =201.8kW. | --> | E28 ex MILFORD (MWR) | Milford (mwr): T422 | Charleville |  | 52.4033 | -8.7816
MV/LV Substation TH***534X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.159 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20645 | 0 |  | --> | E11 ex BALLYHALE | Ballyhale: T421 | Kilkenny |  | 52.524 | -7.1905
MV/LV Substation TH***537Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =389kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40176 | 0 |  | --> | C20 ex MERVILLE | Merville: T42 | Finglas |  | 53.3878 | -6.2995
MV/LV Substation TH***540Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =170kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.19574 | 0 |  | --> | C24 ex GORESBRIDGE | Goresbridge: T41∥T42 | Kilkenny |  | 52.6302 | -7.0718
MV/LV Substation TH***541Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.309 | 3.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.4033 | 0 |  | --> | E16 ex ASHBOURNE | Ashbourne: T422 | Finglas |  | 53.5007 | -6.3894
MV/LV Substation TH***543Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Building Structure | 0.1 | --> | 0.1 | 0 | 3.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1186 | 0 |  | --> | C18 ex MCDONAGH | Mcdonagh: T42 | Kilkenny |  | 52.6562 | -7.2459
MV/LV Substation TH***547 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =52kVA. | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.10239 | 0 |  | --> | E15 ex WHITECHURCH | Whitechurch: T421 | Kilbarry |  | 51.9311 | -8.5634
MV/LV Substation TH***548Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00285 | 0.049345 | 0 |  | --> | C19 ex CLONMINCH | Clonminch: T41 | Thornsberry |  | 53.2618 | -7.4871
MV/LV Substation TH***548Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =155kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20207 | 0 |  | --> | C19 ex ROSEHILL | Rosehill: T41 | Kilkenny |  | 52.6413 | -7.2537
MV/LV Substation TH***554Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E17 ex CAVAN | Cavan: T421 | Shankill |  | 54.0842 | -7.4165
MV/LV Substation TH***556X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.194 | 3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20096 | 0 |  | --> | C11 ex CROSSMOLINA | Crossmolina: T41∥T42 | Moy |  | 54.0333 | -9.324
MV/LV Substation TH***560X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9466 | -8.0919
MV/LV Substation TH***561Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.385 | 2.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0057 | 0.5 | 0 |  | --> | C18 ex BALLYMAHON | Ballymahon: T41∥T42 | Athlone |  | 53.5621 | -7.7621
MV/LV Substation TH***562Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.324 | 8.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.39298 | 0 |  | --> | C21 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9841 | -6.0697
MV/LV Substation TH***563Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.487 | 3.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0133 | 0.5 | 0 |  | --> | C20 ex CENTRE PARK ROAD | Marina: T106 | Marina |  | 51.8914 | -8.4488
MV/LV Substation TH***566Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05219 | 0 |  | --> | C21 ex MARSHES | Marshes: T41 | Dundalk |  | 53.959 | -6.3765
MV/LV Substation TH***569Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.167 | 5.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20521 | 0 |  | --> | E13 ex CRANE | Crane: T122 | Crane |  | 52.4797 | -6.428
MV/LV Substation TH***569Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.318 | 2.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0 | 0 | Constrained,otherwise capacity available =396.9kW. | --> | C15 ex NEWCASTLEWEST | Newcastlewest: T41∥T42 | Rathkeale |  | 52.4465 | -9.0497
MV/LV Substation TH***569Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =138kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.20068 | 0 |  | --> | C22 ex KILMONEY | Kilmoney: T41∥T42 | Trabeg |  | 51.8072 | -8.3949
MV/LV Substation TH***570X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 1.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =201.8kW. | --> | C23 ex KILKEE | Kilkee: T41 | Tullabrack |  | 52.6698 | -9.66
MV/LV Substation TH***576Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.272 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0.40696 | 0 |  | --> | C18 ex BUSHFIELD | Bushfield: T42 | Athlone |  | 53.4343 | -7.9245
MV/LV Substation TH***577 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.133 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20644 | 0 |  | --> | C16 ex GORT | Gort: T41∥T42 | Ennis |  | 53.0679 | -8.8254
MV/LV Substation TH***583 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.009 | 2.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =51.1kW. | --> | C17 ex MILFORD (MWR) | Milford (mwr): T41 | Charleville |  | 52.3467 | -8.9705
MV/LV Substation TH***584X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.184 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.19755 | 0 |  | --> | E17 ex ACHILL | Achill: T422 | Carrowbeg |  | 53.927 | -9.9299
MV/LV Substation TH***586Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =352kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =407.6kW. | --> | C15 ex PORTARLINGTON | Portarlington: T41∥T42 | Portlaoise |  | 53.1629 | -7.1905
MV/LV Substation TH***593X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =481kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.01045 | 0.5 | 0 |  | --> | C12 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.9385 | -7.7304
MV/LV Substation TH***596 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =31kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05295 | 0 |  | --> | C16 ex MILFORD (NR) | Milford (nr): T41∥T42 | Letterkenny |  | 55.0444 | -7.8082
MV/LV Substation TH***596Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.087 | 1.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.01615 | 0.20029 | 0 |  | --> | C12 ex MONEYCOOLEY | Moneycooley: T42 | Griffinrath |  | 53.3512 | -6.5498
MV/LV Substation TH***607X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.048 | 0 | Constrained,otherwise capacity available =425kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.01045 | 0.5 | 0 |  | --> | C21 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 52.9332 | -9.3468
MV/LV Substation TH***609 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =27kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05355 | 0 |  | --> | E17 ex DULEEK | Duleek: T421∥T422 | Drybridge |  | 53.6503 | -6.4744
MV/LV Substation TH***609X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =56kVA. | --> | 0.095 | 0 | 0 | 0 | 0.00285 | 0.1038 | 0 |  | --> | E11 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4956 | -6.1115
MV/LV Substation TH***609X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.32 | 10.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.02375 | 0.3876 | 0 |  | --> | C18 ex ENNIS | Ennis: T102 | Ennis |  | 52.8589 | -8.9671
MV/LV Substation TH***611 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 6.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =103.3kW. | --> | E17 ex SPRINGS | Springs: T421∥T422 | Dungarvan |  | 52.1084 | -7.6675
MV/LV Substation TH***611 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 9.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex KILLYBEGS | Killybegs: T42 | Binbane |  | 54.6363 | -8.4414
MV/LV Substation TH***611X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.157 | 2.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20276 | 0 |  | --> | E19 ex KILCOCK | Kilcock: T421 | Griffinrath |  | 53.3941 | -6.6696
MV/LV Substation TH***611Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0114 | 0.5 | 0 |  | --> | E21 ex LONGFORD | Longford: T421 | Richmond |  | 53.7687 | -7.8345
MV/LV Substation TH***612Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =213kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0684 | 0.35684 | 0 |  | --> | C21 ex PORTARLINGTON | Portarlington: T43 | Blake |  | 53.1325 | -7.1484
MV/LV Substation TH***614Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =98kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =210.7kW. | --> | C15 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0485 | -7.3147
MV/LV Substation TH***618 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | E17 ex DULEEK | Duleek: T421∥T422 | Drybridge |  | 53.6314 | -6.4835
MV/LV Substation TH***620X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.296 | 3.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0684 | 0.3443 | 0 |  | --> | E16 ex ASHBOURNE | Ashbourne: T422 | Finglas |  | 53.5096 | -6.3904
MV/LV Substation TH***621Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.177 | 1.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | C15 ex DERRYCRAMPH | Derrycramph: T41∥T42 | Shankill |  | 53.9909 | -7.3684
MV/LV Substation TH***623X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =183kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00665 | 0.1957 | 0 |  | --> | C20 ex BALLYGAR | Ballygar: T42 | Athlone |  | 53.5669 | -8.2496
MV/LV Substation TH***625X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.124 | 1.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.2068 | 0 |  | --> | C16 ex JOHNSTOWN | Johnstown: T42 | Kilteel |  | 53.2456 | -6.5945
MV/LV Substation TH***625Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex BALLINACURRA | Ballinacurra: T41 | Limerick |  | 52.6604 | -8.6376
MV/LV Substation TH***627Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.128 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.2082 | 0 |  | --> | C15 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3334 | -6.4843
MV/LV Substation TH***629Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =187kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =202.1kW. | --> | C15 ex TOOMEVARA | Toomevara: T42 | Nenagh |  | 52.9417 | -8.0382
MV/LV Substation TH***630 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C18 ex ORANMORE | Oranmore: T44 | Galway 110kv |  | 53.2763 | -8.9308
MV/LV Substation TH***631 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.161 | 3.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.02755 | 0.17714 | 0 |  | --> | C20 ex OAKFIELD | Oakfield: T42 | Sligo |  | 54.2703 | -8.589
MV/LV Substation TH***633X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex GRANBY ROW | Granby Row: T41 | Mcdermott |  | 53.3544 | -6.2591
MV/LV Substation TH***636 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.062 | 6.8 |  | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0.0959 | 0 |  | --> | C18 ex CARRICKMINES | Carrickmines: T42 | Carrickmines |  | 53.2475 | -6.2183
MV/LV Substation TH***636X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6.7 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex DRUMCONDRA | Drumcondra: T42 | Mcdermott |  | 53.3638 | -6.2482
MV/LV Substation TH***637X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.365 | 3.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.39556 | 0 |  | --> | C26 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.4928 | -10.0186
MV/LV Substation TH***639X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.048 | 0 | Constrained,otherwise capacity available =343kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40902 | 0 |  | --> | C21 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 52.9342 | -9.3394
MV/LV Substation TH***639Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.18 | 0.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20318 | 0 |  | --> | C18 ex KNOCKMULLEN | Knockmullen: T42 | Great Island |  | 52.3845 | -6.9468
MV/LV Substation TH***640Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =338kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =409.8kW. | --> | C13 ex FERMOY NORTH | Fermoy North: T41∥T42 | Barrymore |  | 52.1402 | -8.2703
MV/LV Substation TH***641Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C22 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.3339 | -6.5475
MV/LV Substation TH***642X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.325 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.40782 | 0 |  | --> | E14 ex KILCOCK | Kilcock: T422 | Griffinrath |  | 53.4021 | -6.6715
MV/LV Substation TH***642Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E17 ex BALTRASNA | Baltrasna: T121 | Baltrasna |  | 53.5251 | -6.526
MV/LV Substation TH***643 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.048 | 0 | Constrained,otherwise capacity available =63kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0399 | 0.06375 | 0 |  | --> | C19 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 53.0251 | -9.2839
MV/LV Substation TH***647Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E15 ex JENKINSTOWN | Jenkinstown: T421∥T422 | Dundalk |  | 54.0448 | -6.366
MV/LV Substation TH***648X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.149 | 2 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.203 | 0 |  | --> | C12 ex CAPPAMORE | Cappamore: T41∥T42 | Ardnacrusha |  | 52.6486 | -8.4052
MV/LV Substation TH***649Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C15 ex MALAHIDE | Malahide: T41 | Glasmore |  | 53.4199 | -6.1503
MV/LV Substation TH***650Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E16 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.698 | -6.245
MV/LV Substation TH***651X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.1009 | 0.1 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex COOLCORCORAN | Coolcorcoran: T41∥T42 | Knockearagh |  | 52.0603 | -9.5061
MV/LV Substation TH***651Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.343 | 4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =409kW. | --> | E14 ex CHARLEVILLE | Charleville: T422 | Charleville |  | 52.3574 | -8.6963
MV/LV Substation TH***652Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.073 | 1.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10423 | 0 |  | --> | C17 ex ROOSKY | Roosky: T41 | Richmond |  | 53.7819 | -8.1038
MV/LV Substation TH***652Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex SALLINS | Sallins: T41 | Griffinrath |  | 53.2906 | -6.6824
MV/LV Substation TH***653 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 7.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0.01045 | 0.039477 | 0 |  | --> | C06 ex AHANE | Ahane: T102 | Ahane |  | 52.6685 | -8.4903
MV/LV Substation TH***654Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =339kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40964 | 0 |  | --> | E15 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.5117 | -6.4016
MV/LV Substation TH***655 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E15 ex BALLYCONNELL | Ballyconnell: T421∥T422 | Gortawee |  | 54.1151 | -7.583
MV/LV Substation TH***657 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.128 | 0.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.00665 | 0.2042 | 0 |  | --> | C15 ex COOLMINE | Coolmine: T41 | Finglas |  | 53.3892 | -6.4154
MV/LV Substation TH***657Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.156 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.19692 | 0 |  | --> | C26 ex ATHY | Athy: T102 | Athy |  | 53.1023 | -7.0057
MV/LV Substation TH***660 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =236kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4254 | 0 |  | --> | C17 ex GARVILLE AVENUE | Garville Avenue: T42 | Milltown (dr) |  | 53.3261 | -6.2639
MV/LV Substation TH***660Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =321kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.39344 | 0 |  | --> | E15 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.6292 | -6.2655
MV/LV Substation TH***661X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex PELLETSTOWN | Pelletstown: T102 | Finglas |  | 53.3764 | -6.3334
MV/LV Substation TH***661X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =22kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.01425 | 0 | 0 | Constrained,otherwise capacity available =39.3kW. | --> | C16 ex RAMSTOWN | Ramstown: T41∥T42 | Crane |  | 52.6666 | -6.3023
MV/LV Substation TH***661Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =484kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.076 | 0.5 | 0 |  | --> | C16 ex KILLACLOYNE | Killacloyne: T41∥T42 | Midleton |  | 51.9134 | -8.3223
MV/LV Substation TH***662X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0.5 | 6.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex PELLETSTOWN | Pelletstown: T102 | Finglas |  | 53.3764 | -6.3334
MV/LV Substation TH***663 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 7.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex MILLTOWN (DR) | Milltown (dr): T101 | Poolbeg |  | 53.3153 | -6.2472
MV/LV Substation TH***663X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex PELLETSTOWN | Pelletstown: T102 | Finglas |  | 53.3761 | -6.3314
MV/LV Substation TH***664 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.049 | 4 |  | --> | 0.095 | 0 | 0 | 0 | 0.00665 | 0.10084 | 0 |  | --> | C12 ex ROSS CARBERY | Ross Carbery: T41∥T42 | Dunmanway |  | 51.575 | -9.0185
MV/LV Substation TH***664X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.1009 | 0.1 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0038 | 0.5 | 0 |  | --> | C11 ex COOLCORCORAN | Coolcorcoran: T41∥T42 | Knockearagh |  | 52.0586 | -9.4999
MV/LV Substation TH***665 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 4.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10111 | 0 |  | --> | E13 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.223 | -6.3857
MV/LV Substation TH***666X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E25 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.7211 | -7.3539
MV/LV Substation TH***669Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 1.2 |  | --> | 0.095 | 0 | 0 | 0 | 0.019 | 0.0819 | 0 |  | --> | E11 ex BALLYDEHOB | Ballydehob: T421 | Dunmanway |  | 51.564 | -9.4613
MV/LV Substation TH***671Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =20kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00855 | 0.045577 | 0 |  | --> | C21 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7709 | -6.3061
MV/LV Substation TH***672 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 6.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =104.4kW. | --> | E17 ex SPRINGS | Springs: T421∥T422 | Dungarvan |  | 52.1244 | -7.5606
MV/LV Substation TH***674 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00285 | 0.04873 | 0 |  | --> | E16 ex PATRICKSWELL | Patrickswell: T421∥T422 | Limerick |  | 52.5576 | -8.7971
MV/LV Substation TH***675 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.137 | 1.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0114 | 0 | 0 | Constrained,otherwise capacity available =197.8kW. | --> | E14 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1438 | -7.4523
MV/LV Substation TH***678 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.078 | 7.7 |  | --> | 0.095 | 0 | 0 | 0 | 0.0038 | 0.09946 | 0 |  | --> | C21 ex ATHY | Athy: T101 | Athy |  | 52.9234 | -7.062
MV/LV Substation TH***682X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | C16 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0895 | -7.368
MV/LV Substation TH***683 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 11.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C14 ex SINGLAND | Singland: T102 | Singland |  | 52.6452 | -8.5654
MV/LV Substation TH***684 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =347kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4084 | 0 |  | --> | E16 ex PATRICKSWELL | Patrickswell: T421∥T422 | Limerick |  | 52.5617 | -8.7817
MV/LV Substation TH***684 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.135 | 4 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0 | 0 | Constrained,otherwise capacity available =207.1kW. | --> | C19 ex LISMORE | Lismore: T41∥T42 | Dungarvan |  | 52.1323 | -7.9274
MV/LV Substation TH***685Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 8.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20176 | 0 |  | --> | E18 ex BALTRASNA | Baltrasna: T122 | Baltrasna |  | 53.5005 | -6.4679
MV/LV Substation TH***687X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 4.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1019 | 0 |  | --> | E17 ex BAGENALSTOWN | Bagenalstown: T421∥T422 | Carlow |  | 52.708 | -6.9531
MV/LV Substation TH***687Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.172 | 4.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.19543 | 0 |  | --> | E18 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.2677 | -6.3903
MV/LV Substation TH***688X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.174 | 8.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.02185 | 0.18112 | 0 |  | --> | C17 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9493 | -6.0291
MV/LV Substation TH***688X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.177 | 0.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | E16 ex MILLTOWN (SR) | Milltown (sr): T422 | Oughtragh |  | 52.1051 | -9.7859
MV/LV Substation TH***689X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex BALLYBEG | Ballybeg: T102 | Carrickmines |  | 52.9953 | -6.087
MV/LV Substation TH***694 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =299kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41584 | 0 |  | --> | C11 ex BALLYBODEN | Ballyboden: T41 | Cookstown |  | 53.281 | -6.2736
MV/LV Substation TH***698 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.346 | 10.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0323 | 0.37454 | 0 |  | --> | C19 ex SALTHILL | Salthill: T101 | Salthill |  | 53.266 | -9.0774
MV/LV Substation TH***703 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.017 | 9.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.055012 | 0 |  | --> | C18 ex CONVOY | Convoy: T41∥T42 | Letterkenny |  | 54.8732 | -7.6177
MV/LV Substation TH***706X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.9 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex SHERIFF STREET | Sheriff Street: T41 | Francis Street |  | 53.3458 | -6.2457
MV/LV Substation TH***707 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.168 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0152 | 0.18906 | 0 |  | --> | E20 ex LONGFORD | Longford: T422 | Richmond |  | 53.7378 | -7.7909
MV/LV Substation TH***708 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.113 | 5.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.01805 | 0.19445 | 0 |  | --> | E19 ex ARDNAREE | Ardnaree: T421 | Moy |  | 54.1267 | -9.139
MV/LV Substation TH***711 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.145 | 9.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20861 | 0 |  | --> | C18 ex CONVOY | Convoy: T41∥T42 | Letterkenny |  | 54.877 | -7.6031
MV/LV Substation TH***718 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.332 | 3.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41074 | 0 |  | --> | C11 ex DUN LAOGHAIRE | Dun Laoghaire: T41 | Blackrock |  | 53.2929 | -6.1471
MV/LV Substation TH***718Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 1.1 |  | --> | 0.095 | 0 | 0 | 0 | 0.0038 | 0 | 0 | Constrained,otherwise capacity available =97kW. | --> | C14 ex ROSBERCON | Rosbercon: T42 | Waterford |  | 52.4522 | -6.9615
MV/LV Substation TH***719 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.151 | 10.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.19669 | 0 |  | --> | C17 ex CABRA | Cabra: T102 | Finglas |  | 53.3718 | -6.283
MV/LV Substation TH***719X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =134kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21029 | 0 |  | --> | C16 ex CLONES | Clones: T41∥T42 | Shankill |  | 54.1801 | -7.2306
MV/LV Substation TH***720 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.1009 | 0.1 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex COOLCORCORAN | Coolcorcoran: T41∥T42 | Knockearagh |  | 52.0608 | -9.482
MV/LV Substation TH***721Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 2.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1033 | 0 |  | --> | E12 ex LONGFORD | Longford: T422 | Richmond |  | 53.8182 | -7.7684
MV/LV Substation TH***721Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =335kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0 | 0 | Constrained,otherwise capacity available =407.3kW. | --> | E17 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 52.9228 | -7.3415
MV/LV Substation TH***723 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =86kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21744 | 0 |  | --> | C26 ex COLLOONEY | Collooney: T422 | Sligo |  | 54.1862 | -8.4915
MV/LV Substation TH***723Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.172 | 5.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.01425 | 0 | 0 | Constrained,otherwise capacity available =189.4kW. | --> | C11 ex BANDON | Bandon: T101 | Bandon |  | 51.7541 | -8.7333
MV/LV Substation TH***726Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.378 | 10.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.38852 | 0 |  | --> | E13 ex COOLROE | Coolroe: T121 | Coolroe |  | 51.884 | -8.6225
MV/LV Substation TH***731 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.391 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40144 | 0 |  | --> | C19 ex BELFIELD | Belfield: T41 | Blackrock |  | 53.3028 | -6.2261
MV/LV Substation TH***733 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.04542 | 0 |  | --> | C16 ex BRAY | Bray: T42 | Fassaroe |  | 53.1676 | -6.1446
MV/LV Substation TH***734Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.273 | 5.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0266 | 0.39182 | 0 |  | --> | C12 ex ABBEYLAND | Abbeyland: T42 | Navan |  | 53.6692 | -6.6835
MV/LV Substation TH***735 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.04 | 0 | Constrained,otherwise capacity available =90kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10159 | 0 |  | --> | C17 ex GRAIGUENAMANAGH | Graiguenamanagh: T41∥T42 | Kilkenny |  | 52.5428 | -6.9493
MV/LV Substation TH***735X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.102 | 7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.21109 | 0 |  | --> | C13 ex ARDGEEHA | Ardgeeha: T41∥T42 | Doon |  | 52.3666 | -7.6964
MV/LV Substation TH***736X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.151 | 7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex ARDGEEHA | Ardgeeha: T41∥T42 | Doon |  | 52.3522 | -7.7028
MV/LV Substation TH***736Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.00285 | 0.5 | 0 |  | --> | E17 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4474 | -6.2446
MV/LV Substation TH***737Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0019 | 0.5 | 0 |  | --> | E17 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4477 | -6.2427
MV/LV Substation TH***738X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =138kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0285 | 0 | 0 | Constrained,otherwise capacity available =179.7kW. | --> | C18 ex RAMSTOWN | Ramstown: T41∥T42 | Crane |  | 52.6679 | -6.3014
MV/LV Substation TH***738Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =76kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.2089 | 0 |  | --> | E12 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.6412 | -6.6574
MV/LV Substation TH***738Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.311 | 0.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.03895 | 0.373 | 0 |  | --> | C20 ex RATHMULLAN | Rathmullan: T42 | Drybridge |  | 53.6926 | -6.4129
MV/LV Substation TH***739Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.163 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20183 | 0 |  | --> | C12 ex MOUNT MISERY | Mount Misery: T41 | Waterford |  | 52.2729 | -7.1115
MV/LV Substation TH***741 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0228 | 0.19138 | 0 |  | --> | C16 ex KILLACLOYNE | Killacloyne: T41∥T42 | Midleton |  | 51.9182 | -8.3392
MV/LV Substation TH***744 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.062 | 4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1059 | 0 |  | --> | E16 ex TULLOW | Tullow: T422 | Carlow |  | 52.7716 | -6.6746
MV/LV Substation TH***746Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =306kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41476 | 0 |  | --> | E17 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4488 | -6.2452
MV/LV Substation TH***749 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.347 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4084 | 0 |  | --> | C18 ex MOUNT MERRION | Mount Merrion: T42 | Carrickmines |  | 53.2978 | -6.1956
MV/LV Substation TH***751X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6.7 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex DRUMCONDRA | Drumcondra: T42 | Mcdermott |  | 53.363 | -6.2489
MV/LV Substation TH***751Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex CARRIGALINE | Carrigaline: T41∥T42 | Barnahely |  | 51.8169 | -8.373
MV/LV Substation TH***754Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.191 | 1.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20144 | 0 |  | --> | C16 ex DERRYCRAMPH | Derrycramph: T41∥T42 | Shankill |  | 53.9754 | -7.3558
MV/LV Substation TH***757X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =168kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20506 | 0 |  | --> | C16 ex ATHENRY | Athenry: T41∥T42 | Galway 110kv |  | 53.3057 | -8.748
MV/LV Substation TH***758 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.248 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.4196 | 0 |  | --> | C16 ex MONKSTOWN | Monkstown: T42 | Blackrock |  | 53.2924 | -6.1608
MV/LV Substation TH***758X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.161 | 11.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20614 | 0 |  | --> | C22 ex BALLYBEG | Ballybeg: T102 | Carrickmines |  | 52.9776 | -6.0354
MV/LV Substation TH***759Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.7 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E20 ex LONGFORD | Longford: T422 | Richmond |  | 53.7408 | -7.8032
MV/LV Substation TH***761X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 2.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =103kW. | --> | E17 ex LISDRUM | Lisdrum: T422 | Lisdrum |  | 54.2167 | -7.0454
MV/LV Substation TH***764Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.158 | 3.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =206.6kW. | --> | C18 ex TELAYDON | Telaydon: T42 | Lisdrum |  | 54.251 | -6.9741
MV/LV Substation TH***764Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | E18 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.5082 | -7.2409
MV/LV Substation TH***770 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =74kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0171 | 0 | 0 | Constrained,otherwise capacity available =86.1kW. | --> | E12 ex FERNS | Ferns: T421 | Crane |  | 52.5884 | -6.5042
MV/LV Substation TH***770X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.169 | 2.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.1949 | 0 |  | --> | C11 ex CASTLECOMER | Castlecomer: T41∥T42 | Ballyragget |  | 52.7978 | -7.2138
MV/LV Substation TH***770X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.153 | 1.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.19738 | 0 |  | --> | C15 ex TULLA | Tulla: T41 | Ennis |  | 52.8646 | -8.7508
MV/LV Substation TH***770X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =70kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.069851 | 0 | Constrained,otherwise capacity available =104.7kW. | --> | E12 ex BIRR | Birr: T422 | Dallow |  | 53.0974 | -7.7193
MV/LV Substation TH***778Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =126kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01615 | 0.1945 | 0 |  | --> | E17 ex BALTRASNA | Baltrasna: T121 | Baltrasna |  | 53.5125 | -6.5349
MV/LV Substation TH***779Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.319 | 13.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41276 | 0 |  | --> | C38 ex CASTLEVIEW | Castleview: T102 | Castleview |  | 51.8847 | -8.3931
MV/LV Substation TH***781 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.375 | 3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex GREENHILLS | Greenhills: T42 | Inchicore 110kv |  | 53.3173 | -6.3362
MV/LV Substation TH***782X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =89kVA. | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.096745 | 0 |  | --> | C16 ex CLONAKILTY | Clonakilty: T41∥T42 | Dunmanway |  | 51.626 | -8.8935
MV/LV Substation TH***789X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.262 | 6 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.40548 | 0 |  | --> | C14 ex MALLOW | Mallow: T42 | Mallow |  | 52.1459 | -8.6432
MV/LV Substation TH***790X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.343 | 6 |  | --> | 0.38 | 0 | 0 | 0 | 0.02375 | 0.38402 | 0 |  | --> | C14 ex MALLOW | Mallow: T42 | Mallow |  | 52.1481 | -8.6426
MV/LV Substation TH***791Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =162kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =196kW. | --> | C14 ex PORTLAOISE | Portlaoise: T42 | Portlaoise |  | 53.0522 | -7.2753
MV/LV Substation TH***792X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.014 | 5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.055442 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn: T41 | Cookstown |  | 53.273 | -6.3604
MV/LV Substation TH***792X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex MISERY HILL | Misery Hill: T102 | Poolbeg |  | 53.346 | -6.2437
MV/LV Substation TH***793X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.077 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10361 | 0 |  | --> | C14 ex BALLYHALE | Ballyhale: T42 | Kilkenny |  | 52.3706 | -7.1721
MV/LV Substation TH***794X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =53kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0475 | 0.057245 | 0 |  | --> | E25 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.7122 | -7.3287
MV/LV Substation TH***796X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10064 | 0 |  | --> | E11 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.4409 | -6.3377
MV/LV Substation TH***798Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.147 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0.0114 | 0.1963 | 0 |  | --> | C17 ex MOUNT MISERY | Mount Misery: T41 | Waterford |  | 52.2749 | -7.1138
MV/LV Substation TH***799X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =114kVA. | --> | 0.19 | 0 | 0 | 0 | 0.04845 | 0.1623 | 0 |  | --> | C11 ex NAAS | Naas: T41 | Newbridge |  | 53.2165 | -6.6472
MV/LV Substation TH***799Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.318 | 1.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.4069 | 0 |  | --> | E12 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.2363 | -7.0706
MV/LV Substation TH***800 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =319kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02185 | 0.38976 | 0 |  | --> | C11 ex CLONTARF | Clontarf: T42 | Finglas |  | 53.3753 | -6.1936
MV/LV Substation TH***800X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C15 ex STICKILLEN | Stickillen: T41∥T42 | Drybridge |  | 53.8481 | -6.5395
MV/LV Substation TH***801Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =81kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0019 | 0.10099 | 0 |  | --> | C17 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.7519 | -7.952
MV/LV Substation TH***802X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =95kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | C17 ex CARRIGSHANE | Carrigshane: T41 | Midleton |  | 51.8598 | -8.1618
MV/LV Substation TH***805X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.165 | 2.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =205.5kW. | --> | C12 ex FOYNES | Foynes: T42 | Rathkeale |  | 52.6123 | -9.1124
MV/LV Substation TH***808Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 0.7 |  | --> | 0.095 | 0 | 0 | 0 | 0.0038 | 0.09837 | 0 |  | --> | C12 ex AGHAMORE | Aghamore: T42 | Lanesboro |  | 53.7707 | -8.0463
MV/LV Substation TH***811 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =127kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01425 | 0 | 0 | Constrained,otherwise capacity available =196.3kW. | --> | C13 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6498 | -8.1088
MV/LV Substation TH***811Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.148 | 7.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20815 | 0 |  | --> | C23 ex ATHY | Athy: T101 | Athy |  | 52.9449 | -7.0401
MV/LV Substation TH***812X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.176 | 1.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.1948 | 0 |  | --> | C19 ex GRAIGUE | Graigue: T41 | Carlow |  | 52.8214 | -6.9387
MV/LV Substation TH***815X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =89kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.214 | 0 |  | --> | E21 ex GLENAMADDY | Glenamaddy: T422 | Athlone |  | 53.6175 | -8.7457
MV/LV Substation TH***815Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =316kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.40822 | 0 |  | --> | C18 ex DOUGLAS | Douglas: T41 | Trabeg |  | 51.8622 | -8.4091
MV/LV Substation TH***816 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.127 | 4.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21135 | 0 |  | --> | C15 ex MAYFIELD | Mayfield: T41 | Kilbarry |  | 51.9191 | -8.3972
MV/LV Substation TH***818Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.045107 | 0 |  | --> | E18 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.5073 | -7.2442
MV/LV Substation TH***819Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.172 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20443 | 0 |  | --> | C12 ex MOUNT MISERY | Mount Misery: T41 | Waterford |  | 52.2731 | -7.0876
MV/LV Substation TH***819Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =69kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10484 | 0 |  | --> | E18 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.5153 | -7.2703
MV/LV Substation TH***822 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.4 | 1.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00665 | 0.5 | 0 |  | --> | C19 ex DUNDRUM | Dundrum: T41 | Blackrock |  | 53.2935 | -6.2463
MV/LV Substation TH***822X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.142 | 11.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.19807 | 0 |  | --> | C28 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2536 | -9.155
MV/LV Substation TH***825 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.181 | 0.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20302 | 0 |  | --> | C12 ex AGHAMORE | Aghamore: T42 | Lanesboro |  | 53.6766 | -7.9924
MV/LV Substation TH***825 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.297 | 1.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.40614 | 0 |  | --> | C19 ex DUNDRUM | Dundrum: T41 | Blackrock |  | 53.3077 | -6.2418
MV/LV Substation TH***829 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.394 | 0.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40096 | 0 |  | --> | E17 ex DINGLE | Dingle: T421 | Oughtragh |  | 52.1413 | -10.2866
MV/LV Substation TH***830 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.135 | 4.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex DONNYBROOK | Donnybrook: T42 | Milltown (dr) |  | 53.3316 | -6.2303
MV/LV Substation TH***830X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central: T45 | Inchicore 110kv |  | 53.338 | -6.3202
MV/LV Substation TH***831 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 9.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10064 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole: T41∥T42 | Fassaroe |  | 53.0803 | -6.0659
MV/LV Substation TH***831Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =492kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex ROCHES STREET | Roches Street: T41 | Limerick |  | 52.6612 | -8.6199
MV/LV Substation TH***832X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.184 | 1.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20255 | 0 |  | --> | C11 ex RATHMORE | Rathmore: T42 | Knockearagh |  | 52.0863 | -9.2155
MV/LV Substation TH***833X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C17 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.6728 | -7.8461
MV/LV Substation TH***834 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.273 | 9.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.04275 | 0.37482 | 0 |  | --> | C19 ex ENNIS | Ennis: T101 | Ennis |  | 52.8169 | -8.8641
MV/LV Substation TH***845X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.135 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0.03325 | 0.17514 | 0 |  | --> | C11 ex MANOR STREET | Manor Street: T41 | Waterford |  | 52.2523 | -7.0738
MV/LV Substation TH***845Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =308kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.41146 | 0 |  | --> | E15 ex DULEEK | Duleek: T421∥T422 | Drybridge |  | 53.6561 | -6.4269
MV/LV Substation TH***848X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =308kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.40446 | 0 |  | --> | C17 ex SKIBBEREEN | Skibbereen: T41∥T42 | Dunmanway |  | 51.5279 | -9.1781
MV/LV Substation TH***849X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.264 | 10.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0247 | 0.39518 | 0 |  | --> | C18 ex ENNIS | Ennis: T102 | Ennis |  | 52.8522 | -8.9623
MV/LV Substation TH***852X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.171 | 4.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.20159 | 0 |  | --> | C11 ex DUNMANWAY | Dunmanway: T43 | Dunmanway |  | 51.7157 | -9.1223
MV/LV Substation TH***855X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =296kVA. | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.3963 | 0 |  | --> | C11 ex POLLERTON | Pollerton: T41 | Carlow |  | 52.8419 | -6.9054
MV/LV Substation TH***856 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 7.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex MILLTOWN (DR) | Milltown (dr): T101 | Poolbeg |  | 53.325 | -6.2552
MV/LV Substation TH***860 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =60kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1062 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.5307 | -6.1742
MV/LV Substation TH***860 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.12 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.0076 | 0.2044 | 0 |  | --> | E11 ex BALLYHALE | Ballyhale: T421 | Kilkenny |  | 52.5219 | -7.1362
MV/LV Substation TH***861 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =289kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41238 | 0 |  | --> | E14 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.4177 | -7.2977
MV/LV Substation TH***861Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.345 | 5.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.4057 | 0 |  | --> | C13 ex MCDONAGH | Mcdonagh: T41 | Kilkenny |  | 52.6656 | -7.2347
MV/LV Substation TH***862 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =134kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =205.3kW. | --> | C12 ex LEE BRIDGE | Lee Bridge: T42 | Macroom |  | 51.9462 | -9.1702
MV/LV Substation TH***862X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =453kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | E12 ex BUNCLODY | Bunclody: T421∥T422 | Crane |  | 52.6554 | -6.651
MV/LV Substation TH***864Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =381kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.39804 | 0 |  | --> | C15 ex KINSALE | Kinsale: T41∥T42 | Bandon |  | 51.7076 | -8.5218
MV/LV Substation TH***865 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.287 | 3.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41768 | 0 |  | --> | C21 ex DEANSGRANGE | Deansgrange: T41 | Carrickmines |  | 53.2669 | -6.1849
MV/LV Substation TH***865 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.164 | 1.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.02375 | 0.18068 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.8299 | -6.9036
MV/LV Substation TH***865X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =338kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.4068 | 0 |  | --> | C17 ex CARRIGALINE | Carrigaline: T41∥T42 | Barnahely |  | 51.8009 | -8.2914
MV/LV Substation TH***866X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E12 ex MILLTOWN (SR) | Milltown (sr): T422 | Oughtragh |  | 52.0703 | -9.8441
MV/LV Substation TH***866X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =343kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01995 | 0.38802 | 0 |  | --> | E11 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4872 | -6.141
MV/LV Substation TH***867X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =247kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0323 | 0.38976 | 0 |  | --> | E11 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4883 | -6.1432
MV/LV Substation TH***867Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 13.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C38 ex CASTLEVIEW | Castleview: T102 | Castleview |  | 51.885 | -8.3921
MV/LV Substation TH***870X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.044477 | 0 |  | --> | E14 ex BLESSINGTON | Blessington: T422 | Kilteel |  | 53.1192 | -6.5834
MV/LV Substation TH***870Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.162 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.01235 | 0.19299 | 0 |  | --> | C26 ex ATHY | Athy: T102 | Athy |  | 53.1066 | -7.0133
MV/LV Substation TH***874X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.046265 | 0 |  | --> | C13 ex MORNINGTON ROAD | Mornington Road: T41 | Drybridge |  | 53.717 | -6.2649
MV/LV Substation TH***874X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex DELVIN | Delvin: T42 | Mullingar |  | 53.6125 | -7.0923
MV/LV Substation TH***875X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.168 | 2.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20506 | 0 |  | --> | C15 ex CASTLECOMER | Castlecomer: T41∥T42 | Ballyragget |  | 52.885 | -7.1577
MV/LV Substation TH***875X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.046795 | 0 |  | --> | E64 ex ATHY | Athy: T102 | Athy |  | 53.0855 | -7.0878
MV/LV Substation TH***878X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 0.9 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex STICKILLEN | Stickillen: T41∥T42 | Drybridge |  | 53.857 | -6.5423
MV/LV Substation TH***879X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0528 | 0 |  | --> | C18 ex DUNDALK | Dundalk: T41 | Dundalk |  | 54.0138 | -6.4281
MV/LV Substation TH***879X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 0.9 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex STICKILLEN | Stickillen: T41∥T42 | Drybridge |  | 53.857 | -6.5421
MV/LV Substation TH***880X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =144kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0133 | 0.19476 | 0 |  | --> | C11 ex POLLERTON | Pollerton: T41 | Carlow |  | 52.8477 | -6.8974
MV/LV Substation TH***880Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.245 | 0.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0209 | 0.40206 | 0 |  | --> | C14 ex KNOCKMULLEN | Knockmullen: T42 | Great Island |  | 52.3926 | -6.939
MV/LV Substation TH***881X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =40.9kW. | --> | E17 ex LISDRUM | Lisdrum: T422 | Lisdrum |  | 54.2163 | -7.0418
MV/LV Substation TH***881X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 4.2 |  | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0.09377 | 0 |  | --> | C12 ex LLOYD | Lloyd: T41∥T42 | Navan |  | 53.7291 | -6.889
MV/LV Substation TH***884X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C22 ex BELLFIELD | Bellfield: T41∥T42 | Crane |  | 52.4968 | -6.5677
MV/LV Substation TH***884Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.181 | 8.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.43356 | 0 |  | --> | C12 ex MONREAD | Monread: T102 | Monread |  | 53.2208 | -6.6581
MV/LV Substation TH***885 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =322kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.39328 | 0 |  | --> | C17 ex POLLERTON | Pollerton: T41 | Carlow |  | 52.847 | -6.9302
MV/LV Substation TH***887X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.388 | 2.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =401.9kW. | --> | C16 ex KILRUSH | Kilrush: T41∥T42 | Tullabrack |  | 52.6346 | -9.5983
MV/LV Substation TH***887Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E18 ex BLESSINGTON | Blessington: T422 | Kilteel |  | 53.1894 | -6.4815
MV/LV Substation TH***888Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.107 | 7.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.21035 | 0 |  | --> | C21 ex ATHY | Athy: T101 | Athy |  | 52.9431 | -7.0431
MV/LV Substation TH***890X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 0.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.5kW. | --> | C16 ex RATHDRUM | Rathdrum: T42 | Arklow |  | 53.0131 | -6.3272
MV/LV Substation TH***891 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0.01045 | 0 | 0 | Constrained,otherwise capacity available =47.1kW. | --> | C16 ex BANTRY | Bantry: T41∥T42 | Ballylicky |  | 51.6837 | -9.4368
MV/LV Substation TH***892 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.368 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.3991 | 0 |  | --> | C14 ex LITTLE BRAY | Little Bray: T42 | Fassaroe |  | 53.2041 | -6.115
MV/LV Substation TH***892 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.051 | 4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10755 | 0 |  | --> | C12 ex ROSS CARBERY | Ross Carbery: T41∥T42 | Dunmanway |  | 51.5821 | -9.0294
MV/LV Substation TH***895Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 1.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.2kW. | --> | E21 ex CASTLETOWNBERE | Castletownbere: T421 | Ballylicky |  | 51.6642 | -9.809
MV/LV Substation TH***897 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =170kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20474 | 0 |  | --> | C15 ex LITTLE BRAY | Little Bray: T41 | Fassaroe |  | 53.2133 | -6.1073
MV/LV Substation TH***897Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C15 ex PORTARLINGTON | Portarlington: T41∥T42 | Portlaoise |  | 53.1576 | -7.1803
MV/LV Substation TH***898 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =126kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01615 | 0.1945 | 0 |  | --> | C18 ex DOUGLAS | Douglas: T41 | Trabeg |  | 51.8748 | -8.4289
MV/LV Substation TH***899 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 7.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05325 | 0 |  | --> | E05 ex MARSHES | Marshes: T423 | Dundalk |  | 53.9629 | -6.4931
MV/LV Substation TH***900 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.158 | 8.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20661 | 0 |  | --> | C21 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9923 | -6.0822
MV/LV Substation TH***902 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.344 | 1.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.39886 | 0 |  | --> | C18 ex KINGSCOURT | Kingscourt: T42 | Meath Hill |  | 53.9075 | -6.8147
MV/LV Substation TH***902Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.186 | 4.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.19623 | 0 |  | --> | E18 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.2831 | -6.3961
MV/LV Substation TH***907 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 2.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05325 | 0 |  | --> | E18 ex STRANORLAR | Stranorlar: T422 | Letterkenny |  | 54.7949 | -7.6779
MV/LV Substation TH***908X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.057 | 0.1 | Constrained,otherwise capacity available =197kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20048 | 0 |  | --> | C16 ex OLDBAWN | Oldbawn: T42 | Cookstown |  | 53.2853 | -6.3643
MV/LV Substation TH***910Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.301 | 3.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.40754 | 0 |  | --> | C20 ex ATHY | Athy: T102 | Athy |  | 52.9824 | -6.9753
MV/LV Substation TH***912 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.166 | 3.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =205.4kW. | --> | C14 ex DERRYBEG | Derrybeg: T41∥T42 | Ardnagappary |  | 55.0654 | -8.2868
MV/LV Substation TH***912 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.335 | 0.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.40226 | 0 |  | --> | C15 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.8303 | -8.9905
MV/LV Substation TH***913 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =226kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0836 | 0.3389 | 0 |  | --> | C19 ex CARRICKMINES | Carrickmines: T41 | Carrickmines |  | 53.2639 | -6.2095
MV/LV Substation TH***913 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.361 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.3862 | 0 |  | --> | C17 ex GREYSTONES | Greystones: T41 | Fassaroe |  | 53.1396 | -6.0604
MV/LV Substation TH***915 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.108 | 8.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.04465 | 0.1672 | 0 |  | --> | C29 ex STEPHENSTOWN | Stephenstown: T101 | Finglas |  | 53.5966 | -6.1802
MV/LV Substation TH***915X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.164 | 2.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20568 | 0 |  | --> | E18 ex BLESSINGTON | Blessington: T422 | Kilteel |  | 53.2046 | -6.4
MV/LV Substation TH***916 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.323 | 10.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.40114 | 0 |  | --> | C29 ex PELLETSTOWN | Pelletstown: T101 | Finglas |  | 53.3708 | -6.3295
MV/LV Substation TH***916X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =264kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =421.2kW. | --> | C12 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.0891 | -7.6177
MV/LV Substation TH***916Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =364kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40572 | 0 |  | --> | C17 ex GARRYOWEN | Garryowen: T41 | Limerick |  | 52.6668 | -8.6155
MV/LV Substation TH***917Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.333 | 12.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0.39758 | 0 |  | --> | C19 ex MONREAD | Monread: T101 | Monread |  | 53.2331 | -6.6589
MV/LV Substation TH***918 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex WHITEHALL | Whitehall: T41 | Finglas |  | 53.3772 | -6.2674
MV/LV Substation TH***918 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.148 | 5.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.19715 | 0 |  | --> | E15 ex BALLYBUNION | Ballybunion: T421∥T422 | Trien |  | 52.5147 | -9.6701
MV/LV Substation TH***920Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =146kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0209 | 0.18646 | 0 |  | --> | E15 ex DULEEK | Duleek: T421∥T422 | Drybridge |  | 53.6601 | -6.4072
MV/LV Substation TH***921 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.7kW. | --> | E17 ex CHARLEVILLE | Charleville: T422 | Charleville |  | 52.3555 | -8.6875
MV/LV Substation TH***922X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 12.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex HEUSTON SQUARE | Heuston Square: T101 | Inchicore 110kv |  | 53.3445 | -6.2975
MV/LV Substation TH***923Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.358 | 7.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.39466 | 0 |  | --> | C21 ex ATHY | Athy: T101 | Athy |  | 52.9436 | -7.0461
MV/LV Substation TH***925X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =347kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4084 | 0 |  | --> | C11 ex MORRISTOWN | Morristown: T41∥T42 | Newbridge |  | 53.1728 | -6.8147
MV/LV Substation TH***926Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =183kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2027 | 0 |  | --> | C11 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1422 | -7.0613
MV/LV Substation TH***927Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =320kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0 | 0 | Constrained,otherwise capacity available =401.6kW. | --> | C15 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0479 | -7.3191
MV/LV Substation TH***928X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.151 | 2.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.19869 | 0 |  | --> | E13 ex AGHADA | Aghada: T721 | N/A |  | 51.8292 | -8.2255
MV/LV Substation TH***928X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =344kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.069851 | 0 | Constrained,otherwise capacity available =404.9kW. | --> | E20 ex BIRR | Birr: T422 | Dallow |  | 53.094 | -7.9141
MV/LV Substation TH***928Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =326kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =411.7kW. | --> | C15 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0488 | -7.3206
MV/LV Substation TH***931 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.232 | 1.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.426 | 0 |  | --> | C18 ex KINGSCOURT | Kingscourt: T42 | Meath Hill |  | 53.9063 | -6.8046
MV/LV Substation TH***931Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =287kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.41368 | 0 |  | --> | C15 ex MORRISTOWN | Morristown: T41∥T42 | Newbridge |  | 53.1873 | -6.8184
MV/LV Substation TH***932 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 5.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | E16 ex BALLYBUNION | Ballybunion: T421∥T422 | Trien |  | 52.4968 | -9.6581
MV/LV Substation TH***933 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.3kW. | --> | E17 ex CREESLOUGH | Creeslough: T421 | Ardnagappary |  | 55.177 | -7.9289
MV/LV Substation TH***933Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ROCHES STREET | Roches Street: T42 | Limerick |  | 52.6605 | -8.6309
MV/LV Substation TH***945Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =332kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0 | 0 | Constrained,otherwise capacity available =401.7kW. | --> | C15 ex PORTARLINGTON | Portarlington: T41∥T42 | Portlaoise |  | 53.1593 | -7.1787
MV/LV Substation TH***946Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =355kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0 | 0 | Constrained,otherwise capacity available =399.1kW. | --> | C15 ex PORTARLINGTON | Portarlington: T41∥T42 | Portlaoise |  | 53.1585 | -7.1774
MV/LV Substation TH***947Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex ATHLONE | Athlone: T41 | Athlone |  | 53.4217 | -7.9975
MV/LV Substation TH***948Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =167kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.069851 | 0 | Constrained,otherwise capacity available =205.2kW. | --> | E24 ex BIRR | Birr: T422 | Dallow |  | 53.1793 | -7.718
MV/LV Substation TH***951X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.153 | 1.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.0266 | 0.17938 | 0 |  | --> | C14 ex KELLS | Kells: T41∥T42 | Navan |  | 53.76 | -6.8387
MV/LV Substation TH***951Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =335kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.40426 | 0 |  | --> | C17 ex DOUGLAS | Douglas: T42 | Trabeg |  | 51.8663 | -8.4314
MV/LV Substation TH***952 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.174 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.20112 | 0 |  | --> | E16 ex BALLYCROSSAUN | Ballycrossaun: T421∥T422 | Somerset |  | 53.0939 | -8.2253
MV/LV Substation TH***952X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C15 ex CASTLECOMER | Castlecomer: T41∥T42 | Ballyragget |  | 52.8842 | -7.1526
MV/LV Substation TH***955Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 5.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053992 | 0 |  | --> | E16 ex WHITECHURCH | Whitechurch: T422 | Kilbarry |  | 51.9813 | -8.5103
MV/LV Substation TH***955Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =437kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex MOYLISH | Moylish: T41∥T42 | Ardnacrusha |  | 52.6815 | -8.6597
MV/LV Substation TH***956Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex MOYLISH | Moylish: T41∥T42 | Ardnacrusha |  | 52.6826 | -8.6587
MV/LV Substation TH***957Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex MOYLISH | Moylish: T41∥T42 | Ardnacrusha |  | 52.683 | -8.6605
MV/LV Substation TH***957Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 12.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C23 ex MONREAD | Monread: T101 | Monread |  | 53.2259 | -6.7431
MV/LV Substation TH***959X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.382 | 9.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40288 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.7972 | -9.5517
MV/LV Substation TH***965 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 0.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.7kW. | --> | C15 ex KANTURK | Kanturk: T41∥T42 | Glenlara |  | 52.1661 | -8.8202
MV/LV Substation TH***965X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.335 | 8.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.39526 | 0 |  | --> | C21 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9876 | -6.0876
MV/LV Substation TH***966Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.165 | 3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20152 | 0 |  | --> | C16 ex LOUGHANALLA | Loughanalla: T41∥T42 | Mullingar |  | 53.6756 | -7.2923
MV/LV Substation TH***969Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =288kVA. | --> | 0.38 | 0 | 0 | 0 | 0.07125 | 0.34252 | 0 |  | --> | C21 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7636 | -6.2662
MV/LV Substation TH***974X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =168kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20506 | 0 |  | --> | C15 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.846 | -8.3118
MV/LV Substation TH***974X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.272 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41996 | 0 |  | --> | C20 ex MANOR STREET | Manor Street: T42 | Waterford |  | 52.2486 | -7.1186
MV/LV Substation TH***976X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =381kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40304 | 0 |  | --> | C15 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8516 | -8.2855
MV/LV Substation TH***978X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.6kW. | --> | C22 ex PORTLAOISE | Portlaoise: T42 | Portlaoise |  | 53.0587 | -7.208
MV/LV Substation TH***983Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 10.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10174 | 0 |  | --> | C24 ex MULLINGAR | Mullingar: T102 | Mullingar |  | 53.5974 | -7.3826
MV/LV Substation TH***984 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | E18 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.5523 | -6.2098
MV/LV Substation TH***984X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.052 | 2.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1074 | 0 |  | --> | C16 ex PORTLAW | Portlaw: T41∥T42 | Butlerstown |  | 52.2838 | -7.3147
MV/LV Substation TH***990 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 3.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C19 ex KINGSCOURT | Kingscourt: T41 | Meath Hill |  | 53.8717 | -6.7877
MV/LV Substation TH***990Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.329 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.4012 | 0 |  | --> | E13 ex TULLOW | Tullow: T421 | Carlow |  | 52.7369 | -6.773
MV/LV Substation TH***991X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 7 |  | --> | 0.095 | 0 | 0 | 0 | 0.0171 | 0.086535 | 0 |  | --> | C12 ex ARDGEEHA | Ardgeeha: T41∥T42 | Doon |  | 52.3695 | -7.6997
MV/LV Substation TH***994X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.139 | 2.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =209.5kW. | --> | C20 ex KILRUSH | Kilrush: T41∥T42 | Tullabrack |  | 52.7474 | -9.4943
MV/LV Substation TH***997Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.338 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.4008 | 0 |  | --> | C19 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3268 | -6.4975
MV/LV Substation TH***998X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C35 ex SEMPERIT | Semperit: T43 | Grange Castle |  | 53.3232 | -6.352
MV/LV Substation TH***999 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.081 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =218.2kW. | --> | E17 ex BELMULLET | Belmullet: T421 | Bellacorick |  | 54.2265 | -9.9905
MV/LV Substation TH***999X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 51.8281 | -10.2704
MV/LV Substation TI***002X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 9.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10111 | 0 |  | --> | C12 ex CONVOY | Convoy: T41∥T42 | Letterkenny |  | 54.8268 | -7.7452
MV/LV Substation TI***002Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052647 | 0 |  | --> | C18 ex DEERPARK | Deerpark: T41∥T42 | Ballydine |  | 52.4648 | -7.5528
MV/LV Substation TI***005 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.234 | 5.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4257 | 0 |  | --> | E17 ex MOY | Moy: T421∥T422 | Moy |  | 54.1159 | -9.1641
MV/LV Substation TI***010 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =99kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0 | 0 | Constrained,otherwise capacity available =94.2kW. | --> | C11 ex TIMOLEAGUE | Timoleague: T41 | Bandon |  | 51.6068 | -8.7338
MV/LV Substation TI***022 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =41.9kW. | --> | C11 ex RATHDRUM | Rathdrum: T42 | Arklow |  | 52.8762 | -6.2201
MV/LV Substation TI***023 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.345 | 7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4087 | 0 |  | --> | C13 ex ARDGEEHA | Ardgeeha: T41∥T42 | Doon |  | 52.3609 | -7.6879
MV/LV Substation TI***023 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.048 | 0 | Constrained,otherwise capacity available =80kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.21231 | 0 |  | --> | C19 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 53.0322 | -9.2894
MV/LV Substation TI***025 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 8.3 |  | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0.09559 | 0 |  | --> | C25 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9969 | -6.0652
MV/LV Substation TI***027 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.04 | 0 | Constrained,otherwise capacity available =148kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0114 | 0.19615 | 0 |  | --> | C11 ex GRAIGUENAMANAGH | Graiguenamanagh: T41∥T42 | Kilkenny |  | 52.5384 | -6.9524
MV/LV Substation TI***035 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =499kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0019 | 0.39433 | 0 | Constrained,otherwise capacity available =500kW. | --> | C17 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.7512 | -7.957
MV/LV Substation TI***042 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.044 | 3.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =213.5kW. | --> | C17 ex BALLYSHANNON | Ballyshannon: T41∥T42 | Cathaleens Fall |  | 54.5036 | -8.1897
MV/LV Substation TI***042X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 2.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =41.4kW. | --> | E17 ex BALLYMACARRY | Ballymacarry: T421 | Trillick |  | 55.0684 | -7.4352
MV/LV Substation TI***050 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 0 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0534 | 0 |  | --> | C11 ex GRAIGUENAMANAGH | Graiguenamanagh: T41∥T42 | Kilkenny |  | 52.5351 | -6.9495
MV/LV Substation TI***051Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10315 | 0 |  | --> | C14 ex DRYBRIDGE | Drybridge: T42 | Drybridge |  | 53.79 | -6.4219
MV/LV Substation TI***061X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.33 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41104 | 0 |  | --> | E19 ex KENMARE | Kenmare: T421 | Knockearagh |  | 51.8998 | -9.6068
MV/LV Substation TI***064X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.053525 | 0 |  | --> | C16 ex CARRAROE | Carraroe: T42 | Screeb |  | 53.0627 | -9.5305
MV/LV Substation TI***065X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =249kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.41346 | 0 |  | --> | C22 ex GARRYOWEN | Garryowen: T42 | Limerick |  | 52.6526 | -8.5916
MV/LV Substation TI***068 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex BALLYBEGGAN | Ballybeggan: T43∥T44 | Tralee |  | 52.2726 | -9.6836
MV/LV Substation TI***070Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C20 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.2977 | -6.5792
MV/LV Substation TI***074 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.312 | 5.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41384 | 0 |  | --> | C22 ex CLOON | Cloon: T42 | Cloon |  | 53.5079 | -8.8562
MV/LV Substation TI***074Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =28kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0534 | 0 |  | --> | C16 ex CLONES | Clones: T41∥T42 | Shankill |  | 54.205 | -7.229
MV/LV Substation TI***075 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8607 | -8.2971
MV/LV Substation TI***078 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E16 ex GARRANACANTY | Garranacanty: T422 | Tipperary |  | 52.4727 | -8.1587
MV/LV Substation TI***080 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | C18 ex BALLYBAY | Ballybay: T41∥T42 | Lisdrum |  | 54.1733 | -6.9495
MV/LV Substation TI***114Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0152 | 0.034002 | 0 |  | --> | C14 ex SMEARLA | Smearla: T42 | Trien |  | 52.5708 | -9.3713
MV/LV Substation TI***116 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.391 | 2.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.01425 | 0.5 | 0 |  | --> | C20 ex SALLYNOGGIN ROAD | Sallynoggin Road: T42 | Cherrywood |  | 53.2886 | -6.1391
MV/LV Substation TI***119X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.481 | 1.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex SANDYFORD | Sandyford: T41 | Carrickmines |  | 53.2679 | -6.2454
MV/LV Substation TI***134X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.307 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.3946 | 0 |  | --> | C19 ex SANDYFORD | Sandyford: T41 | Carrickmines |  | 53.2691 | -6.2449
MV/LV Substation TI***140Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 2.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | E18 ex BLESSINGTON | Blessington: T422 | Kilteel |  | 53.2116 | -6.4839
MV/LV Substation TI***147X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 5.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C22 ex CLOON | Cloon: T42 | Cloon |  | 53.5047 | -8.8592
MV/LV Substation TI***157X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 1.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10016 | 0 |  | --> | E13 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.8 | -6.4748
MV/LV Substation TI***158X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.013 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00285 | 0.052585 | 0 |  | --> | E13 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.7973 | -6.4742
MV/LV Substation TI***158Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.38 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4032 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.7985 | -6.8942
MV/LV Substation TI***160X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.044 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.21847 | 0 |  | --> | E13 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.7993 | -6.4661
MV/LV Substation TI***162X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 1.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10575 | 0 |  | --> | E13 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.8036 | -6.4721
MV/LV Substation TI***165Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =31kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.04695 | 0 |  | --> | E20 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9849 | -6.8075
MV/LV Substation TI***168Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C12 ex KILMAGIG | Kilmagig: T42 | Arklow |  | 52.8606 | -6.2157
MV/LV Substation TI***168Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =177kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01425 | 0.18865 | 0 |  | --> | E20 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9904 | -6.8041
MV/LV Substation TI***173Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05142 | 0 |  | --> | E20 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9982 | -6.7973
MV/LV Substation TI***182 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 0.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | E15 ex KILMAGIG | Kilmagig: T42 | Arklow |  | 52.8564 | -6.3177
MV/LV Substation TI***192Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E20 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 53.0025 | -6.8068
MV/LV Substation TI***196Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.7986 | -6.8915
MV/LV Substation TI***197Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.03135 | 0 | 0 | Constrained,otherwise capacity available =20.7kW. | --> | C17 ex FOYNES | Foynes: T41 | Rathkeale |  | 52.5529 | -9.2233
MV/LV Substation TI***199Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =77kVA. | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.098615 | 0 |  | --> | E20 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9858 | -6.8094
MV/LV Substation TI***200 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 4.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E11 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.1934 | -6.492
MV/LV Substation TI***201Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =364kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =405.7kW. | --> | E19 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 53.028 | -7.2914
MV/LV Substation TI***203 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 9.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C14 ex KILCOOLE | Kilcoole: T41∥T42 | Fassaroe |  | 53.0895 | -6.1585
MV/LV Substation TI***224 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.12 | 0.1 | Constrained,otherwise capacity available =357kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40682 | 0 |  | --> | C16 ex CREGG ROAD | Cregg Road: T41∥T42 | Ballydine |  | 52.3494 | -7.3933
MV/LV Substation TI***229 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 11.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.9kW. | --> | E15 ex WESTPORT | Westport: T421∥T422 | Castlebar |  | 53.8028 | -9.4741
MV/LV Substation TI***239X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 1.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =104.1kW. | --> | E14 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1475 | -7.4611
MV/LV Substation TI***242X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.325 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.40282 | 0 |  | --> | E17 ex EDGEWORTHSTOWN | Edgeworthstown: T421∥T422 | Richmond |  | 53.6998 | -7.6157
MV/LV Substation TI***245X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E12 ex CARNDONAGH | Carndonagh: T421∥T422 | Trillick |  | 55.2597 | -7.2782
MV/LV Substation TI***259 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.12 | 0.1 | Constrained,otherwise capacity available =167kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20521 | 0 |  | --> | C23 ex CREGG ROAD | Cregg Road: T41∥T42 | Ballydine |  | 52.3579 | -7.3913
MV/LV Substation TI***262X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 0.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CAMDEN ROW | Camden Row: T41 | Francis Street |  | 53.3417 | -6.2754
MV/LV Substation TI***266X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.376 | 5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40382 | 0 |  | --> | C23 ex KILMORE | Kilmore: T101 | Finglas |  | 53.403 | -6.2227
MV/LV Substation TI***268Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.199 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20016 | 0 |  | --> | E13 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.7909 | -6.458
MV/LV Substation TI***274Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex MAYFIELD | Mayfield: T42 | Kilbarry |  | 51.9034 | -8.4278
MV/LV Substation TI***287Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex ARTANE | Artane: T101 | Finglas |  | 53.3848 | -6.211
MV/LV Substation TI***288Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 11.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex ARTANE | Artane: T101 | Finglas |  | 53.3836 | -6.2123
MV/LV Substation TI***296 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =95kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0.0908 | 0 |  | --> | E14 ex BIRDHILL | Birdhill: T422 | Ardnacrusha |  | 52.8293 | -8.2668
MV/LV Substation TI***297Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =368kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =405.1kW. | --> | C14 ex DRUMBEAR | Drumbear: T41∥T42 | Lisdrum |  | 54.2474 | -6.9651
MV/LV Substation TI***309Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 3.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.2kW. | --> | C12 ex TELAYDON | Telaydon: T42 | Lisdrum |  | 54.2789 | -6.9703
MV/LV Substation TI***311 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.452 | 1.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0.02945 | 0.5 | 0 |  | --> | C18 ex HEADFORD ROAD | Headford Road: T42 | Galway 110kv |  | 53.2896 | -9.0468
MV/LV Substation TI***324 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =88kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1019 | 0 |  | --> | C11 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.6582 | -7.8311
MV/LV Substation TI***328 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.307 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.0266 | 0.3866 | 0 |  | --> | C18 ex HEADFORD ROAD | Headford Road: T42 | Galway 110kv |  | 53.2917 | -9.0454
MV/LV Substation TI***329 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.304 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.40608 | 0 |  | --> | C18 ex HEADFORD ROAD | Headford Road: T42 | Galway 110kv |  | 53.2907 | -9.0436
MV/LV Substation TI***334Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.148 | 1.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0.20615 | 0 |  | --> | C11 ex DERRYCRAMPH | Derrycramph: T41∥T42 | Shankill |  | 53.9781 | -7.351
MV/LV Substation TI***340X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex PARKMORE | Parkmore: T41∥T42 | Galway 110kv |  | 53.2915 | -8.9921
MV/LV Substation TI***340Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 3.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | C12 ex TELAYDON | Telaydon: T42 | Lisdrum |  | 54.2795 | -6.9696
MV/LV Substation TI***344 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 26.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0531 | 0 |  | --> | E21 ex WEXFORD | Wexford: T121∥T122 | Wexford |  | 52.4161 | -6.5239
MV/LV Substation TI***347X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =385kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4024 | 0 |  | --> | C15 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.9504 | -7.6969
MV/LV Substation TI***353 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052647 | 0 |  | --> | E17 ex MILLTOWN (SR) | Milltown (sr): T421 | Oughtragh |  | 52.1204 | -9.7522
MV/LV Substation TI***362 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 4.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | E19 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.2797 | -6.9143
MV/LV Substation TI***365 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.249 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.01995 | 0.40246 | 0 |  | --> | C20 ex SALLYNOGGIN ROAD | Sallynoggin Road: T42 | Cherrywood |  | 53.2903 | -6.1406
MV/LV Substation TI***366Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.18 | 3.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.20018 | 0 |  | --> | C12 ex MAYFIELD | Mayfield: T42 | Kilbarry |  | 51.9054 | -8.4298
MV/LV Substation TI***372 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.158 | 3.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =201.6kW. | --> | C16 ex BALLYSHANNON | Ballyshannon: T41∥T42 | Cathaleens Fall |  | 54.5086 | -8.195
MV/LV Substation TI***381X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 1.9 |  | --> | 0.095 | 0 | 0 | 0 | 0.0038 | 0.10084 | 0 |  | --> | C11 ex DERRYCRAMPH | Derrycramph: T41∥T42 | Shankill |  | 53.9766 | -7.3498
MV/LV Substation TI***381Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 11.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.046477 | 0 |  | --> | C14 ex BALLYBEG | Ballybeg: T102 | Carrickmines |  | 52.9985 | -6.0874
MV/LV Substation TI***385X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.047107 | 0 |  | --> | C16 ex CLONES | Clones: T41∥T42 | Shankill |  | 54.1951 | -7.2273
MV/LV Substation TI***4015 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C13 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6619 | -8.0788
MV/LV Substation TI***4018 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E14 ex EMYVALE | Emyvale: T422 | Lisdrum |  | 54.339 | -6.9904
MV/LV Substation TI***402 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =81kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =103kW. | --> | C20 ex ROSCREA | Roscrea: T42 | Ikerrin |  | 52.9574 | -7.8398
MV/LV Substation TI***4023 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 1.1 |  | --> | 0.095 | 0 | 0 | 0 | 0.0076 | 0.094685 | 0 |  | --> | E13 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.7969 | -6.4569
MV/LV Substation TI***4025 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C26 ex GLENTIES | Glenties: T41 | Binbane |  | 54.81 | -8.2362
MV/LV Substation TI***4033 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E19 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.2796 | -6.9165
MV/LV Substation TI***4073 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C18 ex LOUGHLINSTOWN | Loughlinstown: T42 | Carrickmines |  | 53.2359 | -6.1644
MV/LV Substation TI***4096 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.06 | 3.4 |  | --> | 0.095 | 0 | 0 | 0 | 0.0266 | 0 | 0 | Constrained,otherwise capacity available =78.2kW. | --> | C12 ex TELAYDON | Telaydon: T42 | Lisdrum |  | 54.2768 | -6.9653
MV/LV Substation TI***4112 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =33kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =42.6kW. | --> | C20 ex MOUNTMELLICK | Mountmellick: T41∥T42 | Portlaoise |  | 53.1236 | -7.2565
MV/LV Substation TI***4113 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C11 ex SCARIFF | Scariff: T42 | Ennis |  | 52.8666 | -8.4538
MV/LV Substation TI***4124 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex GARVILLE AVENUE | Garville Avenue: T42 | Milltown (dr) |  | 53.3203 | -6.2798
MV/LV Substation TI***4132 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E11 ex LUMCLOON | Lumcloon: T421∥T422 | Dallow |  | 53.1896 | -7.9328
MV/LV Substation TI***4134 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C12 ex MAYFIELD | Mayfield: T42 | Kilbarry |  | 51.9063 | -8.4296
MV/LV Substation TI***4144 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.8 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex BALLYBODEN | Ballyboden: T42 | Cookstown |  | 53.2801 | -6.3122
MV/LV Substation TI***419 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.047885 | 0 |  | --> | C15 ex BLAKE | Blake: T41∥T42 | Blake |  | 53.3285 | -6.8436
MV/LV Substation TI***425Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.39433 | 0 | Constrained,otherwise capacity available =400kW. | --> | C12 ex LOUGHTAGALLA | Loughtagalla: T41∥T42 | Thurles |  | 52.6592 | -7.7953
MV/LV Substation TI***4308 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E11 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.195 | -6.4958
MV/LV Substation TI***4310 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C15 ex BLAKE | Blake: T41∥T42 | Blake |  | 53.3383 | -6.8409
MV/LV Substation TI***4316 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.412 | 5.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0342 | 0.5 | 0 |  | --> | E13 ex BLESSINGTON | Blessington: T421 | Kilteel |  | 53.1365 | -6.6149
MV/LV Substation TI***4339 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C30 ex KINSALE | Kinsale: T41∥T42 | Bandon |  | 51.715 | -8.5801
MV/LV Substation TI***437 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =36kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.2kW. | --> | E11 ex FERNS | Ferns: T421 | Crane |  | 52.6166 | -6.5159
MV/LV Substation TI***4421 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | E12 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 52.9701 | -7.2116
MV/LV Substation TI***448 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C11 ex JOHNSTOWN | Johnstown: T41 | Kilteel |  | 53.2123 | -6.6247
MV/LV Substation TI***4519 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 26.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E12 ex WEXFORD | Wexford: T121∥T122 | Wexford |  | 52.402 | -6.5785
MV/LV Substation TI***456Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =152kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20754 | 0 |  | --> | C41 ex CASTLEVIEW | Castleview: T101 | Castleview |  | 51.9026 | -8.4275
MV/LV Substation TI***468Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =80kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10315 | 0 |  | --> | C17 ex LOUGHREA | Loughrea: T41∥T42 | Somerset |  | 53.2043 | -8.5835
MV/LV Substation TI***483X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10111 | 0 |  | --> | E17 ex MILLTOWN (SR) | Milltown (sr): T421 | Oughtragh |  | 52.1212 | -9.7517
MV/LV Substation TI***489X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.0471 | 0 |  | --> | C15 ex KILMARTIN | Kilmartin: T41 | Arklow |  | 53.0665 | -6.0975
MV/LV Substation TI***490 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 2.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.3kW. | --> | E17 ex BALLYMACARRY | Ballymacarry: T421 | Trillick |  | 55.0653 | -7.4226
MV/LV Substation TI***490 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 1.6 |  | --> | 0.095 | 0 | 0 | 0 | 0.01045 | 0.09215 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.7986 | -6.8993
MV/LV Substation TI***498 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.322 | 5.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41228 | 0 |  | --> | C22 ex CLOON | Cloon: T42 | Cloon |  | 53.5094 | -8.8518
MV/LV Substation TI***498Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.04673 | 0 |  | --> | C14 ex DRYBRIDGE | Drybridge: T42 | Drybridge |  | 53.7916 | -6.424
MV/LV Substation TI***499 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.365 | 5.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.39956 | 0 |  | --> | C22 ex CLOON | Cloon: T42 | Cloon |  | 53.5081 | -8.8524
MV/LV Substation TI***499Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.027 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.04355 | 0 |  | --> | C14 ex DRYBRIDGE | Drybridge: T42 | Drybridge |  | 53.7915 | -6.4217
MV/LV Substation TI***502X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.125 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.0171 | 0.19365 | 0 |  | --> | E13 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.7961 | -6.4554
MV/LV Substation TI***502X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 1.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10111 | 0 |  | --> | C11 ex DERRYCRAMPH | Derrycramph: T41∥T42 | Shankill |  | 53.949 | -7.1912
MV/LV Substation TI***503Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10315 | 0 |  | --> | C14 ex DRYBRIDGE | Drybridge: T42 | Drybridge |  | 53.7985 | -6.425
MV/LV Substation TI***508X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E13 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.7904 | -6.4524
MV/LV Substation TI***516 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | C11 ex JOHNSTOWN | Johnstown: T41 | Kilteel |  | 53.2056 | -6.6209
MV/LV Substation TI***524X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.119 | 0.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =212.5kW. | --> | C15 ex GARRYSPILLANE | Garryspillane: T41 | Tipperary |  | 52.4024 | -8.2966
MV/LV Substation TI***526X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 26.8 |  | --> | 0.095 | 0 | 0 | 0 | 0.00285 | 0.099685 | 0 |  | --> | E21 ex WEXFORD | Wexford: T121∥T122 | Wexford |  | 52.418 | -6.5299
MV/LV Substation TI***535X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C14 ex BALLYMOUNT | Ballymount: T42 | Inchicore 110kv |  | 53.3185 | -6.3598
MV/LV Substation TI***537X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E11 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.1977 | -6.4971
MV/LV Substation TI***544Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E14 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.3211 | -6.9562
MV/LV Substation TI***548Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.058 | 1.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1065 | 0 |  | --> | C20 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.2956 | -6.5677
MV/LV Substation TI***556Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.328 | 5.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41136 | 0 |  | --> | C21 ex BALLINCOLLIG | Ballincollig: T41 | Kilbarry |  | 51.8877 | -8.5882
MV/LV Substation TI***559 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C11 ex SCARIFF | Scariff: T42 | Ennis |  | 52.866 | -8.4501
MV/LV Substation TI***560Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =92kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101.3kW. | --> | E17 ex BEALISTOWN | Bealistown: T421 | Great Island |  | 52.2355 | -6.8393
MV/LV Substation TI***566 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.019 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.054725 | 0 |  | --> | C20 ex KILMARTIN | Kilmartin: T41 | Arklow |  | 53.0238 | -6.1628
MV/LV Substation TI***566X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex ORANMORE | Oranmore: T41 | Galway 110kv |  | 53.2686 | -8.9291
MV/LV Substation TI***576X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 2.1 |  | --> | 0.095 | 0 | 0 | 0 | 0.38 | 0 | 0 |  | --> | E11 ex NEWPORT | Newport: T421 | Carrowbeg |  | 53.8808 | -9.4559
MV/LV Substation TI***582 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C15 ex KILMARTIN | Kilmartin: T41 | Arklow |  | 53.0697 | -6.0926
MV/LV Substation TI***586Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =295kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.40546 | 0 |  | --> | E14 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.4578 | -7.1103
MV/LV Substation TI***593 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.013 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =55.6kW. | --> | C16 ex KILCLOHER | Kilcloher: T42 | Dungarvan |  | 52.1589 | -7.8358
MV/LV Substation TI***601Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E16 ex GLENAMADDY | Glenamaddy: T422 | Athlone |  | 53.5843 | -8.6473
MV/LV Substation TI***605Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =405kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.01995 | 0.5 | 0 |  | --> | C22 ex MIDLETON | Midleton: T102 | Midleton |  | 51.9301 | -8.1877
MV/LV Substation TI***612 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E16 ex MILLTOWN (SR) | Milltown (sr): T422 | Oughtragh |  | 52.1201 | -9.7615
MV/LV Substation TI***616 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C12 ex ROSSGEIR | Rossgeir: T41∥T42 | Letterkenny |  | 54.7947 | -7.613
MV/LV Substation TI***616Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.171 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.19859 | 0 |  | --> | C18 ex SLANE | Slane: T42 | Drybridge |  | 53.7783 | -6.4774
MV/LV Substation TI***619 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 9.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C14 ex KILCOOLE | Kilcoole: T41∥T42 | Fassaroe |  | 53.0927 | -6.1639
MV/LV Substation TI***633X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05142 | 0 |  | --> | C12 ex SPIDDAL | Spiddal: T42 | Screeb |  | 53.2452 | -9.3524
MV/LV Substation TI***639 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C21 ex PORTARLINGTON | Portarlington: T43 | Blake |  | 53.1416 | -7.1594
MV/LV Substation TI***649X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C11 ex MOUNTMELLICK | Mountmellick: T41∥T42 | Portlaoise |  | 53.1404 | -7.4731
MV/LV Substation TI***658 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | C15 ex DUNGLOE | Dungloe: T42 | Ardnagappary |  | 54.8525 | -8.3141
MV/LV Substation TI***661X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.025 | 0.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.048845 | 0 |  | --> | C11 ex RIVERSTOWN | Riverstown: T41∥T42 | Kilbarry |  | 52.0138 | -8.3424
MV/LV Substation TI***662X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.358 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40666 | 0 |  | --> | C17 ex STICKILLEN | Stickillen: T41∥T42 | Drybridge |  | 53.8557 | -6.5358
MV/LV Substation TI***692Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.12 | 0.1 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CREGG ROAD | Cregg Road: T41∥T42 | Ballydine |  | 52.3524 | -7.3915
MV/LV Substation TI***701 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.343 | 1.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40902 | 0 |  | --> | C16 ex SCREEB | Screeb: T41 | Screeb |  | 53.2747 | -9.6618
MV/LV Substation TI***705X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E11 ex ARDFINNAN | Ardfinnan: T421 | Cahir |  | 52.2586 | -7.8919
MV/LV Substation TI***706 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =14kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.055442 | 0 |  | --> | E16 ex GLENAMADDY | Glenamaddy: T422 | Athlone |  | 53.581 | -8.6535
MV/LV Substation TI***708 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 1.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10206 | 0 |  | --> | C16 ex SCREEB | Screeb: T41 | Screeb |  | 53.2666 | -9.6656
MV/LV Substation TI***708 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05295 | 0 |  | --> | C14 ex DRYBRIDGE | Drybridge: T42 | Drybridge |  | 53.7718 | -6.4291
MV/LV Substation TI***717 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.157 | 0.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =206.8kW. | --> | E12 ex CARNDONAGH | Carndonagh: T421∥T422 | Trillick |  | 55.2577 | -7.2759
MV/LV Substation TI***725 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C12 ex WOODFORD | Woodford: T41∥T42 | Knockearagh |  | 52.0735 | -9.4459
MV/LV Substation TI***734X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =19kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =54.7kW. | --> | E12 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 52.962 | -7.2012
MV/LV Substation TI***746 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 2.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.2kW. | --> | E17 ex BALLYMACARRY | Ballymacarry: T421 | Trillick |  | 55.0652 | -7.4261
MV/LV Substation TI***777 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0 | 0 | Constrained,otherwise capacity available =47.3kW. | --> | C20 ex ROSCREA | Roscrea: T42 | Ikerrin |  | 52.9551 | -7.8338
MV/LV Substation TI***780X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.04616 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.8011 | -6.8969
MV/LV Substation TI***781X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.155 | 7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0076 | 0.19907 | 0 |  | --> | C13 ex ARDGEEHA | Ardgeeha: T41∥T42 | Doon |  | 52.361 | -7.6841
MV/LV Substation TI***786X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =172kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =204.4kW. | --> | C11 ex TIMOLEAGUE | Timoleague: T41 | Bandon |  | 51.642 | -8.7672
MV/LV Substation TI***788Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.6kW. | --> | E17 ex BEALISTOWN | Bealistown: T421 | Great Island |  | 52.2478 | -6.8381
MV/LV Substation TI***789Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =94kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101kW. | --> | E12 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 52.9634 | -7.1989
MV/LV Substation TI***794 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =144kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =208.8kW. | --> | E12 ex FERNS | Ferns: T421 | Crane |  | 52.5746 | -6.5451
MV/LV Substation TI***797 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =32kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.8kW. | --> | E12 ex FERNS | Ferns: T421 | Crane |  | 52.5587 | -6.5567
MV/LV Substation TI***797 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 1.6 |  | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0.09284 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.8007 | -6.901
MV/LV Substation TI***815Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | E19 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.2798 | -6.918
MV/LV Substation TI***832Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.04532 | 0 |  | --> | C11 ex JOHNSTOWN | Johnstown: T41 | Kilteel |  | 53.2164 | -6.6384
MV/LV Substation TI***834Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E18 ex BLESSINGTON | Blessington: T422 | Kilteel |  | 53.2151 | -6.4712
MV/LV Substation TI***842 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05219 | 0 |  | --> | C13 ex SANDYFORD | Sandyford: T41 | Carrickmines |  | 53.26 | -6.2939
MV/LV Substation TI***849Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.172 | 2.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20443 | 0 |  | --> | E18 ex BLESSINGTON | Blessington: T422 | Kilteel |  | 53.2096 | -6.4902
MV/LV Substation TI***863 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 4.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | E21 ex ATHENRY | Athenry: T423 | Galway 110kv |  | 53.3484 | -8.7087
MV/LV Substation TI***867X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E12 ex KILCULLEN | Kilcullen: T424 | Stratford |  | 53.0791 | -6.8293
MV/LV Substation TI***880 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.188 | 1.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20191 | 0 |  | --> | E18 ex GARRANACANTY | Garranacanty: T422 | Tipperary |  | 52.5004 | -8.2089
MV/LV Substation TI***882 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =12kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0076 | 0 | 0 | Constrained,otherwise capacity available =219.9kW. | --> | C11 ex TIMOLEAGUE | Timoleague: T41 | Bandon |  | 51.6442 | -8.7668
MV/LV Substation TI***888X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.187 | 5.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20207 | 0 |  | --> | E18 ex CRANE | Crane: T122 | Crane |  | 52.5161 | -6.2895
MV/LV Substation TI***892X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =88kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1019 | 0 |  | --> | C11 ex GARDEN CITY | Garden City: T41∥T42 | Arklow |  | 52.7129 | -6.2667
MV/LV Substation TI***905 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =92kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10128 | 0 |  | --> | E17 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.89 | -6.619
MV/LV Substation TI***905 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 7.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.045575 | 0 |  | --> | C23 ex ATHY | Athy: T101 | Athy |  | 52.9016 | -6.9931
MV/LV Substation TI***913X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 2.3 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E18 ex BLESSINGTON | Blessington: T422 | Kilteel |  | 53.2092 | -6.4909
MV/LV Substation TI***921 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C20 ex KINGSCOURT | Kingscourt: T42 | Meath Hill |  | 53.8411 | -6.6819
MV/LV Substation TI***932 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 1.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10315 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.7952 | -6.895
MV/LV Substation TI***941 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.047885 | 0 |  | --> | C15 ex DEERPARK | Deerpark: T41∥T42 | Ballydine |  | 52.3365 | -7.3761
MV/LV Substation TI***944Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E12 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 52.9487 | -7.2279
MV/LV Substation TI***960 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 5.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | E20 ex CLARA | Clara: T422 | Thornsberry |  | 53.3011 | -7.4814
MV/LV Substation TI***969Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | E19 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.284 | -6.9117
MV/LV Substation TI***991X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.05 | 8.3 |  | --> | 0.095 | 0 | 0 | 0 | 0.019 | 0.08769 | 0 |  | --> | C21 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9946 | -6.0761
MV/LV Substation TI***997 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.04532 | 0 |  | --> | C15 ex KILMARTIN | Kilmartin: T41 | Arklow |  | 53.0517 | -6.0728
MV/LV Substation TK***688Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 5.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex MCDONAGH | Mcdonagh: T41 | Kilkenny |  | 52.6561 | -7.244
MV/LV Substation TL***269Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0.03895 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest: T101 | Inchicore 110kv |  | 53.2863 | -6.4316
MV/LV Substation TL***354Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 5.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C17 ex SANTRY | Santry: T41 | Finglas |  | 53.4052 | -6.2518
MV/LV Substation TM***4178 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E12 ex OLDCASTLE | Oldcastle: T422 | Mullingar |  | 53.7112 | -7.1576
MV/LV Substation TM***464Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E21 ex WHITECHURCH | Whitechurch: T421 | Kilbarry |  | 51.9714 | -8.4355
MV/LV Substation TO***001X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham: T41∥T42 | Letterkenny |  | 55.0072 | -7.4903
MV/LV Substation TO***003 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.318 | 4 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0 | 0 | Constrained,otherwise capacity available =409.9kW. | --> | C19 ex LISMORE | Lismore: T41∥T42 | Dungarvan |  | 52.1327 | -7.9307
MV/LV Substation TO***003 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.337 | 3.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =405kW. | --> | E14 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 51.9517 | -7.8486
MV/LV Substation TO***003 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.066 | 9.9 |  | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0.095295 | 0 |  | --> | C12 ex CONVOY | Convoy: T41∥T42 | Letterkenny |  | 54.8624 | -7.6695
MV/LV Substation TO***005X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10128 | 0 |  | --> | E17 ex INCH | Inch: T421∥T422 | Oughtragh |  | 52.2305 | -9.9248
MV/LV Substation TO***006Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.397 | 4.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40048 | 0 |  | --> | C12 ex GLEBE | Glebe: T41∥T42 | Richmond |  | 53.7238 | -7.8022
MV/LV Substation TO***008 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.177 | 0.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | C20 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.8311 | -9.0194
MV/LV Substation TO***009 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.095 | 0.1 | Constrained,otherwise capacity available =192kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20128 | 0 |  | --> | C22 ex CASTLEISLAND | Castleisland: T41∥T42 | Tralee |  | 52.2316 | -9.4412
MV/LV Substation TO***010Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.397 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40048 | 0 |  | --> | E21 ex CURRALEIGH | Curraleigh: T421∥T422 | Kilbarry |  | 51.9247 | -8.5932
MV/LV Substation TO***012 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.091 | 0.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0 | 0 | Constrained,otherwise capacity available =435.5kW. | --> | C16 ex BANTRY | Bantry: T41∥T42 | Ballylicky |  | 51.6799 | -9.4562
MV/LV Substation TO***013 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0114 | 0.5 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry: T42 | Tonroe |  | 54.0537 | -8.7382
MV/LV Substation TO***013Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.04619 | 0 |  | --> | E18 ex CURRALEIGH | Curraleigh: T421∥T422 | Kilbarry |  | 51.9221 | -8.6078
MV/LV Substation TO***015 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex GORT | Gort: T41∥T42 | Ennis |  | 53.0627 | -8.8236
MV/LV Substation TO***015Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =79kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21846 | 0 |  | --> | C13 ex GRANGE (DR) | Grange (dr): T41 | Grange (dr) |  | 53.4024 | -6.1788
MV/LV Substation TO***016X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C19 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 53.0462 | -9.2437
MV/LV Substation TO***017 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex KILCOLGAN | Kilcolgan: T42 | Galway 110kv |  | 53.2487 | -8.8871
MV/LV Substation TO***020 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.193 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20112 | 0 |  | --> | C15 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5516 | -6.7949
MV/LV Substation TO***020 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C11 ex LOUGHTAGALLA | Loughtagalla: T41∥T42 | Thurles |  | 52.6669 | -7.7645
MV/LV Substation TO***021Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =195kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2008 | 0 |  | --> | C11 ex ATHENRY | Athenry: T41∥T42 | Galway 110kv |  | 53.3232 | -8.8023
MV/LV Substation TO***023 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =191kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20144 | 0 |  | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9506 | -8.097
MV/LV Substation TO***026 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.157 | 4 |  | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0 | 0 | Constrained,otherwise capacity available =197.8kW. | --> | C19 ex LISMORE | Lismore: T41∥T42 | Dungarvan |  | 52.0946 | -8.0006
MV/LV Substation TO***026Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =259kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0171 | 0.40394 | 0 |  | --> | C20 ex TOGHER | Togher: T42 | Trabeg |  | 51.8769 | -8.4951
MV/LV Substation TO***027 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.285 | 4.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =413kW. | --> | E21 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.2554 | -6.9663
MV/LV Substation TO***033 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =63kVA. | --> | 0.095 | 0 | 0 | 0 | 0.00665 | 0 | 0 | Constrained,otherwise capacity available =98.7kW. | --> | C15 ex MOUNTMELLICK | Mountmellick: T41∥T42 | Portlaoise |  | 53.1223 | -7.3296
MV/LV Substation TO***033Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex SWORDS | Swords: T41 | Glasmore |  | 53.4573 | -6.2195
MV/LV Substation TO***034Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =336kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0 | 0 | Constrained,otherwise capacity available =406.1kW. | --> | C11 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.099 | -7.6015
MV/LV Substation TO***036 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.139 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20953 | 0 |  | --> | C18 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5611 | -6.7874
MV/LV Substation TO***036Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =334kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41042 | 0 |  | --> | C18 ex NAAS | Naas: T42 | Newbridge |  | 53.2067 | -6.7427
MV/LV Substation TO***037 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =157kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =206.8kW. | --> | C12 ex ROSCREA | Roscrea: T42 | Ikerrin |  | 52.9531 | -7.7944
MV/LV Substation TO***040 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.461 | 4.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C13 ex BUNDORAN | Bundoran: T41∥T42 | Cathaleens Fall |  | 54.4779 | -8.2805
MV/LV Substation TO***041 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.165 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20552 | 0 |  | --> | C20 ex ATHY | Athy: T102 | Athy |  | 52.9955 | -6.9905
MV/LV Substation TO***043 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 3.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =53.1kW. | --> | C17 ex BALLYSHANNON | Ballyshannon: T41∥T42 | Cathaleens Fall |  | 54.502 | -8.1742
MV/LV Substation TO***043Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.151 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.00665 | 0.20069 | 0 |  | --> | C12 ex LLOYD | Lloyd: T41∥T42 | Navan |  | 53.7272 | -6.8881
MV/LV Substation TO***044X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex ROCHES STREET | Roches Street: T41 | Limerick |  | 52.6631 | -8.6264
MV/LV Substation TO***061 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.305 | 7.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.39892 | 0 |  | --> | C21 ex ATHY | Athy: T101 | Athy |  | 52.9865 | -6.9952
MV/LV Substation TO***062Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.29 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.02185 | 0.39422 | 0 |  | --> | C17 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.7378 | -6.4178
MV/LV Substation TO***063X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =197kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20048 | 0 |  | --> | C30 ex CLAREGALWAY | Claregalway: T42 | Galway 110kv |  | 53.3952 | -9.0338
MV/LV Substation TO***069 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.016 | 0 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.055157 | 0 |  | --> | C19 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 53.113 | -9.1495
MV/LV Substation TO***069Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.141 | 1.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.01235 | 0.19622 | 0 |  | --> | C23 ex KELLS | Kells: T41∥T42 | Navan |  | 53.7168 | -6.8838
MV/LV Substation TO***072X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 3.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =103.3kW. | --> | E19 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 52.0932 | -8.0001
MV/LV Substation TO***073 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.393 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40112 | 0 |  | --> | C12 ex MONFIN | Monfin: T41∥T42 | Wexford |  | 52.4839 | -6.589
MV/LV Substation TO***075Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =84kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10253 | 0 |  | --> | E13 ex DALTON | Dalton: T421∥T422 | Dalton |  | 53.7206 | -8.9813
MV/LV Substation TO***080 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C19 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 53.051 | -9.2477
MV/LV Substation TO***082 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.023 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =54.1kW. | --> | C18 ex ATHBOY | Athboy: T42 | Navan |  | 53.6147 | -6.905
MV/LV Substation TO***083Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.452 | 2.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0.01425 | 0.5 | 0 |  | --> | C16 ex MALAHIDE | Malahide: T42 | Glasmore |  | 53.4356 | -6.1402
MV/LV Substation TO***084Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =107.8kW. | --> | E18 ex BUNCLODY | Bunclody: T421∥T422 | Crane |  | 52.6067 | -6.603
MV/LV Substation TO***085 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101.7kW. | --> | C19 ex LISMORE | Lismore: T41∥T42 | Dungarvan |  | 52.0927 | -8.0022
MV/LV Substation TO***088X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis: T41∥T42 | Dalton |  | 53.8099 | -8.7681
MV/LV Substation TO***091X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex SANDYFORD | Sandyford: T41 | Carrickmines |  | 53.2673 | -6.2364
MV/LV Substation TO***091X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.168 | 5.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20506 | 0 |  | --> | E14 ex MOY | Moy: T421∥T422 | Moy |  | 54.137 | -9.1681
MV/LV Substation TO***096 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052647 | 0 |  | --> | C15 ex DRUMQUIN | Drumquin: T42 | Ennis |  | 52.7544 | -9.1356
MV/LV Substation TO***096 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.265 | 4.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.05035 | 0.36804 | 0 |  | --> | C16 ex LAWLESSTOWN | Lawlesstown: T42 | Doon |  | 52.352 | -7.7288
MV/LV Substation TO***096Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C21 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7444 | -6.3276
MV/LV Substation TO***098 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =313kVA. | --> | 0.38 | 0 | 0 | 0 | 0.038 | 0 | 0 | Constrained,otherwise capacity available =373.7kW. | --> | C16 ex TOOMEVARA | Toomevara: T42 | Nenagh |  | 52.8488 | -8.037
MV/LV Substation TO***098 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 5.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E12 ex DUNMANWAY | Dunmanway: T422 | Dunmanway |  | 51.6443 | -9.1597
MV/LV Substation TO***103 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.292 | 10.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.40292 | 0 |  | --> | C12 ex ENNIS | Ennis: T102 | Ennis |  | 52.838 | -8.9784
MV/LV Substation TO***105 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.381 | 4.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.02375 | 0.37804 | 0 |  | --> | C16 ex LOUGHSHINNY | Loughshinny: T42 | Glasmore |  | 53.5775 | -6.1236
MV/LV Substation TO***105X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.227 | 0.2 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C16 ex DUNGLOE | Dungloe: T42 | Ardnagappary |  | 54.98 | -8.4398
MV/LV Substation TO***106X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.098 | 1.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21568 | 0 |  | --> | C17 ex BALLINDERRY | Ballinderry: T41 | Mullingar |  | 53.5273 | -7.3177
MV/LV Substation TO***108X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =180kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20318 | 0 |  | --> | E47 ex CLAREGALWAY | Claregalway: T421 | Galway 110kv |  | 53.3616 | -8.9237
MV/LV Substation TO***112 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.061 | 4.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.0665 | 0.15105 | 0 |  | --> | C16 ex LOUGHSHINNY | Loughshinny: T42 | Glasmore |  | 53.5774 | -6.1157
MV/LV Substation TO***116X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 10.8 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E11 ex COOLROE | Coolroe: T121 | Coolroe |  | 51.888 | -8.6079
MV/LV Substation TO***116X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 |  | --> | 0.5985 | 0 | 0 | 0 | 0.19 | 0.46137 | 0 |  | --> | C22 ex SEMPERIT | Semperit: T42 | Grange Castle |  | 53.3272 | -6.3591
MV/LV Substation TO***119 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E15 ex RATHMORE | Rathmore: T421 | Knockearagh |  | 52.1307 | -9.2928
MV/LV Substation TO***121 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.054 | 2.5 |  | --> | 0.095 | 0 | 0 | 0 | 0.00855 | 0.0981 | 0 |  | --> | C13 ex MONFIN | Monfin: T41∥T42 | Wexford |  | 52.481 | -6.5873
MV/LV Substation TO***125X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.041 | 6.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.0228 | 0.19989 | 0 |  | --> | C22 ex CARRICKMINES | Carrickmines: T42 | Carrickmines |  | 53.2579 | -6.1981
MV/LV Substation TO***126Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E19 ex GARRANACANTY | Garranacanty: T421 | Tipperary |  | 52.4118 | -7.9796
MV/LV Substation TO***130 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =179kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20333 | 0 |  | --> | C13 ex TUAM SOUTH | Tuam South: T42 | Cloon |  | 53.5141 | -8.8596
MV/LV Substation TO***134 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =66kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10529 | 0 |  | --> | E19 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.4527 | -7.0293
MV/LV Substation TO***143X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E33 ex TRIM | Trim: T421 | Navan |  | 53.4753 | -6.856
MV/LV Substation TO***144Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =97kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10048 | 0 |  | --> | E21 ex FINEA | Finea: T421∥T422 | Shankill |  | 53.865 | -7.3148
MV/LV Substation TO***147 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.018 | 5.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0152 | 0.038867 | 0 |  | --> | E18 ex WHITECHURCH | Whitechurch: T422 | Kilbarry |  | 51.9839 | -8.5148
MV/LV Substation TO***148Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 6.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C13 ex CASHEL | Cashel: T41 | Cahir |  | 52.5192 | -7.8785
MV/LV Substation TO***153Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.152 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20754 | 0 |  | --> | C15 ex GLENGOOLE | Glengoole: T41 | Thurles |  | 52.7154 | -7.5877
MV/LV Substation TO***154 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 1 |  | --> | 0.095 | 0 | 0 | 0 | 0.01425 | 0 | 0 | Constrained,otherwise capacity available =89.4kW. | --> | C25 ex KILCLOHER | Kilcloher: T42 | Dungarvan |  | 52.2042 | -7.7157
MV/LV Substation TO***154 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.281 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.00665 | 0.4116 | 0 |  | --> | C11 ex ABBEYLAND | Abbeyland: T41 | Navan |  | 53.6424 | -6.6951
MV/LV Substation TO***158Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C18 ex TOOMEVARA | Toomevara: T42 | Nenagh |  | 52.8477 | -8.0464
MV/LV Substation TO***159X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.268 | 12.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex TANEY | Taney: T101 | Carrickmines |  | 53.2878 | -6.2433
MV/LV Substation TO***160 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 3.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05219 | 0 |  | --> | C14 ex CAUSEWAY | Causeway: T41∥T42 | Tralee |  | 52.457 | -9.6601
MV/LV Substation TO***160X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.342 | 9.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex TANEY | Taney: T102 | Carrickmines |  | 53.2875 | -6.243
MV/LV Substation TO***161X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.306 | 9.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex TANEY | Taney: T102 | Carrickmines |  | 53.2864 | -6.2403
MV/LV Substation TO***162X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 12.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex TANEY | Taney: T101 | Carrickmines |  | 53.2867 | -6.2405
MV/LV Substation TO***163 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.184 | 2.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.41312 | 0 |  | --> | C19 ex COOLOCK | Coolock: T41 | Finglas |  | 53.3903 | -6.1837
MV/LV Substation TO***164Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C11 ex RAHEEN | Raheen: T41 | Limerick |  | 52.6029 | -8.6329
MV/LV Substation TO***165X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex ARDNAREE | Ardnaree: T42 | Moy |  | 54.1135 | -9.1567
MV/LV Substation TO***169Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =217kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.41724 | 0 |  | --> | C14 ex TOGHER | Togher: T42 | Trabeg |  | 51.8743 | -8.4956
MV/LV Substation TO***169Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C11 ex PORTLAOISE | Portlaoise: T41 | Portlaoise |  | 53.0237 | -7.3154
MV/LV Substation TO***172Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C11 ex PORTLAOISE | Portlaoise: T41 | Portlaoise |  | 53.0241 | -7.3133
MV/LV Substation TO***173Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C11 ex PORTLAOISE | Portlaoise: T41 | Portlaoise |  | 53.023 | -7.3211
MV/LV Substation TO***178 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C20 ex CASTLEBLAYNEY | Castleblayney: T42 | Dundalk |  | 54.0822 | -6.6795
MV/LV Substation TO***180Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =94kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10095 | 0 |  | --> | E15 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.6449 | -6.3121
MV/LV Substation TO***181 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.255 | 4.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.03895 | 0.38154 | 0 |  | --> | C15 ex BALLINCLEA | Ballinclea: T41 | Cherrywood |  | 53.2716 | -6.1022
MV/LV Substation TO***188X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.177 | 1.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | C13 ex SANDYFORD | Sandyford: T41 | Carrickmines |  | 53.2661 | -6.2367
MV/LV Substation TO***190 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.214 | 3.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.4097 | 0 |  | --> | C17 ex MONKSTOWN | Monkstown: T41 | Blackrock |  | 53.2987 | -6.1675
MV/LV Substation TO***192Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C21 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7437 | -6.3141
MV/LV Substation TO***193Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =137kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20983 | 0 |  | --> | E11 ex CAVAN | Cavan: T421 | Shankill |  | 54.0452 | -7.3176
MV/LV Substation TO***194Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =305kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41492 | 0 |  | --> | C14 ex CAVAN | Cavan: T42 | Shankill |  | 53.9908 | -7.3622
MV/LV Substation TO***196Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.44613 | 0 | Constrained,otherwise capacity available =500kW. | --> | C24 ex BALLYCOOLIN | Ballycoolin: T42 | Finglas |  | 53.3929 | -6.3778
MV/LV Substation TO***202 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.396 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40064 | 0 |  | --> | C11 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.718 | -6.3753
MV/LV Substation TO***202X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | C14 ex BALLYBEGGAN | Ballybeggan: T43∥T44 | Tralee |  | 52.2897 | -9.6734
MV/LV Substation TO***204X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =364kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40572 | 0 |  | --> | E18 ex BIRDHILL | Birdhill: T422 | Ardnacrusha |  | 52.7161 | -8.5017
MV/LV Substation TO***206X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 3.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.6kW. | --> | E20 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 51.9709 | -7.8667
MV/LV Substation TO***213Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E18 ex FINEA | Finea: T421∥T422 | Shankill |  | 53.7693 | -7.3377
MV/LV Substation TO***218 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.19 | 3.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.04275 | 0.38724 | 0 |  | --> | C21 ex DEANSGRANGE | Deansgrange: T41 | Carrickmines |  | 53.2699 | -6.1842
MV/LV Substation TO***221X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 12.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex TANEY | Taney: T101 | Carrickmines |  | 53.2879 | -6.2434
MV/LV Substation TO***222X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex TANEY | Taney: T102 | Carrickmines |  | 53.2875 | -6.2431
MV/LV Substation TO***223X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex TANEY | Taney: T102 | Carrickmines |  | 53.2863 | -6.2405
MV/LV Substation TO***224 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex WOODFORD | Woodford: T41∥T42 | Knockearagh |  | 52.0583 | -9.5063
MV/LV Substation TO***224X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 12.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex TANEY | Taney: T101 | Carrickmines |  | 53.2867 | -6.2403
MV/LV Substation TO***226X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 3.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052495 | 0 |  | --> | C17 ex CASTLEBLAYNEY | Castleblayney: T41 | Dundalk |  | 54.1203 | -6.7561
MV/LV Substation TO***235 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =108kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.2042 | 0 |  | --> | C12 ex SAGGART | Saggart: T41∥T42 | Grange Castle |  | 53.2782 | -6.4893
MV/LV Substation TO***236Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =316kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0 | 0 | Constrained,otherwise capacity available =398.2kW. | --> | C11 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.0989 | -7.6028
MV/LV Substation TO***242X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =91kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101.4kW. | --> | C13 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.697 | -8.0539
MV/LV Substation TO***243X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex EAST WALL ROAD | East Wall Road: T42 | Mcdermott |  | 53.3536 | -6.2165
MV/LV Substation TO***244 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 1.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052037 | 0 |  | --> | C11 ex RATHMORE | Rathmore: T42 | Knockearagh |  | 52.1283 | -9.3442
MV/LV Substation TO***244X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C12 ex ABBEYFEALE | Abbeyfeale: T42 | Trien |  | 52.3925 | -9.303
MV/LV Substation TO***247 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.289 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.01615 | 0.40038 | 0 |  | --> | E21 ex CURRALEIGH | Curraleigh: T421∥T422 | Kilbarry |  | 51.9253 | -8.607
MV/LV Substation TO***250Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.166 | 6.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20537 | 0 |  | --> | C11 ex MERVILLE | Merville: T41 | Finglas |  | 53.3811 | -6.3151
MV/LV Substation TO***254Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =72kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0.09438 | 0 |  | --> | C17 ex BALLYCOOLIN | Ballycoolin: T41 | Finglas |  | 53.4039 | -6.3158
MV/LV Substation TO***257Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E11 ex CAVAN | Cavan: T421 | Shankill |  | 54.0451 | -7.314
MV/LV Substation TO***257Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.187 | 9.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20207 | 0 |  | --> | C13 ex SINGLAND | Singland: T101 | Singland |  | 52.6659 | -8.6053
MV/LV Substation TO***259 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 7.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E19 ex BANOGE | Banoge: T122 | Banoge |  | 52.608 | -6.3161
MV/LV Substation TO***261X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52kW. | --> | C18 ex ATHBOY | Athboy: T42 | Navan |  | 53.6256 | -6.919
MV/LV Substation TO***263Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.8 |  | --> | 0.95 | 0 | 0 | 0 | 0.0475 | 0.5 | 0 |  | --> | C17 ex TRABEG | Trabeg: T102 | Trabeg |  | 51.8716 | -8.4743
MV/LV Substation TO***266Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.329 | 1.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0.3982 | 0 |  | --> | C18 ex DUNDALK | Dundalk: T41 | Dundalk |  | 54.0228 | -6.4281
MV/LV Substation TO***270X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C15 ex KILCAR | Kilcar: T41 | Binbane |  | 54.6251 | -8.5994
MV/LV Substation TO***275X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex GRANGE (DR) | Grange (dr): T42 | Grange (dr) |  | 53.3949 | -6.144
MV/LV Substation TO***279 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.291 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41206 | 0 |  | --> | C11 ex RINEANNA | Rineanna: T42 | Drumline |  | 52.7095 | -8.876
MV/LV Substation TO***282X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.177 | 3.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | C19 ex CAUSEWAY | Causeway: T41∥T42 | Tralee |  | 52.396 | -9.8306
MV/LV Substation TO***291Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C20 ex KILMARTIN | Kilmartin: T41 | Arklow |  | 53.0375 | -6.2167
MV/LV Substation TO***295Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.337 | 9.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40996 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.7959 | -9.5264
MV/LV Substation TO***297 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =114kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2133 | 0 |  | --> | C12 ex EAST WALL ROAD | East Wall Road: T42 | Mcdermott |  | 53.3523 | -6.2199
MV/LV Substation TO***300 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.29 | 3.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.39722 | 0 |  | --> | C22 ex COOLOCK | Coolock: T42 | Finglas |  | 53.3907 | -6.1707
MV/LV Substation TO***303Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 5.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | C20 ex NEWMARKET (SR) | Newmarket (sr): T41∥T42 | Glenlara |  | 52.2756 | -9.0635
MV/LV Substation TO***308Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.047885 | 0 |  | --> | C23 ex CREGG ROAD | Cregg Road: T41∥T42 | Ballydine |  | 52.3565 | -7.333
MV/LV Substation TO***309Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C23 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4233 | -6.4767
MV/LV Substation TO***313 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 6.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.4kW. | --> | E21 ex ABBEYFEALE | Abbeyfeale: T421 | Trien |  | 52.3651 | -9.1516
MV/LV Substation TO***315X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =432kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex MISERY HILL | Misery Hill: T101 | Poolbeg |  | 53.3464 | -6.2531
MV/LV Substation TO***321Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C25 ex KILCLOHER | Kilcloher: T42 | Dungarvan |  | 52.2124 | -7.7113
MV/LV Substation TO***326X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.01425 | 0.5 | 0 |  | --> | E18 ex BIRDHILL | Birdhill: T422 | Ardnacrusha |  | 52.7124 | -8.5019
MV/LV Substation TO***332X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C13 ex DUNMANWAY | Dunmanway: T43 | Dunmanway |  | 51.7804 | -9.2092
MV/LV Substation TO***332Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.274 | 3.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.41666 | 0 |  | --> | C20 ex GRAIGUE | Graigue: T42 | Carlow |  | 52.8357 | -6.9473
MV/LV Substation TO***333 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E17 ex ACHILL | Achill: T422 | Carrowbeg |  | 54.0067 | -9.9599
MV/LV Substation TO***337Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.18 | 1.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20318 | 0 |  | --> | C31 ex CLONSHAUGH | Clonshaugh: T41 | Finglas |  | 53.4028 | -6.2213
MV/LV Substation TO***348Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.487 | 1.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex ROSCOMMON | Roscommon: T41 | Lanesboro |  | 53.6309 | -8.1886
MV/LV Substation TO***352Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20176 | 0 |  | --> | C22 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.3499 | -6.6013
MV/LV Substation TO***354X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C26 ex KILBARRY | Kilbarry: T43 | Kilbarry |  | 51.9315 | -8.5172
MV/LV Substation TO***356 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 2.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.3kW. | --> | C18 ex FOYNES | Foynes: T42 | Rathkeale |  | 52.6046 | -9.0142
MV/LV Substation TO***364Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.362 | 0.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =406kW. | --> | C18 ex BALLYMOTE | Ballymote: T41 | Sligo |  | 54.0884 | -8.5247
MV/LV Substation TO***366 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.254 | 5.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.02755 | 0.3937 | 0 |  | --> | C19 ex POTTERY ROAD | Pottery Road: T101 | Carrickmines |  | 53.273 | -6.155
MV/LV Substation TO***368 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C22 ex BALLYARD | Ballyard: T41∥T42 | Tralee |  | 52.2448 | -9.7498
MV/LV Substation TO***368Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.147 | 3.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.43352 | 0 |  | --> | C14 ex GRAIGUE | Graigue: T42 | Carlow |  | 52.8379 | -6.9335
MV/LV Substation TO***369Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.15 | 0.2 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.44613 | 0 | Constrained,otherwise capacity available =500kW. | --> | C11 ex COOLMINE | Coolmine: T41 | Finglas |  | 53.3652 | -6.3888
MV/LV Substation TO***370 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CRANMORE | Cranmore: T41∥T42 | Sligo |  | 54.2715 | -8.4745
MV/LV Substation TO***372 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =499kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex NAAS | Naas: T41 | Newbridge |  | 53.2088 | -6.737
MV/LV Substation TO***372Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =327kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0 | 0 | Constrained,otherwise capacity available =408.5kW. | --> | C20 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.0874 | -7.6312
MV/LV Substation TO***373X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex POPPINTREE | Poppintree: T101 | Finglas |  | 53.4029 | -6.2847
MV/LV Substation TO***377Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =25kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053845 | 0 |  | --> | C17 ex KILLACLOYNE | Killacloyne: T41∥T42 | Midleton |  | 51.9116 | -8.2771
MV/LV Substation TO***380Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 5.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E12 ex WHITECHURCH | Whitechurch: T422 | Kilbarry |  | 51.9836 | -8.5108
MV/LV Substation TO***381X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex MISERY HILL | Misery Hill: T101 | Poolbeg |  | 53.3464 | -6.253
MV/LV Substation TO***381Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | C13 ex MOUNT MISERY | Mount Misery: T41 | Waterford |  | 52.2678 | -7.1123
MV/LV Substation TO***384X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 5.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | E17 ex CRANE | Crane: T122 | Crane |  | 52.5556 | -6.4268
MV/LV Substation TO***387X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0342 | 0.5 | 0 |  | --> | C20 ex BALLYBEGGAN | Ballybeggan: T43∥T44 | Tralee |  | 52.2681 | -9.6988
MV/LV Substation TO***389 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.256 | 3 |  | --> | 0.38 | 0 | 0 | 0 | 0.01995 | 0.4014 | 0 |  | --> | C20 ex GREENHILLS | Greenhills: T42 | Inchicore 110kv |  | 53.3085 | -6.3437
MV/LV Substation TO***390Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.185 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20239 | 0 |  | --> | C18 ex SUTTON | Sutton: T42 | Grange (dr) |  | 53.3915 | -6.1195
MV/LV Substation TO***395Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 10.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C12 ex WATERFORD IND EST | Waterford Ind Est: T42∥T44 | Butlerstown |  | 52.2476 | -7.1512
MV/LV Substation TO***4001 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex CARRICKMACROSS | Carrickmacross: T41 | Meath Hill |  | 53.9669 | -6.568
MV/LV Substation TO***4010 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =343kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40902 | 0 |  | --> | C21 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4538 | -6.4817
MV/LV Substation TO***4016 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =172kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =204.4kW. | --> | C12 ex MOUNTRATH | Mountrath: T41∥T42 | Portlaoise |  | 53.0016 | -7.3912
MV/LV Substation TO***4021 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.447 | 9.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.01995 | 0.5 | 0 |  | --> | C11 ex KILCOOLE | Kilcoole: T41∥T42 | Fassaroe |  | 53.0887 | -6.1155
MV/LV Substation TO***4035 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C20 ex CLONSHAUGH | Clonshaugh: T41 | Finglas |  | 53.4123 | -6.2174
MV/LV Substation TO***4036 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 3.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C24 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.5535 | -10.0353
MV/LV Substation TO***4038 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham: T41∥T42 | Letterkenny |  | 54.9631 | -7.4299
MV/LV Substation TO***4043 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 2.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | E17 ex BALLYMACARRY | Ballymacarry: T421 | Trillick |  | 55.0653 | -7.4308
MV/LV Substation TO***4052 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 5.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05295 | 0 |  | --> | E16 ex BALLYBUNION | Ballybunion: T421∥T422 | Trien |  | 52.4575 | -9.5132
MV/LV Substation TO***405Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.393 | 9.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00855 | 0.5 | 0 |  | --> | C12 ex TRABEG | Trabeg: T101 | Trabeg |  | 51.8836 | -8.4693
MV/LV Substation TO***406 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =174kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =199.1kW. | --> | E11 ex FERNS | Ferns: T421 | Crane |  | 52.6018 | -6.5478
MV/LV Substation TO***4060 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 4.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E13 ex EDGEWORTHSTOWN | Edgeworthstown: T421∥T422 | Richmond |  | 53.7454 | -7.535
MV/LV Substation TO***4064 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C17 ex DUNLEER | Dunleer: T41∥T42 | Drybridge |  | 53.8412 | -6.2609
MV/LV Substation TO***4066 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C17 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9442 | -8.0861
MV/LV Substation TO***4073 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen: T41∥T42 | Tonroe |  | 53.9095 | -8.5724
MV/LV Substation TO***4078 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052037 | 0 |  | --> | C14 ex BALLYMAHON | Ballymahon: T41∥T42 | Athlone |  | 53.6335 | -7.7622
MV/LV Substation TO***407Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =316kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41322 | 0 |  | --> | C18 ex BALGADDY | Balgaddy: T42 | Grange Castle |  | 53.3377 | -6.4178
MV/LV Substation TO***4088 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | E11 ex CREAGH | Creagh: T421∥T422 | Athlone |  | 53.375 | -8.1892
MV/LV Substation TO***4089 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E17 ex BALLYCONNELL | Ballyconnell: T421∥T422 | Gortawee |  | 54.0809 | -7.6345
MV/LV Substation TO***408X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C11 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1617 | -7.0153
MV/LV Substation TO***409X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =387kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0.38908 | 0 |  | --> | C15 ex SKIBBEREEN | Skibbereen: T41∥T42 | Dunmanway |  | 51.546 | -9.2668
MV/LV Substation TO***4111 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | E16 ex PATRICKSWELL | Patrickswell: T421∥T422 | Limerick |  | 52.5679 | -8.8322
MV/LV Substation TO***4111 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.342 | 4.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40918 | 0 |  | --> | C12 ex LIFFEY VALLEY | Liffey Valley: T42 | Inchicore 110kv |  | 53.3547 | -6.4007
MV/LV Substation TO***411X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052037 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 53.0379 | -6.6721
MV/LV Substation TO***4120 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0.00285 | 0.098275 | 0 |  | --> | C19 ex SMEARLA | Smearla: T41 | Trien |  | 52.3929 | -9.4156
MV/LV Substation TO***4131 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex LOUGHLINSTOWN | Loughlinstown: T41 | Carrickmines |  | 53.2419 | -6.1412
MV/LV Substation TO***4149 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C11 ex MALLOW | Mallow: T41 | Mallow |  | 52.1336 | -8.6482
MV/LV Substation TO***4159 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 9.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4411 | 0 |  | --> | C21 ex SINGLAND | Singland: T101 | Singland |  | 52.653 | -8.5938
MV/LV Substation TO***4177 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C12 ex CRANMORE | Cranmore: T41∥T42 | Sligo |  | 54.2599 | -8.4577
MV/LV Substation TO***4193 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 7.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C03 ex AHANE | Ahane: T102 | Ahane |  | 52.6697 | -8.5399
MV/LV Substation TO***4200 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines: T41 | Carrickmines |  | 53.2429 | -6.193
MV/LV Substation TO***4212 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =29kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0266 | 0.02525 | 0 |  | --> | E28 ex LOUGHREA | Loughrea: T41∥T42 | Somerset |  | 53.2526 | -8.5606
MV/LV Substation TO***4214 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =292kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =416.9kW. | --> | C15 ex MOUNTRATH | Mountrath: T41∥T42 | Portlaoise |  | 52.8669 | -7.4816
MV/LV Substation TO***4218 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | C12 ex SRAH | Srah: T41∥T42 | Thornsberry |  | 53.3005 | -7.5292
MV/LV Substation TO***422 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.008 | 7.4 |  | --> | 0.095 | 0 | 0 | 0 | 0.00855 | 0 | 0 | Constrained,otherwise capacity available =104.7kW. | --> | E14 ex ARIGNA | Arigna: T121 | Arigna |  | 54.0464 | -8.0365
MV/LV Substation TO***4222 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C12 ex SCARIFF | Scariff: T42 | Ennis |  | 52.9215 | -8.5224
MV/LV Substation TO***4230 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =394kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C14 ex FERMOY NORTH | Fermoy North: T41∥T42 | Barrymore |  | 52.164 | -8.2644
MV/LV Substation TO***4269 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.384 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40256 | 0 |  | --> | C15 ex ORANMORE | Oranmore: T41 | Galway 110kv |  | 53.2572 | -8.9268
MV/LV Substation TO***427X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C12 ex BALBRIGGAN | Balbriggan: T42 | Glasmore |  | 53.555 | -6.2471
MV/LV Substation TO***4280 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | C21 ex LEE BRIDGE | Lee Bridge: T41 | Macroom |  | 51.9346 | -9.1277
MV/LV Substation TO***429 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.048345 | 0 |  | --> | C17 ex TUBBERCURRY | Tubbercurry: T42 | Tonroe |  | 54.0395 | -8.843
MV/LV Substation TO***4308 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C12 ex LEE BRIDGE | Lee Bridge: T42 | Macroom |  | 51.9363 | -9.1155
MV/LV Substation TO***430X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex HEADFORD ROAD | Headford Road: T41 | Galway 110kv |  | 53.2748 | -9.046
MV/LV Substation TO***4315 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.183 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0.2007 | 0 |  | --> | C12 ex BALBRIGGAN | Balbriggan: T42 | Glasmore |  | 53.5559 | -6.2512
MV/LV Substation TO***4334 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex GARRYOWEN | Garryowen: T42 | Limerick |  | 52.6537 | -8.5778
MV/LV Substation TO***433Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.184 | 8.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20255 | 0 |  | --> | C17 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9907 | -6.0952
MV/LV Substation TO***434 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 10.7 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex CABRA | Cabra: T102 | Finglas |  | 53.3734 | -6.2989
MV/LV Substation TO***4346 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =388kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40192 | 0 |  | --> | C22 ex SEMPERIT | Semperit: T42 | Grange Castle |  | 53.3281 | -6.3591
MV/LV Substation TO***434Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.387 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40208 | 0 |  | --> | E21 ex CURRALEIGH | Curraleigh: T421∥T422 | Kilbarry |  | 51.9251 | -8.6055
MV/LV Substation TO***436X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.137 | 1.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.20683 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin: T42 | Inchicore 110kv |  | 53.3213 | -6.3951
MV/LV Substation TO***438 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex NORTH QUAYS | North Quays: T102 | Poolbeg |  | 53.3562 | -6.231
MV/LV Substation TO***439 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.095 | 0.1 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C23 ex CASTLEISLAND | Castleisland: T41∥T42 | Tralee |  | 52.2904 | -9.427
MV/LV Substation TO***4403 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 0.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | C17 ex KYLEERAGH | Kyleeragh: T41 | Nenagh |  | 53.0152 | -8.1644
MV/LV Substation TO***442 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.191 | 3.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20144 | 0 |  | --> | E20 ex CLONMINCH | Clonminch: T422 | Thornsberry |  | 53.2909 | -7.2942
MV/LV Substation TO***4426 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | C14 ex BALLYMAHON | Ballymahon: T41∥T42 | Athlone |  | 53.6118 | -7.6865
MV/LV Substation TO***4434 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C11 ex LOUGHTAGALLA | Loughtagalla: T41∥T42 | Thurles |  | 52.6349 | -7.7466
MV/LV Substation TO***445 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =32kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0528 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton: T422 | Sligo |  | 54.2901 | -7.8727
MV/LV Substation TO***447X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | C18 ex TOOMEVARA | Toomevara: T42 | Nenagh |  | 52.8475 | -8.0499
MV/LV Substation TO***451Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 13.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | C14 ex CASTLEVIEW | Castleview: T102 | Castleview |  | 51.9009 | -8.3699
MV/LV Substation TO***452Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9938 | -6.6503
MV/LV Substation TO***453 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E15 ex RATHMORE | Rathmore: T421 | Knockearagh |  | 52.1462 | -9.1816
MV/LV Substation TO***455 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.025 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.048845 | 0 |  | --> | C12 ex MONFIN | Monfin: T41∥T42 | Wexford |  | 52.485 | -6.5873
MV/LV Substation TO***456Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =176kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0076 | 0 | 0 | Constrained,otherwise capacity available =195.8kW. | --> | C15 ex TOOMEVARA | Toomevara: T42 | Nenagh |  | 52.9399 | -8.0343
MV/LV Substation TO***457 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10064 | 0 |  | --> | C19 ex SMEARLA | Smearla: T41 | Trien |  | 52.3948 | -9.4096
MV/LV Substation TO***457 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 7.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052495 | 0 |  | --> | E24 ex BANOGE | Banoge: T122 | Banoge |  | 52.6561 | -6.2562
MV/LV Substation TO***4578 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =381kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40304 | 0 |  | --> | C20 ex MISERY HILL | Misery Hill: T102 | Poolbeg |  | 53.3458 | -6.2537
MV/LV Substation TO***466Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =382kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0475 | 0 | 0 | Constrained,otherwise capacity available =352.9kW. | --> | C12 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.0919 | -7.6257
MV/LV Substation TO***468X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.033 | 2.7 |  | --> | 0.095 | 0 | 0 | 0 | 0.0038 | 0.10617 | 0 |  | --> | C15 ex GLENGOOLE | Glengoole: T41 | Thurles |  | 52.7172 | -7.5818
MV/LV Substation TO***469 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 3.3 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10016 | 0 |  | --> | E20 ex CLONMINCH | Clonminch: T422 | Thornsberry |  | 53.2988 | -7.3092
MV/LV Substation TO***471Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 2.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.3kW. | --> | C15 ex MILFORD (MWR) | Milford (mwr): T41 | Charleville |  | 52.3389 | -8.8607
MV/LV Substation TO***475 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.073 | 2.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10423 | 0 |  | --> | C15 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.337 | -6.4836
MV/LV Substation TO***492 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 7.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C23 ex ATHY | Athy: T101 | Athy |  | 52.9794 | -6.9886
MV/LV Substation TO***496X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C13 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9441 | -8.0897
MV/LV Substation TO***497Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =184kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20255 | 0 |  | --> | E20 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.3582 | -7.2171
MV/LV Substation TO***501X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9492 | -8.0971
MV/LV Substation TO***501Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | E18 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.478 | -6.2743
MV/LV Substation TO***503 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C16 ex CAPPAMORE | Cappamore: T41∥T42 | Ardnacrusha |  | 52.5858 | -8.2545
MV/LV Substation TO***503Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =386kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex NAAS | Naas: T41 | Newbridge |  | 53.2068 | -6.7377
MV/LV Substation TO***506X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex SHERIFF STREET | Sheriff Street: T41 | Francis Street |  | 53.3495 | -6.2496
MV/LV Substation TO***509X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 1.3 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10064 | 0 |  | --> | C16 ex ENNIS NORTH | Ennis North: T41∥T42 | Ennis |  | 52.89 | -9.047
MV/LV Substation TO***511X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C18 ex MIDLETON | Midleton: T102 | Midleton |  | 51.9426 | -8.2058
MV/LV Substation TO***515X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.9421 | -7.653
MV/LV Substation TO***516X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 4.1 |  | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.09784 | 0 |  | --> | E21 ex CLARA | Clara: T421 | Thornsberry |  | 53.3794 | -7.6619
MV/LV Substation TO***517Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E18 ex COLLOONEY | Collooney: T422 | Sligo |  | 54.1774 | -8.4815
MV/LV Substation TO***518X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 5.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05142 | 0 |  | --> | E13 ex CRANE | Crane: T122 | Crane |  | 52.5017 | -6.5106
MV/LV Substation TO***520X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.165 | 4.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20552 | 0 |  | --> | C12 ex CASTLEKNOCK | Castleknock: T41∥T42 | Finglas |  | 53.3644 | -6.3831
MV/LV Substation TO***521X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.04 | 0 | Constrained,otherwise capacity available =177kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | C11 ex GRAIGUENAMANAGH | Graiguenamanagh: T41∥T42 | Kilkenny |  | 52.5379 | -6.9594
MV/LV Substation TO***522Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 5.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05219 | 0 |  | --> | E18 ex CRANE | Crane: T122 | Crane |  | 52.5291 | -6.5024
MV/LV Substation TO***526 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0114 | 0.5 | 0 |  | --> | C15 ex RINEANNA | Rineanna: T42 | Drumline |  | 52.7093 | -8.8841
MV/LV Substation TO***529 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0.01425 | 0.045987 | 0 |  | --> | C11 ex SCARIFF | Scariff: T42 | Ennis |  | 52.8966 | -8.5402
MV/LV Substation TO***530 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =85kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0.09637 | 0 |  | --> | C30 ex CLAREGALWAY | Claregalway: T42 | Galway 110kv |  | 53.3859 | -9.0675
MV/LV Substation TO***541X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.3kW. | --> | C17 ex BALLYBAY | Ballybay: T41∥T42 | Lisdrum |  | 54.0792 | -6.8458
MV/LV Substation TO***552X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 4.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | E21 ex CLARA | Clara: T421 | Thornsberry |  | 53.3849 | -7.6818
MV/LV Substation TO***552Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E11 ex CREAGH | Creagh: T421∥T422 | Athlone |  | 53.3674 | -8.1883
MV/LV Substation TO***558 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.0428 | 0 |  | --> | C15 ex KILMARTIN | Kilmartin: T41 | Arklow |  | 53.042 | -6.1285
MV/LV Substation TO***558Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C12 ex LEIXLIP | Leixlip: T42 | Griffinrath |  | 53.3647 | -6.486
MV/LV Substation TO***559Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.177 | 0.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | C12 ex SWORDS | Swords: T42 | Glasmore |  | 53.4639 | -6.2195
MV/LV Substation TO***560 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C12 ex ROSSGEIR | Rossgeir: T41∥T42 | Letterkenny |  | 54.8341 | -7.5414
MV/LV Substation TO***569Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 0.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C16 ex RIVERSTOWN | Riverstown: T41∥T42 | Kilbarry |  | 51.9398 | -8.3789
MV/LV Substation TO***577Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =390kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4016 | 0 |  | --> | C20 ex TOGHER | Togher: T42 | Trabeg |  | 51.8846 | -8.4765
MV/LV Substation TO***581 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 11.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101.3kW. | --> | E11 ex WESTPORT | Westport: T421∥T422 | Castlebar |  | 53.7635 | -9.7939
MV/LV Substation TO***595Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E14 ex COLLOONEY | Collooney: T422 | Sligo |  | 54.1733 | -8.4872
MV/LV Substation TO***595Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =392kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.39028 | 0 |  | --> | C13 ex TOGHER | Togher: T41 | Trabeg |  | 51.8768 | -8.4956
MV/LV Substation TO***596Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 9.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C28 ex ARTANE | Artane: T102 | Finglas |  | 53.3932 | -6.1958
MV/LV Substation TO***598X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =32kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.01995 | 0.0318 | 0 |  | --> | C17 ex CARRIGSHANE | Carrigshane: T41 | Midleton |  | 51.9062 | -8.1563
MV/LV Substation TO***602 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =24kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053992 | 0 |  | --> | C12 ex CRANMORE | Cranmore: T41∥T42 | Sligo |  | 54.2589 | -8.4531
MV/LV Substation TO***605Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =196kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200.6kW. | --> | E12 ex CASTLELYONS | Castlelyons: T421∥T422 | Barrymore |  | 52.0275 | -8.329
MV/LV Substation TO***610 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C17 ex GRAIGUENAMANAGH | Graiguenamanagh: T41∥T42 | Kilkenny |  | 52.6205 | -6.8395
MV/LV Substation TO***619X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.144 | 0.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20376 | 0 |  | --> | C15 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.8335 | -8.9802
MV/LV Substation TO***620 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =26kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.048697 | 0 |  | --> | C17 ex BANAGHER | Banagher: T42 | Dallow |  | 53.199 | -8.1372
MV/LV Substation TO***620Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.021 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.054432 | 0 |  | --> | C11 ex COES ROAD | Coes Road: T41∥T42 | Dundalk |  | 54 | -6.3816
MV/LV Substation TO***626 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.353 | 1.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex HEADFORD ROAD | Headford Road: T42 | Galway 110kv |  | 53.2761 | -9.0538
MV/LV Substation TO***632 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C18 ex KILCOLGAN | Kilcolgan: T42 | Galway 110kv |  | 53.2495 | -8.8896
MV/LV Substation TO***635X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10237 | 0 |  | --> | C17 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.7362 | -6.4515
MV/LV Substation TO***638Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.376 | 5.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40382 | 0 |  | --> | E17 ex BLESSINGTON | Blessington: T421 | Kilteel |  | 53.1842 | -6.5257
MV/LV Substation TO***641Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C12 ex MONFIN | Monfin: T41∥T42 | Wexford |  | 52.4879 | -6.5832
MV/LV Substation TO***644Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E20 ex ADAMSTOWN | Adamstown: T122 | Inchicore 110kv |  | 53.3499 | -6.4733
MV/LV Substation TO***657 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =160kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.1953 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy: T422 | Athlone |  | 53.607 | -8.5589
MV/LV Substation TO***659X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.187 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20207 | 0 |  | --> | C15 ex STICKILLEN | Stickillen: T41∥T42 | Drybridge |  | 53.8491 | -6.5411
MV/LV Substation TO***675 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.078 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0.0076 | 0.09546 | 0 |  | --> | C17 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.7289 | -6.4459
MV/LV Substation TO***680 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05142 | 0 |  | --> | E19 ex CAVAN | Cavan: T421 | Shankill |  | 53.981 | -7.4034
MV/LV Substation TO***681 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 1.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10064 | 0 |  | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham: T41∥T42 | Letterkenny |  | 54.9894 | -7.4222
MV/LV Substation TO***683X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C18 ex BALLYJAMESDUFF | Ballyjamesduff: T42 | Shankill |  | 53.958 | -7.0622
MV/LV Substation TO***687 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | C19 ex LISMORE | Lismore: T41∥T42 | Dungarvan |  | 52.1343 | -7.9431
MV/LV Substation TO***688 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052647 | 0 |  | --> | C12 ex MONFIN | Monfin: T41∥T42 | Wexford |  | 52.4889 | -6.5948
MV/LV Substation TO***696 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.046795 | 0 |  | --> | E25 ex PATRICKSWELL | Patrickswell: T421∥T422 | Limerick |  | 52.6368 | -8.8585
MV/LV Substation TO***698Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C18 ex DUNDALK | Dundalk: T41 | Dundalk |  | 54.0214 | -6.4306
MV/LV Substation TO***699X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.185 | 4.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20239 | 0 |  | --> | C12 ex GLEBE | Glebe: T41∥T42 | Richmond |  | 53.7235 | -7.8051
MV/LV Substation TO***702Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.153 | 4 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0 | 0 | Constrained,otherwise capacity available =203.4kW. | --> | E11 ex CHARLEVILLE | Charleville: T422 | Charleville |  | 52.4248 | -8.6552
MV/LV Substation TO***707 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 4.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052345 | 0 |  | --> | E13 ex BALLYRAGGET | Ballyragget: T421∥T422 | Ballyragget |  | 52.7346 | -7.426
MV/LV Substation TO***709 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10032 | 0 |  | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham: T41∥T42 | Letterkenny |  | 54.9654 | -7.4299
MV/LV Substation TO***715Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 4.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C18 ex BALLYJAMESDUFF | Ballyjamesduff: T42 | Shankill |  | 53.9314 | -7.1015
MV/LV Substation TO***717Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1033 | 0 |  | --> | C13 ex MORNINGTON ROAD | Mornington Road: T41 | Drybridge |  | 53.7233 | -6.2563
MV/LV Substation TO***719 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.202 | 0.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0266 | 0.40248 | 0 |  | --> | E17 ex DINGLE | Dingle: T421 | Oughtragh |  | 52.1402 | -10.2701
MV/LV Substation TO***722X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.044637 | 0 |  | --> | C22 ex BUSHFIELD | Bushfield: T42 | Athlone |  | 53.4914 | -7.8574
MV/LV Substation TO***724Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =95kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.8kW. | --> | C16 ex TOOMEVARA | Toomevara: T42 | Nenagh |  | 52.8494 | -8.0414
MV/LV Substation TO***724Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.014 | 0 | Constrained,otherwise capacity available =180kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20318 | 0 |  | --> | C18 ex CASTLETROY | Castletroy: T41∥T42 | Ardnacrusha |  | 52.6763 | -8.5559
MV/LV Substation TO***731Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.187 | 2.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20207 | 0 |  | --> | C18 ex MALAHIDE | Malahide: T42 | Glasmore |  | 53.442 | -6.1569
MV/LV Substation TO***732 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 6.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C12 ex COLLINSTOWN | Collinstown: T41∥T42 | Grange (dr) |  | 53.4186 | -6.2333
MV/LV Substation TO***735X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | C22 ex BUSHFIELD | Bushfield: T42 | Athlone |  | 53.4962 | -7.8523
MV/LV Substation TO***736X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 7.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400kW. | --> | E13 ex DUNFIRTH | Dunfirth: T122 | Dunfirth |  | 53.4096 | -6.7398
MV/LV Substation TO***741 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | C19 ex LISMORE | Lismore: T41∥T42 | Dungarvan |  | 52.1285 | -8.0557
MV/LV Substation TO***747Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.274 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41966 | 0 |  | --> | E19 ex LONGFORD | Longford: T421 | Richmond |  | 53.725 | -7.808
MV/LV Substation TO***753X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.058 | 2.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =106.5kW. | --> | E17 ex LISDRUM | Lisdrum: T422 | Lisdrum |  | 54.2029 | -7.0267
MV/LV Substation TO***756Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =184kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7215 | -6.3076
MV/LV Substation TO***763 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 8.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | C17 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9511 | -6.052
MV/LV Substation TO***768 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =350kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.39892 | 0 |  | --> | E18 ex BIRDHILL | Birdhill: T422 | Ardnacrusha |  | 52.7148 | -8.5002
MV/LV Substation TO***773Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =34kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052495 | 0 |  | --> | C11 ex RAHEEN | Raheen: T41 | Limerick |  | 52.6365 | -8.6889
MV/LV Substation TO***776 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =150kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20784 | 0 |  | --> | C17 ex SKIBBEREEN | Skibbereen: T41∥T42 | Dunmanway |  | 51.5289 | -9.1752
MV/LV Substation TO***779 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.047345 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1978 | -6.7601
MV/LV Substation TO***780 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.095 | 0.1 | Constrained,otherwise capacity available =180kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20318 | 0 |  | --> | C21 ex CASTLEISLAND | Castleisland: T41∥T42 | Tralee |  | 52.2237 | -9.4632
MV/LV Substation TO***782 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.06 | 0.7 |  | --> | 0.095 | 0 | 0 | 0 | 0.0171 | 0.0882 | 0 |  | --> | C20 ex KILMARTIN | Kilmartin: T41 | Arklow |  | 53.0702 | -6.2229
MV/LV Substation TO***788 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.012 | 0 | Constrained,otherwise capacity available =32kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0528 | 0 |  | --> | C16 ex MOATE | Moate: T42 | Athlone |  | 53.516 | -7.6941
MV/LV Substation TO***791 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =194kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =201kW. | --> | C16 ex TOOMEVARA | Toomevara: T42 | Nenagh |  | 52.8495 | -8.0447
MV/LV Substation TO***801 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 3.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =46.7kW. | --> | C17 ex BALLYSHANNON | Ballyshannon: T41∥T42 | Cathaleens Fall |  | 54.4967 | -8.175
MV/LV Substation TO***803 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.153 | 0.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =207.4kW. | --> | E12 ex KILMACTHOMAS | Kilmacthomas: T421∥T422 | Dungarvan |  | 52.2013 | -7.4074
MV/LV Substation TO***807X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | C15 ex CASTLECOMER | Castlecomer: T41∥T42 | Ballyragget |  | 52.8566 | -7.0703
MV/LV Substation TO***811X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =355kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40714 | 0 |  | --> | C20 ex BUTTEVANT | Buttevant: T41∥T42 | Mallow |  | 52.2323 | -8.6767
MV/LV Substation TO***816X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =22kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =54.3kW. | --> | E17 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 53.0186 | -7.3067
MV/LV Substation TO***823X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex NORTH QUAYS | North Quays: T102 | Poolbeg |  | 53.3574 | -6.2348
MV/LV Substation TO***824X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 5.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E14 ex CRANE | Crane: T122 | Crane |  | 52.5548 | -6.5634
MV/LV Substation TO***828Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex NAAS | Naas: T41 | Newbridge |  | 53.2086 | -6.7377
MV/LV Substation TO***833Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 0.9 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex MORNINGTON ROAD | Mornington Road: T42 | Drybridge |  | 53.7141 | -6.3515
MV/LV Substation TO***834X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.6763 | -7.8519
MV/LV Substation TO***835 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.265 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42104 | 0 |  | --> | C17 ex GREYSTONES | Greystones: T41 | Fassaroe |  | 53.1456 | -6.0637
MV/LV Substation TO***836X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex MISERY HILL | Misery Hill: T101 | Poolbeg |  | 53.3464 | -6.253
MV/LV Substation TO***842 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C11 ex NEWTOWNCUNNINGHAM | Newtowncunningham: T41∥T42 | Letterkenny |  | 54.9801 | -7.4167
MV/LV Substation TO***842X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C17 ex SKIBBEREEN | Skibbereen: T41∥T42 | Dunmanway |  | 51.5318 | -9.1799
MV/LV Substation TO***856 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =139kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =209.5kW. | --> | C16 ex TOOMEVARA | Toomevara: T42 | Nenagh |  | 52.849 | -8.0336
MV/LV Substation TO***860X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C17 ex KYLEERAGH | Kyleeragh: T41 | Nenagh |  | 53.0059 | -8.1862
MV/LV Substation TO***861Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 8.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | C25 ex MULLINGAR | Mullingar: T101 | Mullingar |  | 53.583 | -7.5291
MV/LV Substation TO***870X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.499 | 0.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex RATHMORE | Rathmore: T421 | Knockearagh |  | 52.06 | -9.0667
MV/LV Substation TO***871X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =68kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10499 | 0 |  | --> | E11 ex BALLINROBE | Ballinrobe: T421∥T422 | Dalton |  | 53.6135 | -9.2168
MV/LV Substation TO***874X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1093 | 0 |  | --> | C17 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.6874 | -7.8412
MV/LV Substation TO***879X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.322 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41228 | 0 |  | --> | C11 ex MALLOW | Mallow: T41 | Mallow |  | 52.1276 | -8.6446
MV/LV Substation TO***879Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.177 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | C25 ex TYCOR | Tycor: T41∥T42 | Waterford |  | 52.2746 | -7.1592
MV/LV Substation TO***887Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy: T422 | Athlone |  | 53.6599 | -8.6953
MV/LV Substation TO***888 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05325 | 0 |  | --> | C16 ex ENNIS NORTH | Ennis North: T41∥T42 | Ennis |  | 52.8902 | -9.032
MV/LV Substation TO***892 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.328 | 10.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.40336 | 0 |  | --> | C14 ex CABRA | Cabra: T102 | Finglas |  | 53.3693 | -6.2796
MV/LV Substation TO***894X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | C14 ex CASHEL | Cashel: T42 | Cahir |  | 52.6151 | -8.0258
MV/LV Substation TO***900Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.6629 | -6.3294
MV/LV Substation TO***903Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0528 | 0 |  | --> | E19 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.7208 | -6.4957
MV/LV Substation TO***910 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 6.1 |  | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =98kW. | --> | E21 ex ABBEYFEALE | Abbeyfeale: T421 | Trien |  | 52.379 | -9.1354
MV/LV Substation TO***910Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 8.3 |  | --> | 0.95 | 0 | 0 | 0 | 0.0475 | 0.5 | 0 |  | --> | C18 ex MONREAD | Monread: T102 | Monread |  | 53.2133 | -6.7102
MV/LV Substation TO***912X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =57kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10665 | 0 |  | --> | E21 ex FINEA | Finea: T421∥T422 | Shankill |  | 53.8645 | -7.3213
MV/LV Substation TO***915X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E21 ex FINEA | Finea: T421∥T422 | Shankill |  | 53.8653 | -7.3229
MV/LV Substation TO***915X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | E12 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 52.9785 | -7.175
MV/LV Substation TO***915X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 1.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10222 | 0 |  | --> | C26 ex KELLS | Kells: T41∥T42 | Navan |  | 53.7244 | -6.8636
MV/LV Substation TO***920 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =59kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10635 | 0 |  | --> | E11 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.4525 | -6.2882
MV/LV Substation TO***921 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =28kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =53.4kW. | --> | E20 ex ROSCREA | Roscrea: T42 | Ikerrin |  | 52.9428 | -7.6439
MV/LV Substation TO***921X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.057 | 0.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10665 | 0 |  | --> | C17 ex KYLEERAGH | Kyleeragh: T41 | Nenagh |  | 53 | -8.1241
MV/LV Substation TO***929 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 5.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0531 | 0 |  | --> | E17 ex CRANE | Crane: T122 | Crane |  | 52.5473 | -6.4056
MV/LV Substation TO***930X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 1.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10048 | 0 |  | --> | E19 ex GARRANACANTY | Garranacanty: T421 | Tipperary |  | 52.4715 | -8.0668
MV/LV Substation TO***931 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 11.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C36 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2938 | -9.1055
MV/LV Substation TO***933 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 11.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0528 | 0 |  | --> | C36 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2923 | -9.1129
MV/LV Substation TO***934 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.185 | 11.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20239 | 0 |  | --> | C36 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2908 | -9.1118
MV/LV Substation TO***936 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 11.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.0431 | 0 |  | --> | C36 ex SALTHILL | Salthill: T102 | Salthill |  | 53.29 | -9.1124
MV/LV Substation TO***937 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | E16 ex GWEEDORE | Gweedore: T421 | Ardnagappary |  | 55.0546 | -8.2583
MV/LV Substation TO***940X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex NORTH QUAYS | North Quays: T102 | Poolbeg |  | 53.3574 | -6.2348
MV/LV Substation TO***943 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C19 ex GRANGE (DR) | Grange (dr): T41 | Grange (dr) |  | 53.3996 | -6.1519
MV/LV Substation TO***944Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 0.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10284 | 0 |  | --> | C12 ex SRAH | Srah: T41∥T42 | Thornsberry |  | 53.2869 | -7.512
MV/LV Substation TO***946X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E15 ex BUSH | Bush: T421∥T422 | Dundalk |  | 54.0259 | -6.1359
MV/LV Substation TO***951X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E14 ex BALLINROBE | Ballinrobe: T421∥T422 | Dalton |  | 53.6944 | -9.18
MV/LV Substation TO***952X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | E18 ex TULLOW | Tullow: T422 | Carlow |  | 52.8342 | -6.6727
MV/LV Substation TO***952X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =60kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0038 | 0.1022 | 0 |  | --> | E11 ex CAVAN | Cavan: T421 | Shankill |  | 54.049 | -7.3168
MV/LV Substation TO***952Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =194kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20096 | 0 |  | --> | C17 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.7505 | -7.9532
MV/LV Substation TO***956 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | E23 ex BALTRASNA | Baltrasna: T121 | Baltrasna |  | 53.5545 | -6.3977
MV/LV Substation TO***957X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =86kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10222 | 0 |  | --> | E12 ex BALLINROBE | Ballinrobe: T421∥T422 | Dalton |  | 53.6149 | -9.2226
MV/LV Substation TO***958Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =76kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10377 | 0 |  | --> | E15 ex DULEEK | Duleek: T421∥T422 | Drybridge |  | 53.6602 | -6.4274
MV/LV Substation TO***963 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =139kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20553 | 0 |  | --> | C11 ex GARDEN CITY | Garden City: T41∥T42 | Arklow |  | 52.7108 | -6.2951
MV/LV Substation TO***963X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 13.7 |  | --> | 0.095 | 0 | 0 | 0 | 0.00855 | 0.09415 | 0 |  | --> | C16 ex CASTLEVIEW | Castleview: T102 | Castleview |  | 51.9096 | -8.369
MV/LV Substation TO***967 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | C13 ex LEE BRIDGE | Lee Bridge: T41 | Macroom |  | 51.8697 | -8.9697
MV/LV Substation TO***968X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =186kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20223 | 0 |  | --> | C12 ex SAGGART | Saggart: T41∥T42 | Grange Castle |  | 53.2462 | -6.5392
MV/LV Substation TO***984X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | E15 ex BRUFF | Bruff: T421 | Limerick |  | 52.5219 | -8.5177
MV/LV Substation TO***987 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053697 | 0 |  | --> | C17 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.4935 | -8.8114
MV/LV Substation TO***989X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 9.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.044795 | 0 |  | --> | C12 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.7891 | -9.5002
MV/LV Substation TO***995 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.095 | 0.1 | Constrained,otherwise capacity available =185kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20239 | 0 |  | --> | C21 ex CASTLEISLAND | Castleisland: T41∥T42 | Tralee |  | 52.224 | -9.4592
MV/LV Substation TO***999X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.6 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex HEADFORD ROAD | Headford Road: T42 | Galway 110kv |  | 53.2944 | -9.0373
MV/LV Substation TR***006 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.311 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.405 | 0 |  | --> | C19 ex MULGANNON | Mulgannon: T41 | Wexford |  | 52.3333 | -6.4538
MV/LV Substation TR***012 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5519 | -6.7944
MV/LV Substation TR***012 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.135 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21014 | 0 |  | --> | C14 ex CARRAROE | Carraroe: T42 | Screeb |  | 53.263 | -9.5653
MV/LV Substation TR***014Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.251 | 9.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.40316 | 0 |  | --> | C22 ex ARTANE | Artane: T102 | Finglas |  | 53.3928 | -6.2126
MV/LV Substation TR***020Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.054 | 0.1 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C20 ex SANTRY | Santry: T42 | Finglas |  | 53.3998 | -6.2546
MV/LV Substation TR***021X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.256 | 14.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4224 | 0 |  | --> | C26 ex HEUSTON SQUARE | Heuston Square: T102 | Inchicore 110kv |  | 53.3459 | -6.2802
MV/LV Substation TR***024X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C15 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.9447 | -7.6627
MV/LV Substation TR***028 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5645 | -6.7979
MV/LV Substation TR***028 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.303 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41022 | 0 |  | --> | C15 ex DEERPARK | Deerpark: T41∥T42 | Ballydine |  | 52.3479 | -7.4216
MV/LV Substation TR***030 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =29kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.04725 | 0 |  | --> | C17 ex SKIBBEREEN | Skibbereen: T41∥T42 | Dunmanway |  | 51.5018 | -9.2608
MV/LV Substation TR***034X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C17 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5546 | -6.7656
MV/LV Substation TR***035 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.137 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.05605 | 0.38096 | 0 |  | --> | C17 ex GREYSTONES | Greystones: T41 | Fassaroe |  | 53.1492 | -6.0657
MV/LV Substation TR***035 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =382kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.069851 | 0 | Constrained,otherwise capacity available =402.9kW. | --> | C19 ex BIRR | Birr: T41 | Dallow |  | 53.0919 | -7.8944
MV/LV Substation TR***035X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.17 | 5.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20474 | 0 |  | --> | E14 ex MOY | Moy: T421∥T422 | Moy |  | 54.1886 | -9.2292
MV/LV Substation TR***036Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C13 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8591 | -8.3052
MV/LV Substation TR***037 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C15 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3313 | -6.4834
MV/LV Substation TR***038X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.095 | 0.1 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C18 ex CASTLEISLAND | Castleisland: T41∥T42 | Tralee |  | 52.2319 | -9.4738
MV/LV Substation TR***039X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.267 | 1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5559 | -6.7911
MV/LV Substation TR***040X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C20 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.8808 | -7.742
MV/LV Substation TR***040Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =27kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05355 | 0 |  | --> | C20 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1679 | -6.8357
MV/LV Substation TR***046 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.14 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20938 | 0 |  | --> | C32 ex ACADEMY STREET | Academy Street: T44 | Navan |  | 53.6444 | -6.6876
MV/LV Substation TR***053 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =342kVA. | --> | 0.38 | 0 | 0 | 0 | 0.08455 | 0.32018 | 0 |  | --> | E16 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.6981 | -6.2517
MV/LV Substation TR***060X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.28 | 0.3 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C19 ex BREWERY ROAD | Brewery Road: T41 | Carrickmines |  | 53.2703 | -6.1969
MV/LV Substation TR***063Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C12 ex MOUNTRATH | Mountrath: T41∥T42 | Portlaoise |  | 52.9722 | -7.4268
MV/LV Substation TR***064 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =294kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02755 | 0.3876 | 0 |  | --> | C14 ex BELFIELD | Belfield: T42 | Blackrock |  | 53.3095 | -6.2052
MV/LV Substation TR***064X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =399kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40016 | 0 |  | --> | C12 ex BALLINACURRA | Ballinacurra: T42 | Limerick |  | 52.6534 | -8.6397
MV/LV Substation TR***067 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.291 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41706 | 0 |  | --> | C15 ex RINEANNA | Rineanna: T42 | Drumline |  | 52.7036 | -8.8826
MV/LV Substation TR***068X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C13 ex CHARLESTOWN | Charlestown: T41 | Tonroe |  | 53.9144 | -8.8376
MV/LV Substation TR***069 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.273 | 3.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.03895 | 0.37882 | 0 |  | --> | C12 ex TRAMORE | Tramore: T42 | Butlerstown |  | 52.1571 | -7.1667
MV/LV Substation TR***069X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.48 | 3.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BEDFORD ROW | Bedford Row: T43 | Francis Street |  | 53.3456 | -6.2475
MV/LV Substation TR***074 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 3.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10128 | 0 |  | --> | C15 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.4156 | -10.1198
MV/LV Substation TR***074 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =361kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4062 | 0 |  | --> | C11 ex DOCK ROAD | Dock Road: T41∥T42 | Limerick |  | 52.655 | -8.6542
MV/LV Substation TR***076X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =390kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0475 | 0.3516 | 0 |  | --> | C19 ex CENTRAL PARK | Central Park: T101 | Carrickmines |  | 53.2698 | -6.2008
MV/LV Substation TR***077 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.279 | 2.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex ABBEYLAND | Abbeyland: T41 | Navan |  | 53.6519 | -6.6856
MV/LV Substation TR***079Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 9.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C19 ex ENNIS | Ennis: T101 | Ennis |  | 52.8388 | -8.9549
MV/LV Substation TR***081X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.188 | 0.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20191 | 0 |  | --> | E17 ex INCH | Inch: T421∥T422 | Oughtragh |  | 52.2704 | -10.0269
MV/LV Substation TR***082Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C22 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 52.9572 | -9.2807
MV/LV Substation TR***083X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 11.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05142 | 0 |  | --> | C28 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2551 | -9.1525
MV/LV Substation TR***087 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.365 | 26.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40556 | 0 |  | --> | E17 ex WEXFORD | Wexford: T121∥T122 | Wexford |  | 52.3217 | -6.6472
MV/LV Substation TR***092Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | E20 ex GARRANACANTY | Garranacanty: T422 | Tipperary |  | 52.4878 | -8.0653
MV/LV Substation TR***097 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.493 | 7.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E41 ex KINSALE | Kinsale: T423 | Bandon |  | 51.701 | -8.5187
MV/LV Substation TR***098X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =353kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.40446 | 0 |  | --> | C17 ex TOGHER | Togher: T41 | Trabeg |  | 51.8776 | -8.481
MV/LV Substation TR***101 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C23 ex CASTLEISLAND | Castleisland: T41∥T42 | Tralee |  | 52.2946 | -9.3934
MV/LV Substation TR***109Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E17 ex BALLINROBE | Ballinrobe: T421∥T422 | Dalton |  | 53.6406 | -9.1162
MV/LV Substation TR***112 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.161 | 4.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.19714 | 0 |  | --> | E12 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.2394 | -6.3433
MV/LV Substation TR***120X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =41.7kW. | --> | C15 ex MILLTOWN MALBAY | Milltown Malbay: T42 | Tullabrack |  | 52.8091 | -9.4522
MV/LV Substation TR***126X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.181 | 3.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20302 | 0 |  | --> | C19 ex CAUSEWAY | Causeway: T41∥T42 | Tralee |  | 52.3943 | -9.8595
MV/LV Substation TR***128X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =168kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20506 | 0 |  | --> | C20 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.8897 | -7.7347
MV/LV Substation TR***131 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.294 | 5.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.02755 | 0.3876 | 0 |  | --> | C12 ex ABBEYLAND | Abbeyland: T42 | Navan |  | 53.6649 | -6.6821
MV/LV Substation TR***137X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.451 | 2.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex DUNDRUM | Dundrum: T42 | Blackrock |  | 53.2983 | -6.2319
MV/LV Substation TR***140 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0.5 | 10.9 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex ENNIS | Ennis: T102 | Ennis |  | 52.8438 | -8.9692
MV/LV Substation TR***164X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.378 | 2.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40352 | 0 |  | --> | C21 ex SALLYNOGGIN ROAD | Sallynoggin Road: T41 | Cherrywood |  | 53.2845 | -6.1318
MV/LV Substation TR***167Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 1.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10143 | 0 |  | --> | C12 ex BALBRIGGAN | Balbriggan: T42 | Glasmore |  | 53.5947 | -6.2182
MV/LV Substation TR***178Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0 | 0 | Constrained,otherwise capacity available =44.6kW. | --> | C12 ex MOUNTRATH | Mountrath: T41∥T42 | Portlaoise |  | 52.9709 | -7.4262
MV/LV Substation TR***182 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.242 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.4145 | 0 |  | --> | C20 ex DUNDRUM | Dundrum: T42 | Blackrock |  | 53.2905 | -6.2442
MV/LV Substation TR***182Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.173 | 3.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20427 | 0 |  | --> | C19 ex ERRIGAL | Errigal: T41 | Shankill |  | 54.0802 | -7.0928
MV/LV Substation TR***184X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.167 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =205.2kW. | --> | C16 ex BUNDORAN | Bundoran: T41∥T42 | Cathaleens Fall |  | 54.4987 | -8.2226
MV/LV Substation TR***193Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.304 | 9.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.40608 | 0 |  | --> | C12 ex TRABEG | Trabeg: T101 | Trabeg |  | 51.8826 | -8.4607
MV/LV Substation TR***197Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.059367 | 0 |  | --> | C18 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1529 | -6.9131
MV/LV Substation TR***199X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =176kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2038 | 0 |  | --> | E16 ex PATRICKSWELL | Patrickswell: T421∥T422 | Limerick |  | 52.5605 | -8.7823
MV/LV Substation TR***201Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.39433 | 0 | Constrained,otherwise capacity available =500kW. | --> | C18 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.6867 | -7.8269
MV/LV Substation TR***202 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.383 | 3.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.06175 | 0.5 | 0 |  | --> | C23 ex MOUNT MERRION | Mount Merrion: T41 | Carrickmines |  | 53.2925 | -6.2075
MV/LV Substation TR***204 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0114 | 0.039575 | 0 |  | --> | C15 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.9486 | -7.6639
MV/LV Substation TR***211 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | E25 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6811 | -7.2799
MV/LV Substation TR***219X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C18 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5471 | -6.7933
MV/LV Substation TR***222X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C20 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.8822 | -7.7453
MV/LV Substation TR***225X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.493 | 1.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C20 ex MANOR STREET | Manor Street: T42 | Waterford |  | 52.2499 | -7.1161
MV/LV Substation TR***231Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =355kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40714 | 0 |  | --> | C17 ex RATHMULLAN | Rathmullan: T41 | Drybridge |  | 53.7094 | -6.3806
MV/LV Substation TR***240X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =86kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10222 | 0 |  | --> | C20 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.8757 | -7.7433
MV/LV Substation TR***263Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =303kVA. | --> | 0.38 | 0 | 0 | 0 | 0.038 | 0.37522 | 0 |  | --> | C20 ex CAHERDAVIN | Caherdavin: T42 | Ardnacrusha |  | 52.6736 | -8.677
MV/LV Substation TR***269 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 4.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | C17 ex GLEBE | Glebe: T41∥T42 | Richmond |  | 53.7322 | -7.783
MV/LV Substation TR***278X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =31kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05295 | 0 |  | --> | C14 ex MILFORD (NR) | Milford (nr): T41∥T42 | Letterkenny |  | 55.0918 | -7.6823
MV/LV Substation TR***281Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.292 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0171 | 0.39892 | 0 |  | --> | C11 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.7176 | -6.3594
MV/LV Substation TR***285 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C18 ex SCARTEEN | Scarteen: T41∥T42 | Mallow |  | 52.1685 | -8.774
MV/LV Substation TR***290X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.371 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40462 | 0 |  | --> | C18 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5538 | -6.7907
MV/LV Substation TR***294Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.137 | 14.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.19983 | 0 |  | --> | C22 ex STEPHENSTOWN | Stephenstown: T102 | Finglas |  | 53.6147 | -6.2063
MV/LV Substation TR***315 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.164 | 0.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.04275 | 0.39104 | 0 |  | --> | C19 ex PEMBROKE | Pembroke: T42 | Ringsend |  | 53.3331 | -6.2217
MV/LV Substation TR***320X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central: T45 | Inchicore 110kv |  | 53.3382 | -6.3208
MV/LV Substation TR***324 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0057 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | E11 ex WESTPORT | Westport: T421∥T422 | Castlebar |  | 53.7623 | -9.8065
MV/LV Substation TR***328 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex EAST WALL ROAD | East Wall Road: T42 | Mcdermott |  | 53.3474 | -6.2125
MV/LV Substation TR***332Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =369kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40494 | 0 |  | --> | C13 ex GRANGE (DR) | Grange (dr): T41 | Grange (dr) |  | 53.4024 | -6.1622
MV/LV Substation TR***336Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =304kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41508 | 0 |  | --> | C16 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6585 | -7.2563
MV/LV Substation TR***339X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.177 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.19365 | 0 |  | --> | C18 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5497 | -6.7848
MV/LV Substation TR***344X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex TRIM | Trim: T41∥T42 | Navan |  | 53.553 | -6.8001
MV/LV Substation TR***347X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E21 ex ARDNAREE | Ardnaree: T421 | Moy |  | 54.0705 | -9.1078
MV/LV Substation TR***348 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | C12 ex ROSSGEIR | Rossgeir: T41∥T42 | Letterkenny |  | 54.8036 | -7.5411
MV/LV Substation TR***349Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C18 ex BALLYJAMESDUFF | Ballyjamesduff: T42 | Shankill |  | 53.9547 | -7.0602
MV/LV Substation TR***359X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.388 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.038 | 0 | 0 | Constrained,otherwise capacity available =361.9kW. | --> | E23 ex ATHBOY | Athboy: T423 | Navan |  | 53.5098 | -6.8707
MV/LV Substation TR***389 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.122 | 4.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2121 | 0 |  | --> | E20 ex ENNISCRONE | Enniscrone: T421∥T422 | Moy |  | 54.2155 | -9.0829
MV/LV Substation TR***396Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | C31 ex KILBARRY | Kilbarry: T101 | Kilbarry |  | 51.9531 | -8.44
MV/LV Substation TR***397Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C19 ex SMEARLA | Smearla: T41 | Trien |  | 52.4415 | -9.3746
MV/LV Substation TR***4002 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis: T41∥T42 | Dalton |  | 53.7405 | -8.6281
MV/LV Substation TR***4020 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =380kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4032 | 0 |  | --> | E21 ex WHITECHURCH | Whitechurch: T421 | Kilbarry |  | 51.952 | -8.4657
MV/LV Substation TR***4023 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C15 ex TOOMEVARA | Toomevara: T42 | Nenagh |  | 52.9395 | -8.0298
MV/LV Substation TR***4024 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.9kW. | --> | C17 ex ATHBOY | Athboy: T42 | Navan |  | 53.6635 | -6.97
MV/LV Substation TR***4037 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =78kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0.09346 | 0 |  | --> | E17 ex MANORHAMILTON | Manorhamilton: T422 | Sligo |  | 54.234 | -8.3126
MV/LV Substation TR***403X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.167 | 3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20521 | 0 |  | --> | C15 ex CROSSMOLINA | Crossmolina: T41∥T42 | Moy |  | 54.1142 | -9.2944
MV/LV Substation TR***4044 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 5.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05325 | 0 |  | --> | E15 ex BALLYBUNION | Ballybunion: T421∥T422 | Trien |  | 52.5473 | -9.4727
MV/LV Substation TR***4050 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | C27 ex BALLYCROSSAUN | Ballycrossaun: T421∥T422 | Somerset |  | 53.1458 | -8.2872
MV/LV Substation TR***4055 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C25 ex PEMBROKE | Pembroke: T44 | Ringsend |  | 53.342 | -6.2391
MV/LV Substation TR***4061 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 2.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10159 | 0 |  | --> | C15 ex GLENGOOLE | Glengoole: T41 | Thurles |  | 52.7485 | -7.5734
MV/LV Substation TR***4061 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C17 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9407 | -8.0792
MV/LV Substation TR***4063 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | E13 ex LONGFORD | Longford: T421 | Richmond |  | 53.8488 | -7.6046
MV/LV Substation TR***4074 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.9kW. | --> | E17 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1273 | -7.2055
MV/LV Substation TR***4087 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | C16 ex KANTURK | Kanturk: T41∥T42 | Glenlara |  | 52.2623 | -8.8024
MV/LV Substation TR***4090 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C17 ex ATHBOY | Athboy: T42 | Navan |  | 53.6674 | -6.9731
MV/LV Substation TR***4092 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | E12 ex BELMULLET | Belmullet: T421 | Bellacorick |  | 54.2092 | -9.9704
MV/LV Substation TR***4131 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | E12 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 52.0805 | -9.9251
MV/LV Substation TR***4138 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C47 ex BEDFORD ROW | Bedford Row: T41 | Francis Street |  | 53.3437 | -6.262
MV/LV Substation TR***4148 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E11 ex FERNS | Ferns: T421 | Crane |  | 52.6565 | -6.5548
MV/LV Substation TR***4153 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.066 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10529 | 0 |  | --> | E19 ex LAWLESSTOWN | Lawlesstown: T421 | Doon |  | 52.4925 | -7.68
MV/LV Substation TR***4173 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex LOUGHANALLA | Loughanalla: T41∥T42 | Mullingar |  | 53.6898 | -7.364
MV/LV Substation TR***4179 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C15 ex TRIM | Trim: T41∥T42 | Navan |  | 53.557 | -6.7916
MV/LV Substation TR***4187 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | C21 ex CLONMINCH | Clonminch: T41 | Thornsberry |  | 53.2418 | -7.402
MV/LV Substation TR***4197 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400kW. | --> | C24 ex RAMSTOWN | Ramstown: T41∥T42 | Crane |  | 52.6743 | -6.3128
MV/LV Substation TR***420X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.046037 | 0 |  | --> | E18 ex BALLINROBE | Ballinrobe: T421∥T422 | Dalton |  | 53.6627 | -9.3559
MV/LV Substation TR***4213 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =378kVA. | --> | 0.38 | 0 | 0 | 0 | 0.076 | 0.32352 | 0 |  | --> | C21 ex PORTARLINGTON | Portarlington: T43 | Blake |  | 53.1516 | -7.1669
MV/LV Substation TR***4214 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest: T101 | Inchicore 110kv |  | 53.2845 | -6.4236
MV/LV Substation TR***421X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 2.7 |  | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.10075 | 0 |  | --> | E14 ex KILCOCK | Kilcock: T422 | Griffinrath |  | 53.484 | -6.7362
MV/LV Substation TR***4229 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E11 ex CAVAN | Cavan: T421 | Shankill |  | 54.0791 | -7.2612
MV/LV Substation TR***4258 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 25.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex ARKLOW | Arklow: T101∥T102 | Arklow |  | 52.796 | -6.1432
MV/LV Substation TR***427 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 3.5 |  | --> | 0.095 | 0 | 0 | 0 | 0.0247 | 0.078535 | 0 |  | --> | C18 ex TRAMORE | Tramore: T42 | Butlerstown |  | 52.2322 | -7.2017
MV/LV Substation TR***4276 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 7.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C11 ex GARRYCASTLE | Garrycastle: T41 | Athlone |  | 53.4155 | -7.9267
MV/LV Substation TR***4276 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C19 ex SEMPERIT | Semperit: T41 | Grange Castle |  | 53.3454 | -6.3494
MV/LV Substation TR***428 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =178kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20349 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton: T422 | Sligo |  | 54.3032 | -8.1866
MV/LV Substation TR***4292 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Building Structure | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C13 ex TRINITY | Trinity: T101 | Poolbeg |  | 53.3426 | -6.2491
MV/LV Substation TR***4293 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C12 ex TRINITY | Trinity: T102 | Poolbeg |  | 53.3426 | -6.2491
MV/LV Substation TR***430Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.242 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.4195 | 0 |  | --> | E20 ex BLESSINGTON | Blessington: T422 | Kilteel |  | 53.1739 | -6.5282
MV/LV Substation TR***4333 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E12 ex EMYVALE | Emyvale: T422 | Lisdrum |  | 54.3463 | -7.0591
MV/LV Substation TR***4372 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E17 ex BALTRASNA | Baltrasna: T121 | Baltrasna |  | 53.5399 | -6.5251
MV/LV Substation TR***4395 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C12 ex MOUNTRATH | Mountrath: T41∥T42 | Portlaoise |  | 52.9767 | -7.428
MV/LV Substation TR***4456 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =267kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MISERY HILL | Misery Hill: T102 | Poolbeg |  | 53.3456 | -6.2413
MV/LV Substation TR***4475 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =352kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =407.6kW. | --> | C19 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0364 | -7.3003
MV/LV Substation TR***456 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =105.7kW. | --> | E14 ex BELLACORICK | Bellacorick: T122 | Bellacorick |  | 54.2176 | -9.8182
MV/LV Substation TR***4583 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E20 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.4104 | -7.3931
MV/LV Substation TR***462X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown: T41 | Tonroe |  | 53.8878 | -8.6907
MV/LV Substation TR***4646 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =331kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4109 | 0 |  | --> | C28 ex TRINITY | Trinity: T102 | Poolbeg |  | 53.3397 | -6.2408
MV/LV Substation TR***470Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.373 | 3.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4043 | 0 |  | --> | C12 ex MAYFIELD | Mayfield: T42 | Kilbarry |  | 51.9033 | -8.4303
MV/LV Substation TR***471Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =175kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0 | 0 | Constrained,otherwise capacity available =201kW. | --> | C32 ex CLOYNE | Cloyne: T41 | Midleton |  | 51.8602 | -8.1311
MV/LV Substation TR***475X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =115kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0494 | 0.16115 | 0 |  | --> | E14 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.3409 | -6.9404
MV/LV Substation TR***496X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.9kW. | --> | C18 ex RATHDOWNEY | Rathdowney: T42 | Ikerrin |  | 52.854 | -7.6703
MV/LV Substation TR***499X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =191kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20144 | 0 |  | --> | C24 ex ATHLONE | Athlone: T41 | Athlone |  | 53.4057 | -7.9865
MV/LV Substation TR***511Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E21 ex WHITECHURCH | Whitechurch: T421 | Kilbarry |  | 51.952 | -8.445
MV/LV Substation TR***516 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C19 ex SMEARLA | Smearla: T41 | Trien |  | 52.4245 | -9.426
MV/LV Substation TR***517Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C13 ex MALAHIDE | Malahide: T41 | Glasmore |  | 53.414 | -6.1656
MV/LV Substation TR***532X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 7.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.6kW. | --> | E12 ex DUNFIRTH | Dunfirth: T122 | Dunfirth |  | 53.443 | -6.8609
MV/LV Substation TR***538Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =179kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =203.3kW. | --> | C14 ex TEMPLEMORE | Templemore: T42 | Ikerrin |  | 52.725 | -7.5835
MV/LV Substation TR***544X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C11 ex RATHMORE | Rathmore: T42 | Knockearagh |  | 52.0872 | -9.2052
MV/LV Substation TR***556 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =176kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2038 | 0 |  | --> | C14 ex MILFORD (NR) | Milford (nr): T41∥T42 | Letterkenny |  | 55.2253 | -7.7051
MV/LV Substation TR***560Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =366kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4054 | 0 |  | --> | C18 ex BALGADDY | Balgaddy: T42 | Grange Castle |  | 53.3411 | -6.4184
MV/LV Substation TR***585X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.154 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20723 | 0 |  | --> | C22 ex CAHIR | Cahir: T42 | Cahir |  | 52.3668 | -7.9287
MV/LV Substation TR***591 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex CRANMORE | Cranmore: T41∥T42 | Sligo |  | 54.2507 | -8.4528
MV/LV Substation TR***598 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.235 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0019 | 0.42356 | 0 |  | --> | C16 ex MONKSTOWN | Monkstown: T42 | Blackrock |  | 53.2973 | -6.1598
MV/LV Substation TR***598 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.343 | 4.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40902 | 0 |  | --> | C16 ex BALLYRICKARD | Ballyrickard: T41∥T42 | Tralee |  | 52.2795 | -9.7257
MV/LV Substation TR***600Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex LIBERTY STREET | Liberty Street: T102 | Liberty Street |  | 51.8944 | -8.4699
MV/LV Substation TR***622Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =156kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =206.9kW. | --> | C15 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0414 | -7.3033
MV/LV Substation TR***626 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 4.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | E13 ex MOVILLE | Moville: T421∥T422 | Trillick |  | 55.2699 | -7.0688
MV/LV Substation TR***630X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | E25 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6789 | -7.2762
MV/LV Substation TR***641 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.393 | 0.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0551 | 0.5 | 0 |  | --> | E16 ex DINGLE | Dingle: T422 | Oughtragh |  | 52.1382 | -10.2705
MV/LV Substation TR***641X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10064 | 0 |  | --> | C12 ex SAGGART | Saggart: T41∥T42 | Grange Castle |  | 53.2759 | -6.4953
MV/LV Substation TR***641X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 1.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10159 | 0 |  | --> | C18 ex DUNDALK | Dundalk: T41 | Dundalk |  | 54.0367 | -6.4567
MV/LV Substation TR***645 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E17 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1245 | -7.2112
MV/LV Substation TR***648 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10032 | 0 |  | --> | C15 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5504 | -6.7969
MV/LV Substation TR***649X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North: T41∥T42 | Ennis |  | 52.8404 | -9.0309
MV/LV Substation TR***655X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =313kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41368 | 0 |  | --> | C17 ex TOGHER | Togher: T41 | Trabeg |  | 51.8764 | -8.4814
MV/LV Substation TR***677 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052345 | 0 |  | --> | C16 ex BANAGHER | Banagher: T42 | Dallow |  | 53.1892 | -7.9991
MV/LV Substation TR***683Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 7.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E12 ex DUNFIRTH | Dunfirth: T122 | Dunfirth |  | 53.4237 | -6.9247
MV/LV Substation TR***687X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =172kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =204.4kW. | --> | C22 ex KNOCKAPHUNTA | Knockaphunta: T41∥T42 | Castlebar |  | 53.8468 | -9.3074
MV/LV Substation TR***696 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 5.3 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C12 ex SMEARLA | Smearla: T42 | Trien |  | 52.4333 | -9.5396
MV/LV Substation TR***729 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E18 ex STRANORLAR | Stranorlar: T422 | Letterkenny |  | 54.8086 | -7.7394
MV/LV Substation TR***738 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.122 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2121 | 0 |  | --> | C15 ex TRIM | Trim: T41∥T42 | Navan |  | 53.565 | -6.8015
MV/LV Substation TR***738 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =72kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10438 | 0 |  | --> | C17 ex SKIBBEREEN | Skibbereen: T41∥T42 | Dunmanway |  | 51.5024 | -9.2628
MV/LV Substation TR***749 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =30kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0531 | 0 |  | --> | C21 ex KILMONEY | Kilmoney: T41∥T42 | Trabeg |  | 51.7609 | -8.3918
MV/LV Substation TR***764X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C11 ex DERRYCRAMPH | Derrycramph: T41∥T42 | Shankill |  | 53.9635 | -7.3557
MV/LV Substation TR***764Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400kW. | --> | C22 ex BELLFIELD | Bellfield: T41∥T42 | Crane |  | 52.503 | -6.5647
MV/LV Substation TR***765 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =15kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0553 | 0 |  | --> | C21 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7623 | -6.2721
MV/LV Substation TR***785Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | C12 ex MOUNTRATH | Mountrath: T41∥T42 | Portlaoise |  | 52.9787 | -7.4303
MV/LV Substation TR***786 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | C19 ex SMEARLA | Smearla: T41 | Trien |  | 52.4261 | -9.4173
MV/LV Substation TR***793X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C17 ex SKIBBEREEN | Skibbereen: T41∥T42 | Dunmanway |  | 51.5068 | -9.2612
MV/LV Substation TR***802X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =175kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20396 | 0 |  | --> | C11 ex POLLERTON | Pollerton: T41 | Carlow |  | 52.8427 | -6.9083
MV/LV Substation TR***807 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 0.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10206 | 0 |  | --> | E31 ex TRIM | Trim: T421 | Navan |  | 53.5204 | -6.8251
MV/LV Substation TR***810X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E25 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.687 | -7.2747
MV/LV Substation TR***816 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.045885 | 0 |  | --> | C21 ex KILMONEY | Kilmoney: T41∥T42 | Trabeg |  | 51.7637 | -8.3976
MV/LV Substation TR***818X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E14 ex KILCOCK | Kilcock: T422 | Griffinrath |  | 53.4819 | -6.7253
MV/LV Substation TR***818Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E19 ex CAVAN | Cavan: T421 | Shankill |  | 53.9558 | -7.4469
MV/LV Substation TR***826Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =19kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.054725 | 0 |  | --> | E17 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.5747 | -6.717
MV/LV Substation TR***843 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 9.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C11 ex KILCOOLE | Kilcoole: T41∥T42 | Fassaroe |  | 53.0813 | -6.1071
MV/LV Substation TR***854 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053992 | 0 |  | --> | E16 ex MOHILL | Mohill: T421∥T422 | Carrick On Shannon |  | 53.917 | -7.8772
MV/LV Substation TR***864Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 2.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10408 | 0 |  | --> | C25 ex TYCOR | Tycor: T41∥T42 | Waterford |  | 52.2479 | -7.173
MV/LV Substation TR***871X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C18 ex KILLESHANDRA | Killeshandra: T41∥T42 | Gortawee |  | 54.0084 | -7.5206
MV/LV Substation TR***877 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | E12 ex BELMULLET | Belmullet: T421 | Bellacorick |  | 54.2199 | -9.9854
MV/LV Substation TR***878X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C21 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 52.8699 | -9.3583
MV/LV Substation TR***880Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =19kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =54.7kW. | --> | C22 ex PORTLAOISE | Portlaoise: T42 | Portlaoise |  | 53.1141 | -7.1532
MV/LV Substation TR***881 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 4.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10454 | 0 |  | --> | E16 ex MOHILL | Mohill: T421∥T422 | Carrick On Shannon |  | 53.9171 | -7.8734
MV/LV Substation TR***886Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =119kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =212.5kW. | --> | E14 ex EMYVALE | Emyvale: T422 | Lisdrum |  | 54.3704 | -6.9497
MV/LV Substation TR***891X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.356 | 7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40698 | 0 |  | --> | C11 ex ARDGEEHA | Ardgeeha: T41∥T42 | Doon |  | 52.3639 | -7.7045
MV/LV Substation TR***900 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C19 ex SMEARLA | Smearla: T41 | Trien |  | 52.4428 | -9.3746
MV/LV Substation TR***905 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.131 | 1.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20574 | 0 |  | --> | C17 ex TYMON | Tymon: T41 | Cookstown |  | 53.3008 | -6.3613
MV/LV Substation TR***927X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 2.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10222 | 0 |  | --> | E13 ex AGHADA | Aghada: T721 | N/A |  | 51.822 | -8.2341
MV/LV Substation TR***933X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C16 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 52.9353 | -9.3024
MV/LV Substation TR***945X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C21 ex KILMONEY | Kilmoney: T41∥T42 | Trabeg |  | 51.757 | -8.3957
MV/LV Substation TR***962X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05219 | 0 |  | --> | C18 ex DEERPARK | Deerpark: T41∥T42 | Ballydine |  | 52.5078 | -7.5054
MV/LV Substation TR***967X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 11.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | E16 ex WESTPORT | Westport: T421∥T422 | Castlebar |  | 53.7932 | -9.534
MV/LV Substation TR***970X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.249 | 9.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.038 | 0.38346 | 0 |  | --> | C14 ex TRABEG | Trabeg: T101 | Trabeg |  | 51.8722 | -8.4704
MV/LV Substation TR***974X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | C20 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.8338 | -9.009
MV/LV Substation TR***982X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.185 | 0.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =202.4kW. | --> | C16 ex GARRYSPILLANE | Garryspillane: T41 | Tipperary |  | 52.3585 | -8.4641
MV/LV Substation TR***991 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.478 | 8.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown: T102 | Carrickmines |  | 53.2985 | -6.3754
MV/LV Substation TR***996X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =130kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2109 | 0 |  | --> | C23 ex KILBARRY | Kilbarry: T101 | Kilbarry |  | 51.9095 | -8.5014
MV/LV Substation TS***285Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex DOUGLAS | Douglas: T42 | Trabeg |  | 51.8783 | -8.4344
MV/LV Substation TU***001Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C11 ex SCARIFF | Scariff: T42 | Ennis |  | 52.8899 | -8.5457
MV/LV Substation TU***002X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.04495 | 0 |  | --> | C22 ex CASTLEISLAND | Castleisland: T41∥T42 | Tralee |  | 52.2344 | -9.4352
MV/LV Substation TU***008Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =173kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20427 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.493 | -6.175
MV/LV Substation TU***009 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.132 | 0.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20659 | 0 |  | --> | C15 ex KYLEERAGH | Kyleeragh: T41 | Nenagh |  | 52.8692 | -8.1948
MV/LV Substation TU***009 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.112 | 1.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2136 | 0 |  | --> | C15 ex TULLA | Tulla: T41 | Ennis |  | 52.8679 | -8.7568
MV/LV Substation TU***010Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =177kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | C20 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1683 | -6.8391
MV/LV Substation TU***012 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C13 ex ERRIGAL | Errigal: T41 | Shankill |  | 54.0549 | -7.138
MV/LV Substation TU***015X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.172 | 4.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20443 | 0 |  | --> | E11 ex MOHILL | Mohill: T421∥T422 | Carrick On Shannon |  | 53.9233 | -7.8423
MV/LV Substation TU***018X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 4.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E15 ex MOHILL | Mohill: T421∥T422 | Carrick On Shannon |  | 54.0518 | -7.8017
MV/LV Substation TU***019X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E15 ex MOHILL | Mohill: T421∥T422 | Carrick On Shannon |  | 54.0472 | -7.8022
MV/LV Substation TU***021 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C18 ex BAILIEBORO | Bailieboro: T41∥T42 | Meath Hill |  | 53.8794 | -6.9676
MV/LV Substation TU***023 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.16 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2063 | 0 |  | --> | E15 ex TULLOW | Tullow: T421 | Carlow |  | 52.8023 | -6.7407
MV/LV Substation TU***025Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052037 | 0 |  | --> | E18 ex BIRR | Birr: T422 | Dallow |  | 53.1045 | -7.9047
MV/LV Substation TU***031Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =327kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41152 | 0 |  | --> | C17 ex CLONMINCH | Clonminch: T41 | Thornsberry |  | 53.2709 | -7.4967
MV/LV Substation TU***036 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.189 | 0.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.19676 | 0 |  | --> | C11 ex SRAH | Srah: T41∥T42 | Thornsberry |  | 53.2649 | -7.5035
MV/LV Substation TU***037 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.348 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40824 | 0 |  | --> | E15 ex TULLOW | Tullow: T421 | Carlow |  | 52.7964 | -6.749
MV/LV Substation TU***040 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.281 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0 | 0 | Constrained,otherwise capacity available =414.6kW. | --> | C19 ex TURLOUGH ROAD | Turlough Road: T43 | Castlebar |  | 53.8641 | -9.2941
MV/LV Substation TU***041 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.064 | 2.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0285 | 0.19063 | 0 |  | --> | C15 ex RINEANNA | Rineanna: T42 | Drumline |  | 52.7062 | -8.8891
MV/LV Substation TU***043 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 2.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E15 ex TULLOW | Tullow: T421 | Carlow |  | 52.7943 | -6.7463
MV/LV Substation TU***050Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.367 | 3.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40524 | 0 |  | --> | C12 ex MONEENAGEISHA | Moneenageisha: T42 | Galway 110kv |  | 53.2766 | -9.0397
MV/LV Substation TU***053 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =266kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41588 | 0 |  | --> | C16 ex ATHENRY | Athenry: T41∥T42 | Galway 110kv |  | 53.3041 | -8.7514
MV/LV Substation TU***055 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.284 | 10.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0171 | 0.40014 | 0 |  | --> | C12 ex ENNIS | Ennis: T102 | Ennis |  | 52.8495 | -8.9731
MV/LV Substation TU***063 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C22 ex CASTLEISLAND | Castleisland: T41∥T42 | Tralee |  | 52.2352 | -9.4373
MV/LV Substation TU***066Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =344kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40886 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.4877 | -6.1578
MV/LV Substation TU***072Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =71kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10454 | 0 |  | --> | C16 ex LOUGHREA | Loughrea: T41∥T42 | Somerset |  | 53.199 | -8.5904
MV/LV Substation TU***076 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.145 | 0.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.00665 | 0.4318 | 0 |  | --> | C17 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.8391 | -8.9842
MV/LV Substation TU***076 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C18 ex BAILIEBORO | Bailieboro: T41∥T42 | Meath Hill |  | 53.8799 | -6.9648
MV/LV Substation TU***077 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C14 ex ARDGEEHA | Ardgeeha: T41∥T42 | Doon |  | 52.4542 | -7.6504
MV/LV Substation TU***077Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.5kW. | --> | E11 ex MACROOM | Macroom: T422 | Macroom |  | 51.9404 | -8.7587
MV/LV Substation TU***081 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex GRANGE (DR) | Grange (dr): T42 | Grange (dr) |  | 53.4026 | -6.1945
MV/LV Substation TU***082 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 3.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | C24 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.5926 | -9.9825
MV/LV Substation TU***085 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | E17 ex RATHMORE | Rathmore: T421 | Knockearagh |  | 52.0723 | -9.1232
MV/LV Substation TU***086 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.018 | 1.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0.02945 | 0.023867 | 0 |  | --> | C20 ex RINEANNA | Rineanna: T41 | Drumline |  | 52.7105 | -8.8735
MV/LV Substation TU***088X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex LOUGHLINSTOWN | Loughlinstown: T41 | Carrickmines |  | 53.2478 | -6.1434
MV/LV Substation TU***089 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.136 | 2.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.20698 | 0 |  | --> | E14 ex BLESSINGTON | Blessington: T422 | Kilteel |  | 53.1255 | -6.5608
MV/LV Substation TU***095Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =351kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40776 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.4889 | -6.1571
MV/LV Substation TU***101 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 2.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | C20 ex KILRUSH | Kilrush: T41∥T42 | Tullabrack |  | 52.6727 | -9.4795
MV/LV Substation TU***104 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.079 | 1.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21846 | 0 |  | --> | C16 ex DERRYCRAMPH | Derrycramph: T41∥T42 | Shankill |  | 53.9866 | -7.3585
MV/LV Substation TU***109X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.007 | 2.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.056427 | 0 |  | --> | E17 ex KILROSS ROAD | Kilross Road: T421 | Tipperary |  | 52.4655 | -8.3413
MV/LV Substation TU***117Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.182 | 3.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20286 | 0 |  | --> | E16 ex ASHBOURNE | Ashbourne: T422 | Finglas |  | 53.5165 | -6.3998
MV/LV Substation TU***120 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 5.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C18 ex ABBEYLAND | Abbeyland: T42 | Navan |  | 53.63 | -6.7994
MV/LV Substation TU***121 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 5.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.04032 | 0 |  | --> | E13 ex MOY | Moy: T421∥T422 | Moy |  | 54.0912 | -9.1911
MV/LV Substation TU***123 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.292 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41692 | 0 |  | --> | C16 ex DERRYCRAMPH | Derrycramph: T41∥T42 | Shankill |  | 53.985 | -7.3567
MV/LV Substation TU***124 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex SPIDDAL | Spiddal: T42 | Screeb |  | 53.2384 | -9.4863
MV/LV Substation TU***126Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.9kW. | --> | C18 ex BALLYBAY | Ballybay: T41∥T42 | Lisdrum |  | 54.1832 | -6.9425
MV/LV Substation TU***137 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.321 | 9.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0209 | 0.5 | 0 |  | --> | C12 ex TRABEG | Trabeg: T101 | Trabeg |  | 51.8882 | -8.4668
MV/LV Substation TU***151Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =349kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40808 | 0 |  | --> | C23 ex CLONMINCH | Clonminch: T41 | Thornsberry |  | 53.2694 | -7.4752
MV/LV Substation TU***157X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C11 ex KILMALLOCK | Kilmallock: T42 | Charleville |  | 52.3961 | -8.5311
MV/LV Substation TU***162 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 5.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | E15 ex BALLYBUNION | Ballybunion: T421∥T422 | Trien |  | 52.5407 | -9.6102
MV/LV Substation TU***163Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =311kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.4 | 0 |  | --> | C13 ex BALGADDY | Balgaddy: T41 | Grange Castle |  | 53.3362 | -6.4434
MV/LV Substation TU***164X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E21 ex ARDNAREE | Ardnaree: T421 | Moy |  | 54.0822 | -9.1051
MV/LV Substation TU***164Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.19 | 0 | 0 | 0 | 0.02565 | 0.19661 | 0 |  | --> | C13 ex BALGADDY | Balgaddy: T41 | Grange Castle |  | 53.336 | -6.4385
MV/LV Substation TU***165 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =137kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20483 | 0 |  | --> | C23 ex POLLERTON | Pollerton: T41 | Carlow |  | 52.8322 | -6.9111
MV/LV Substation TU***168Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0.0475 | 0.5 | 0 |  | --> | C26 ex POPPINTREE | Poppintree: T102 | Finglas |  | 53.418 | -6.293
MV/LV Substation TU***169Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =361kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4062 | 0 |  | --> | C13 ex POPPINTREE | Poppintree: T101 | Finglas |  | 53.418 | -6.2862
MV/LV Substation TU***175X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.048 | 0.6 |  | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =103kW. | --> | C18 ex ATHBOY | Athboy: T42 | Navan |  | 53.6259 | -6.9265
MV/LV Substation TU***183 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E12 ex CASTLELYONS | Castlelyons: T421∥T422 | Barrymore |  | 52.0545 | -8.3737
MV/LV Substation TU***187Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 2.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C15 ex TULLYNAMALRA | Tullynamalra: T41∥T42 | Meath Hill |  | 54.0304 | -6.7051
MV/LV Substation TU***199Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =395kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4008 | 0 |  | --> | C13 ex POPPINTREE | Poppintree: T101 | Finglas |  | 53.4183 | -6.284
MV/LV Substation TU***210 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C18 ex CASTLEBLAYNEY | Castleblayney: T42 | Dundalk |  | 54.1351 | -6.7012
MV/LV Substation TU***211Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E21 ex FINEA | Finea: T421∥T422 | Shankill |  | 53.8831 | -7.3704
MV/LV Substation TU***216 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =72kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10438 | 0 |  | --> | E18 ex CREAGH | Creagh: T421∥T422 | Athlone |  | 53.4743 | -8.515
MV/LV Substation TU***219 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 3.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | C24 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.5861 | -9.9633
MV/LV Substation TU***223Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =163kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20583 | 0 |  | --> | E18 ex DALTON | Dalton: T421∥T422 | Dalton |  | 53.6673 | -8.956
MV/LV Substation TU***224Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0 | 0 | Constrained,otherwise capacity available =45.9kW. | --> | C32 ex CLOYNE | Cloyne: T41 | Midleton |  | 51.8601 | -8.1262
MV/LV Substation TU***235Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.282 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.40744 | 0 |  | --> | E15 ex TULLOW | Tullow: T421 | Carlow |  | 52.8016 | -6.7362
MV/LV Substation TU***237Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.119 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.0171 | 0.19455 | 0 |  | --> | C30 ex ACADEMY STREET | Academy Street: T44 | Navan |  | 53.6529 | -6.6582
MV/LV Substation TU***240Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52kW. | --> | E13 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.2508 | -7.0072
MV/LV Substation TU***243 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.356 | 0.4 | Constrained,otherwise capacity available =396kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40064 | 0 |  | --> | C11 ex KYLEERAGH | Kyleeragh: T41 | Nenagh |  | 52.8715 | -8.2153
MV/LV Substation TU***258Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E19 ex TULLOW | Tullow: T421 | Carlow |  | 52.8037 | -6.7033
MV/LV Substation TU***264X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 7.4 |  | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0 | 0 | Constrained,otherwise capacity available =94.3kW. | --> | E14 ex ARIGNA | Arigna: T121 | Arigna |  | 54.0353 | -7.8399
MV/LV Substation TU***271X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.167 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20121 | 0 |  | --> | C22 ex HOWTH JUNCTION | Howth Junction: T42 | Grange (dr) |  | 53.3838 | -6.1722
MV/LV Substation TU***274Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053697 | 0 |  | --> | C14 ex ARDGEEHA | Ardgeeha: T41∥T42 | Doon |  | 52.5005 | -7.5943
MV/LV Substation TU***276X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 0.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.4kW. | --> | C18 ex DUNGLOE | Dungloe: T42 | Ardnagappary |  | 54.9978 | -8.446
MV/LV Substation TU***282 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 4.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E20 ex ENNISCRONE | Enniscrone: T421∥T422 | Moy |  | 54.2086 | -9.092
MV/LV Substation TU***287Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C18 ex SALLINS | Sallins: T42 | Griffinrath |  | 53.2904 | -6.6099
MV/LV Substation TU***290X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.163 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20183 | 0 |  | --> | C12 ex SUTTON | Sutton: T42 | Grange (dr) |  | 53.395 | -6.1321
MV/LV Substation TU***293 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.101 | 0.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0114 | 0.20324 | 0 |  | --> | C19 ex BREWERY ROAD | Brewery Road: T41 | Carrickmines |  | 53.2719 | -6.1945
MV/LV Substation TU***305 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | E12 ex MILLTOWN (SR) | Milltown (sr): T422 | Oughtragh |  | 52.0968 | -9.8296
MV/LV Substation TU***306X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 5 |  | --> | 0.095 | 0 | 0 | 0 | 0.0038 | 0.09977 | 0 |  | --> | C19 ex KILMORE | Kilmore: T101 | Finglas |  | 53.4096 | -6.2299
MV/LV Substation TU***312Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | E14 ex BLESSINGTON | Blessington: T422 | Kilteel |  | 53.1253 | -6.5592
MV/LV Substation TU***314X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex CASTLEBLAYNEY | Castleblayney: T41 | Dundalk |  | 54.1157 | -6.7696
MV/LV Substation TU***316X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 4.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0076 | 0.042477 | 0 |  | --> | E17 ex EDGEWORTHSTOWN | Edgeworthstown: T421∥T422 | Richmond |  | 53.6268 | -7.6568
MV/LV Substation TU***322Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 4.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.19401 | 0 |  | --> | E11 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.2168 | -6.5323
MV/LV Substation TU***336X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =288kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0266 | 0.38952 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.4872 | -6.155
MV/LV Substation TU***343Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | C18 ex SALLINS | Sallins: T42 | Griffinrath |  | 53.286 | -6.624
MV/LV Substation TU***357 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =398kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40032 | 0 |  | --> | C17 ex ROSEHILL | Rosehill: T41 | Kilkenny |  | 52.5647 | -7.3472
MV/LV Substation TU***358Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E15 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.6297 | -6.2458
MV/LV Substation TU***364X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C39 ex NORTH QUAYS | North Quays: T102 | Poolbeg |  | 53.3561 | -6.2309
MV/LV Substation TU***366Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E19 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.3141 | -6.893
MV/LV Substation TU***374 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.285 | 10.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0247 | 0.39198 | 0 |  | --> | C31 ex SALTHILL | Salthill: T101 | Salthill |  | 53.2885 | -9.0775
MV/LV Substation TU***384 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.059622 | 0 |  | --> | C19 ex KILMORE | Kilmore: T101 | Finglas |  | 53.4098 | -6.2324
MV/LV Substation TU***387 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =196kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.19464 | 0 |  | --> | C21 ex CLONMINCH | Clonminch: T41 | Thornsberry |  | 53.236 | -7.4045
MV/LV Substation TU***388X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.128 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.2052 | 0 |  | --> | C18 ex SUTTON | Sutton: T42 | Grange (dr) |  | 53.3946 | -6.1264
MV/LV Substation TU***398 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =203kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.42232 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central: T45 | Inchicore 110kv |  | 53.3409 | -6.3135
MV/LV Substation TU***399X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =86kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10222 | 0 |  | --> | C15 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9413 | -8.1142
MV/LV Substation TU***4003 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 51.8777 | -10.1914
MV/LV Substation TU***4005 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0 | 0 | Constrained,otherwise capacity available =44.5kW. | --> | C13 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6447 | -8.0893
MV/LV Substation TU***4007 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.168 | 5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20506 | 0 |  | --> | C19 ex KILMORE | Kilmore: T101 | Finglas |  | 53.4085 | -6.2289
MV/LV Substation TU***401 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E15 ex TULLOW | Tullow: T421 | Carlow |  | 52.7976 | -6.7529
MV/LV Substation TU***403 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 0.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101.3kW. | --> | E18 ex CARNDONAGH | Carndonagh: T421∥T422 | Trillick |  | 55.2519 | -7.2484
MV/LV Substation TU***4036 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex BALLYRICKARD | Ballyrickard: T41∥T42 | Tralee |  | 52.3209 | -9.7538
MV/LV Substation TU***4037 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9286 | -8.0363
MV/LV Substation TU***4039 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 4.4 |  | --> | 0.095 | 0 | 0 | 0 | 0.0323 | 0 | 0 | Constrained,otherwise capacity available =67.4kW. | --> | E13 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.2587 | -7.0615
MV/LV Substation TU***404 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 4.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0528 | 0 |  | --> | C18 ex BAILIEBORO | Bailieboro: T41∥T42 | Meath Hill |  | 53.8833 | -6.957
MV/LV Substation TU***4043 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E13 ex EDGEWORTHSTOWN | Edgeworthstown: T421∥T422 | Richmond |  | 53.7298 | -7.5596
MV/LV Substation TU***4047 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =262kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42148 | 0 |  | --> | E22 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.4923 | -6.1977
MV/LV Substation TU***4050 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E11 ex CARRIGALLEN | Carrigallen: T421 | Carrick On Shannon |  | 54.1233 | -7.7696
MV/LV Substation TU***406 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C23 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.522 | -8.8016
MV/LV Substation TU***4065 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C19 ex SHERCOCK | Shercock: T41∥T42 | Meath Hill |  | 53.9692 | -6.898
MV/LV Substation TU***4072 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C12 ex ROSSGEIR | Rossgeir: T41∥T42 | Letterkenny |  | 54.8346 | -7.5418
MV/LV Substation TU***408 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.045795 | 0 |  | --> | E17 ex BRUFF | Bruff: T421 | Limerick |  | 52.4947 | -8.5445
MV/LV Substation TU***408 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 3.9 |  | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0.092685 | 0 |  | --> | C20 ex OAKFIELD | Oakfield: T42 | Sligo |  | 54.2728 | -8.5656
MV/LV Substation TU***408 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =164kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0266 | 0.17768 | 0 |  | --> | C15 ex LITTLE MILLS | Little Mills: T41 | Dundalk |  | 53.9804 | -6.3986
MV/LV Substation TU***4083 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E18 ex CARNDONAGH | Carndonagh: T421∥T422 | Trillick |  | 55.2515 | -7.2461
MV/LV Substation TU***4087 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E17 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 52.9101 | -7.3725
MV/LV Substation TU***4089 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.8kW. | --> | C20 ex CLOONLOUGH | Cloonlough: T41∥T42 | Barrymore |  | 52.2446 | -8.2633
MV/LV Substation TU***4096 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex POPPINTREE | Poppintree: T101 | Finglas |  | 53.4173 | -6.2841
MV/LV Substation TU***409X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E13 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.2556 | -7.0132
MV/LV Substation TU***409Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.377 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.39766 | 0 |  | --> | C18 ex DRYBRIDGE | Drybridge: T42 | Drybridge |  | 53.7225 | -6.3886
MV/LV Substation TU***4109 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | E20 ex ENNISCRONE | Enniscrone: T421∥T422 | Moy |  | 54.2083 | -9.0979
MV/LV Substation TU***4118 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =53.1kW. | --> | C17 ex ATHBOY | Athboy: T42 | Navan |  | 53.7044 | -7.0414
MV/LV Substation TU***4119 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C19 ex KILMORE | Kilmore: T101 | Finglas |  | 53.4095 | -6.2294
MV/LV Substation TU***4138 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E11 ex ARDFINNAN | Ardfinnan: T421 | Cahir |  | 52.3085 | -7.9642
MV/LV Substation TU***4143 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.354 | 0.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0798 | 0.3233 | 0 |  | --> | C12 ex ORANMORE | Oranmore: T44 | Galway 110kv |  | 53.2738 | -8.9768
MV/LV Substation TU***4151 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C18 ex KNOCKAPHUNTA | Knockaphunta: T41∥T42 | Castlebar |  | 53.8479 | -9.3399
MV/LV Substation TU***415X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 7.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C21 ex ATHY | Athy: T101 | Athy |  | 52.9701 | -7.101
MV/LV Substation TU***4164 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =330kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.40504 | 0 |  | --> | C13 ex CLONMINCH | Clonminch: T41 | Thornsberry |  | 53.2755 | -7.4864
MV/LV Substation TU***4174 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex LOUGHLINSTOWN | Loughlinstown: T42 | Carrickmines |  | 53.2446 | -6.1547
MV/LV Substation TU***4175 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex LOUGHLINSTOWN | Loughlinstown: T42 | Carrickmines |  | 53.2458 | -6.1562
MV/LV Substation TU***4176 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex LOUGHLINSTOWN | Loughlinstown: T42 | Carrickmines |  | 53.2472 | -6.1576
MV/LV Substation TU***419 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.7kW. | --> | C13 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6298 | -8.0978
MV/LV Substation TU***4195 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E24 ex BIRR | Birr: T422 | Dallow |  | 53.1089 | -7.899
MV/LV Substation TU***4213 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C20 ex CLOONLOUGH | Cloonlough: T41∥T42 | Barrymore |  | 52.2352 | -8.2738
MV/LV Substation TU***4241 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C13 ex ERRIGAL | Errigal: T41 | Shankill |  | 53.9921 | -7.1642
MV/LV Substation TU***426X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 3.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C24 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.5537 | -10.0104
MV/LV Substation TU***426Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C23 ex POLLERTON | Pollerton: T41 | Carlow |  | 52.8333 | -6.9113
MV/LV Substation TU***4270 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.1kW. | --> | E19 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.3151 | -6.9871
MV/LV Substation TU***4274 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C13 ex POPPINTREE | Poppintree: T101 | Finglas |  | 53.4173 | -6.2788
MV/LV Substation TU***4276 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex POPPINTREE | Poppintree: T101 | Finglas |  | 53.4171 | -6.2699
MV/LV Substation TU***4293 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 7.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E22 ex BANOGE | Banoge: T122 | Banoge |  | 52.6117 | -6.384
MV/LV Substation TU***430X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 2.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | C11 ex CASTLECOMER | Castlecomer: T41∥T42 | Ballyragget |  | 52.7191 | -7.1633
MV/LV Substation TU***432 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton: T422 | Sligo |  | 54.2896 | -7.8879
MV/LV Substation TU***4335 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E19 ex TULLOW | Tullow: T421 | Carlow |  | 52.81 | -6.722
MV/LV Substation TU***4338 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C13 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.7498 | -6.3834
MV/LV Substation TU***4348 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex DRYBRIDGE | Drybridge: T42 | Drybridge |  | 53.7218 | -6.3895
MV/LV Substation TU***434X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052495 | 0 |  | --> | C11 ex LOUGHTAGALLA | Loughtagalla: T41∥T42 | Thurles |  | 52.6698 | -7.684
MV/LV Substation TU***434Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.9kW. | --> | E13 ex ABBEYLEIX | Abbeyleix: T422 | Portlaoise |  | 52.9252 | -7.3052
MV/LV Substation TU***435Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.344 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40886 | 0 |  | --> | C23 ex TINAHASK | Tinahask: T41∥T42 | Arklow |  | 52.7778 | -6.1807
MV/LV Substation TU***437 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0.026 | 3.2 |  | --> | 0.0285 | 0 | 0 | 0 | 0.0057 | 0.024633 | 0 |  | --> | C19 ex RECESS | Recess: T41 | Galway 110kv |  | 53.4368 | -9.8689
MV/LV Substation TU***4378 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =85kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10237 | 0 |  | --> | C15 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6633 | -7.436
MV/LV Substation TU***437X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 3.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10095 | 0 |  | --> | C24 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.5982 | -9.9769
MV/LV Substation TU***437X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C23 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.5699 | -9.0949
MV/LV Substation TU***438X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | E11 ex BIRDHILL | Birdhill: T421 | Ardnacrusha |  | 52.7046 | -8.4021
MV/LV Substation TU***4395 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C17 ex ROSEHILL | Rosehill: T41 | Kilkenny |  | 52.5683 | -7.3491
MV/LV Substation TU***443Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.396 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.39064 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.8235 | -6.894
MV/LV Substation TU***448Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0057 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C17 ex ROSCREA | Roscrea: T41 | Ikerrin |  | 52.9473 | -7.7906
MV/LV Substation TU***4562 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E17 ex LONGFORD | Longford: T421 | Richmond |  | 53.7907 | -7.5536
MV/LV Substation TU***459 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C11 ex SRAH | Srah: T41∥T42 | Thornsberry |  | 53.274 | -7.5051
MV/LV Substation TU***469Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.089 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.0475 | 0.167 | 0 |  | --> | E19 ex TULLOW | Tullow: T421 | Carlow |  | 52.8102 | -6.7212
MV/LV Substation TU***475 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | E17 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.0983 | -7.2283
MV/LV Substation TU***475X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex GALWAY 110KV | Galway 110kv: T103 | Galway 110kv |  | 53.2833 | -8.9816
MV/LV Substation TU***475X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.179 | 4.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20333 | 0 |  | --> | E17 ex BAGENALSTOWN | Bagenalstown: T421∥T422 | Carlow |  | 52.7099 | -6.9359
MV/LV Substation TU***480Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052037 | 0 |  | --> | C19 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.2004 | -6.9892
MV/LV Substation TU***483 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.148 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =203.1kW. | --> | C15 ex BUNDORAN | Bundoran: T41∥T42 | Cathaleens Fall |  | 54.4687 | -8.3297
MV/LV Substation TU***496Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 3.3 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C13 ex ERRIGAL | Errigal: T41 | Shankill |  | 53.9777 | -7.104
MV/LV Substation TU***512X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 51.8745 | -10.1901
MV/LV Substation TU***522 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | C18 ex SALLINS | Sallins: T42 | Griffinrath |  | 53.2895 | -6.6163
MV/LV Substation TU***525 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0342 | 0.5 | 0 |  | --> | C15 ex RINEANNA | Rineanna: T42 | Drumline |  | 52.7055 | -8.8812
MV/LV Substation TU***529X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0019 | 0.049107 | 0 |  | --> | C21 ex CARRICKMACROSS | Carrickmacross: T41 | Meath Hill |  | 53.9583 | -6.7112
MV/LV Substation TU***532 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 1.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10268 | 0 |  | --> | E15 ex GORT | Gort: T41∥T42 | Ennis |  | 53.1353 | -8.7863
MV/LV Substation TU***532Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C13 ex ERRIGAL | Errigal: T41 | Shankill |  | 54.0489 | -7.1438
MV/LV Substation TU***535X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C18 ex KILLESHANDRA | Killeshandra: T41∥T42 | Gortawee |  | 53.985 | -7.5295
MV/LV Substation TU***546Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.4885 | -6.153
MV/LV Substation TU***550X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =345kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4087 | 0 |  | --> | C12 ex SPIDDAL | Spiddal: T42 | Screeb |  | 53.2382 | -9.487
MV/LV Substation TU***550Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex ROSEHILL | Rosehill: T41 | Kilkenny |  | 52.5684 | -7.3466
MV/LV Substation TU***552X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E15 ex RATHMORE | Rathmore: T421 | Knockearagh |  | 52.1472 | -9.1818
MV/LV Substation TU***555Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E11 ex LISDRUM | Lisdrum: T422 | Lisdrum |  | 54.2658 | -6.9061
MV/LV Substation TU***556Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =76kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10377 | 0 |  | --> | E20 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.2578 | -7.0823
MV/LV Substation TU***562 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.335 | 10.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41026 | 0 |  | --> | C29 ex SALTHILL | Salthill: T101 | Salthill |  | 53.2774 | -9.0869
MV/LV Substation TU***568 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =33kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.046647 | 0 |  | --> | C13 ex BUTTEVANT | Buttevant: T41∥T42 | Mallow |  | 52.2244 | -8.5814
MV/LV Substation TU***570Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.309 | 4 |  | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.4063 | 0 |  | --> | E16 ex TULLOW | Tullow: T422 | Carlow |  | 52.8087 | -6.7254
MV/LV Substation TU***576Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.388 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40192 | 0 |  | --> | C15 ex DERRYCRAMPH | Derrycramph: T41∥T42 | Shankill |  | 53.9894 | -7.3553
MV/LV Substation TU***577Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.297 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41614 | 0 |  | --> | C15 ex DERRYCRAMPH | Derrycramph: T41∥T42 | Shankill |  | 53.9883 | -7.357
MV/LV Substation TU***578 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | C22 ex CASTLEISLAND | Castleisland: T41∥T42 | Tralee |  | 52.2352 | -9.4431
MV/LV Substation TU***579 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.3kW. | --> | C12 ex TIMOLEAGUE | Timoleague: T41 | Bandon |  | 51.6964 | -8.8225
MV/LV Substation TU***580 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C23 ex GLENTIES | Glenties: T41 | Binbane |  | 54.7792 | -8.3273
MV/LV Substation TU***584Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C20 ex ROSCOMMON | Roscommon: T42 | Lanesboro |  | 53.7772 | -8.2461
MV/LV Substation TU***584Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.164 | 5.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20568 | 0 |  | --> | E13 ex CRANE | Crane: T122 | Crane |  | 52.4391 | -6.473
MV/LV Substation TU***587 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =74kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10408 | 0 |  | --> | C12 ex CRANMORE | Cranmore: T41∥T42 | Sligo |  | 54.2425 | -8.4706
MV/LV Substation TU***587 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 3.8 |  | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0 | 0 | Constrained,otherwise capacity available =97.9kW. | --> | C18 ex TURLOUGH ROAD | Turlough Road: T41∥T42 | Castlebar |  | 53.8839 | -9.2161
MV/LV Substation TU***588 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 1.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.8kW. | --> | E14 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1537 | -7.4527
MV/LV Substation TU***588 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0528 | 0 |  | --> | C13 ex ERRIGAL | Errigal: T41 | Shankill |  | 53.9859 | -7.1547
MV/LV Substation TU***590X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10111 | 0 |  | --> | E12 ex TULLOW | Tullow: T422 | Carlow |  | 52.8075 | -6.7259
MV/LV Substation TU***590Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.055 | 1.6 |  | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.10195 | 0 |  | --> | C20 ex ROSCOMMON | Roscommon: T42 | Lanesboro |  | 53.7799 | -8.2556
MV/LV Substation TU***595X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E21 ex FINEA | Finea: T421∥T422 | Shankill |  | 53.8424 | -7.2973
MV/LV Substation TU***601X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.341 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.39334 | 0 |  | --> | C21 ex GALWAY 110KV | Galway 110kv: T103 | Galway 110kv |  | 53.2816 | -8.9844
MV/LV Substation TU***602 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.096 | 1.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.03135 | 0.18297 | 0 |  | --> | C16 ex DERRYCRAMPH | Derrycramph: T41∥T42 | Shankill |  | 53.9852 | -7.3515
MV/LV Substation TU***609X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C11 ex DERRYCRAMPH | Derrycramph: T41∥T42 | Shankill |  | 53.95 | -7.1273
MV/LV Substation TU***611Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =87kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.1kW. | --> | C13 ex DRUMBEAR | Drumbear: T41∥T42 | Lisdrum |  | 54.2385 | -6.9735
MV/LV Substation TU***632 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 3.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.2kW. | --> | C12 ex TELAYDON | Telaydon: T42 | Lisdrum |  | 54.2583 | -6.9552
MV/LV Substation TU***642X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E21 ex DALTON | Dalton: T421∥T422 | Dalton |  | 53.7938 | -9.1445
MV/LV Substation TU***651X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.355 | 2 |  | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.39214 | 0 |  | --> | C12 ex CAPPAMORE | Cappamore: T41∥T42 | Ardnacrusha |  | 52.6152 | -8.3434
MV/LV Substation TU***653X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 3.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400kW. | --> | C18 ex TURLOUGH ROAD | Turlough Road: T41∥T42 | Castlebar |  | 53.8834 | -9.2076
MV/LV Substation TU***656Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex MOUNTGORRY | Mountgorry: T42 | Grange (dr) |  | 53.4445 | -6.2262
MV/LV Substation TU***658 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C21 ex CARRIGTWOHILL | Carrigtwohill: T42 | Cow Cross |  | 51.9057 | -8.2821
MV/LV Substation TU***659X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C14 ex DRYBRIDGE | Drybridge: T42 | Drybridge |  | 53.736 | -6.4055
MV/LV Substation TU***674Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =127kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =211.3kW. | --> | C15 ex MOUNTMELLICK | Mountmellick: T41∥T42 | Portlaoise |  | 53.1237 | -7.3329
MV/LV Substation TU***676Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 5.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0 | 0 | Constrained,otherwise capacity available =44.5kW. | --> | C17 ex BANDON | Bandon: T101 | Bandon |  | 51.7586 | -8.646
MV/LV Substation TU***682 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0323 | 0.5 | 0 |  | --> | C11 ex BALLYBODEN | Ballyboden: T41 | Cookstown |  | 53.2824 | -6.275
MV/LV Substation TU***690 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 4.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0152 | 0 | 0 | Constrained,otherwise capacity available =34.8kW. | --> | E14 ex MOVILLE | Moville: T421∥T422 | Trillick |  | 55.1651 | -7.1079
MV/LV Substation TU***694Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05219 | 0 |  | --> | C15 ex TULLYNAMALRA | Tullynamalra: T41∥T42 | Meath Hill |  | 54.0619 | -6.8076
MV/LV Substation TU***696 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.066 | 1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10529 | 0 |  | --> | C15 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5915 | -6.8517
MV/LV Substation TU***700Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 2.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101kW. | --> | E11 ex LISDRUM | Lisdrum: T422 | Lisdrum |  | 54.2669 | -6.9187
MV/LV Substation TU***706 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.358 | 3.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.40266 | 0 |  | --> | C24 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.5885 | -9.9648
MV/LV Substation TU***710X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C20 ex BALLYGAR | Ballygar: T42 | Athlone |  | 53.5237 | -8.3078
MV/LV Substation TU***711X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 3.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.4kW. | --> | C18 ex TURLOUGH ROAD | Turlough Road: T41∥T42 | Castlebar |  | 53.8836 | -9.2137
MV/LV Substation TU***712Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.367 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40524 | 0 |  | --> | C15 ex TULLYNAMALRA | Tullynamalra: T41∥T42 | Meath Hill |  | 54.0255 | -6.7075
MV/LV Substation TU***724 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =34kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052495 | 0 |  | --> | E18 ex BALLINROBE | Ballinrobe: T421∥T422 | Dalton |  | 53.6568 | -9.3654
MV/LV Substation TU***729Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 5.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C22 ex CLOON | Cloon: T42 | Cloon |  | 53.4964 | -8.8452
MV/LV Substation TU***730 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis: T41∥T42 | Dalton |  | 53.7031 | -8.7898
MV/LV Substation TU***730X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C21 ex CARRICKMACROSS | Carrickmacross: T41 | Meath Hill |  | 53.9549 | -6.6986
MV/LV Substation TU***735 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =58kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0266 | 0 | 0 | Constrained,otherwise capacity available =78.5kW. | --> | C13 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6458 | -8.1134
MV/LV Substation TU***738 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 3.3 |  | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.10075 | 0 |  | --> | C13 ex ERRIGAL | Errigal: T41 | Shankill |  | 54.0498 | -7.148
MV/LV Substation TU***746Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =90kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10159 | 0 |  | --> | C15 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6615 | -7.4435
MV/LV Substation TU***769X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown: T101 | Inchicore 110kv |  | 53.2914 | -6.4268
MV/LV Substation TU***769Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.356 | 4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40698 | 0 |  | --> | E12 ex TULLOW | Tullow: T422 | Carlow |  | 52.8067 | -6.7273
MV/LV Substation TU***771X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E12 ex MILLTOWN (SR) | Milltown (sr): T422 | Oughtragh |  | 52.1038 | -9.8213
MV/LV Substation TU***771X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C16 ex CURRA | Curra: T41 | Somerset |  | 53.0292 | -8.3193
MV/LV Substation TU***790 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 3.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052495 | 0 |  | --> | C24 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.5893 | -9.974
MV/LV Substation TU***799X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =91kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10143 | 0 |  | --> | C12 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.997 | -7.8968
MV/LV Substation TU***799X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex SPIDDAL | Spiddal: T42 | Screeb |  | 53.2457 | -9.3054
MV/LV Substation TU***800 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =42.2kW. | --> | E13 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.2829 | -7.0251
MV/LV Substation TU***804X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.3kW. | --> | E11 ex CHARLEVILLE | Charleville: T422 | Charleville |  | 52.471 | -8.6676
MV/LV Substation TU***807 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex BAILIEBORO | Bailieboro: T41∥T42 | Meath Hill |  | 53.8801 | -6.9709
MV/LV Substation TU***809 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =16kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.055157 | 0 |  | --> | E47 ex CLAREGALWAY | Claregalway: T421 | Galway 110kv |  | 53.381 | -8.8542
MV/LV Substation TU***827 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.5kW. | --> | C19 ex BALLYBAY | Ballybay: T41∥T42 | Lisdrum |  | 54.0427 | -6.8703
MV/LV Substation TU***827X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.306 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.39876 | 0 |  | --> | C17 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.736 | -6.416
MV/LV Substation TU***827Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =375kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40398 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.4868 | -6.1515
MV/LV Substation TU***828 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052037 | 0 |  | --> | C13 ex ERRIGAL | Errigal: T41 | Shankill |  | 54.0097 | -7.2054
MV/LV Substation TU***833 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =33kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.046647 | 0 |  | --> | C15 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6721 | -7.425
MV/LV Substation TU***835Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C17 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.5089 | -8.8346
MV/LV Substation TU***840X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =36kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05219 | 0 |  | --> | E21 ex FINEA | Finea: T421∥T422 | Shankill |  | 53.8446 | -7.3017
MV/LV Substation TU***841 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =87kVA. | --> | 0.095 | 0 | 0 | 0 | 0.019 | 0.08206 | 0 |  | --> | C15 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6633 | -7.4315
MV/LV Substation TU***842 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C15 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6645 | -7.4256
MV/LV Substation TU***844X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =283kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.4143 | 0 |  | --> | C23 ex POLLERTON | Pollerton: T41 | Carlow |  | 52.8249 | -6.9094
MV/LV Substation TU***847X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 7.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.7kW. | --> | E12 ex CHURCHTOWN | Churchtown: T422 | Rathkeale |  | 52.4456 | -9.0742
MV/LV Substation TU***847Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C18 ex SALLINS | Sallins: T42 | Griffinrath |  | 53.2904 | -6.6131
MV/LV Substation TU***855 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 3.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.6kW. | --> | C18 ex TURLOUGH ROAD | Turlough Road: T41∥T42 | Castlebar |  | 53.8816 | -9.1963
MV/LV Substation TU***872 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05142 | 0 |  | --> | E47 ex CLAREGALWAY | Claregalway: T421 | Galway 110kv |  | 53.3663 | -8.9061
MV/LV Substation TU***873 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.0484 | 0 |  | --> | C17 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.7367 | -6.4273
MV/LV Substation TU***879X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.176 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2038 | 0 |  | --> | C14 ex CARRAROE | Carraroe: T42 | Screeb |  | 53.2377 | -9.4894
MV/LV Substation TU***893 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C14 ex MONEENAGEISHA | Moneenageisha: T42 | Galway 110kv |  | 53.2838 | -9.0372
MV/LV Substation TU***895X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =181kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20302 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.4926 | -6.1937
MV/LV Substation TU***901 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =21kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.054432 | 0 |  | --> | E11 ex KILCOLGAN | Kilcolgan: T421 | Galway 110kv |  | 53.1009 | -9.0621
MV/LV Substation TU***907 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0 | 0 | Constrained,otherwise capacity available =30kVA. | --> | 0.0285 | 0 | 0 | 0 | 0 | 0.030001 | 0 |  | --> | C21 ex CLONMINCH | Clonminch: T41 | Thornsberry |  | 53.2481 | -7.4782
MV/LV Substation TU***907X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10392 | 0 |  | --> | C17 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.723 | -6.4064
MV/LV Substation TU***912 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 2.2 |  | --> | 0.095 | 0 | 0 | 0 | 0.01425 | 0.089535 | 0 |  | --> | C16 ex KILCULLEN | Kilcullen: T42 | Stratford |  | 53.1331 | -6.8135
MV/LV Substation TU***913 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0.026 | 1.2 |  | --> | 0.0285 | 0 | 0 | 0 | 0 | 0.030633 | 0 |  | --> | C24 ex MULLAGH | Mullagh: T44 | Meath Hill |  | 53.8449 | -6.9342
MV/LV Substation TU***916 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.395 | 5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4008 | 0 |  | --> | C12 ex BALLYTIVNAN | Ballytivnan: T42 | Sligo |  | 54.3757 | -8.37
MV/LV Substation TU***930X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.171 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.19959 | 0 |  | --> | C14 ex DRYBRIDGE | Drybridge: T42 | Drybridge |  | 53.7399 | -6.4149
MV/LV Substation TU***933X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 2.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.4kW. | --> | E17 ex LISDRUM | Lisdrum: T422 | Lisdrum |  | 54.2341 | -7.053
MV/LV Substation TU***939X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.197 | 1.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20048 | 0 |  | --> | C15 ex TULLA | Tulla: T41 | Ennis |  | 52.8755 | -8.7626
MV/LV Substation TU***943X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.7 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex BELGARD | Belgard: T42 | Cookstown |  | 53.2883 | -6.3694
MV/LV Substation TU***963Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | E18 ex TULLOW | Tullow: T422 | Carlow |  | 52.8464 | -6.7595
MV/LV Substation TU***966 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C16 ex ROSSGEIR | Rossgeir: T41∥T42 | Letterkenny |  | 54.869 | -7.5156
MV/LV Substation TU***975 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 3.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.3kW. | --> | C17 ex BALLYSHANNON | Ballyshannon: T41∥T42 | Cathaleens Fall |  | 54.5197 | -8.1632
MV/LV Substation TU***982Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =88kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1019 | 0 |  | --> | C15 ex KILMONEY | Kilmoney: T41∥T42 | Trabeg |  | 51.8226 | -8.5223
MV/LV Substation TU***984 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C16 ex ROSSGEIR | Rossgeir: T41∥T42 | Letterkenny |  | 54.8925 | -7.492
MV/LV Substation TU***985 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.045575 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9657 | -6.6939
MV/LV Substation TU***995 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =33kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.6kW. | --> | C12 ex TIMOLEAGUE | Timoleague: T41 | Bandon |  | 51.6942 | -8.7389
MV/LV Substation TU***996X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =368kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.3931 | 0 |  | --> | C16 ex LOUGHREA | Loughrea: T41∥T42 | Somerset |  | 53.1954 | -8.5922
MV/LV Substation TU***999 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0 | 0 | Constrained,otherwise capacity available =44.3kW. | --> | E17 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.0871 | -7.246
MV/LV Substation TV***619X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex TYMON | Tymon: T42 | Cookstown |  | 53.3096 | -6.3552
MV/LV Substation TV***999 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 6.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | E18 ex SPRINGS | Springs: T421∥T422 | Dungarvan |  | 52.0555 | -7.6345
MV/LV Substation TW***009 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.292 | 4 |  | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0 | 0 | Constrained,otherwise capacity available =402.9kW. | --> | C20 ex LISMORE | Lismore: T41∥T42 | Dungarvan |  | 52.1475 | -7.8532
MV/LV Substation TW***033 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C12 ex PARKMORE | Parkmore: T41∥T42 | Galway 110kv |  | 53.3051 | -9.0021
MV/LV Substation TW***034 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =95kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | C12 ex PARKMORE | Parkmore: T41∥T42 | Galway 110kv |  | 53.3059 | -8.9994
MV/LV Substation TW***082 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.04532 | 0 |  | --> | C17 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.4742 | -8.7029
MV/LV Substation TW***282 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =196kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.19564 | 0 |  | --> | C13 ex WOODFORD | Woodford: T41∥T42 | Knockearagh |  | 52.0508 | -9.4491
MV/LV Substation TW***4057 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | C21 ex LEE BRIDGE | Lee Bridge: T41 | Macroom |  | 51.8989 | -9.1434
MV/LV Substation TW***414 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =83kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10268 | 0 |  | --> | C13 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8657 | -8.3236
MV/LV Substation TW***4141 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex BALLYBODEN | Ballyboden: T42 | Cookstown |  | 53.2814 | -6.3123
MV/LV Substation TW***4145 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.8 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex BALLYBODEN | Ballyboden: T42 | Cookstown |  | 53.2795 | -6.3119
MV/LV Substation TW***4265 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | C15 ex KANTURK | Kanturk: T41∥T42 | Glenlara |  | 52.1278 | -8.8112
MV/LV Substation TW***608 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C14 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6557 | -8.1054
MV/LV Substation TW***622 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.392 | 3.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40128 | 0 |  | --> | E16 ex CRATLOE | Cratloe: T421∥T422 | Ardnacrusha |  | 52.6788 | -8.6994
MV/LV Substation TW***665 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C11 ex MOUNTMELLICK | Mountmellick: T41∥T42 | Portlaoise |  | 53.1556 | -7.3696
MV/LV Substation TW***873 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.155 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20707 | 0 |  | --> | C26 ex BAILIEBORO | Bailieboro: T41∥T42 | Meath Hill |  | 53.916 | -6.9658
MV/LV Substation TW***953Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =83kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10268 | 0 |  | --> | C18 ex NAAS | Naas: T42 | Newbridge |  | 53.1706 | -6.699
MV/LV Substation TW***984X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 11.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2516 | -9.1528
MV/LV Substation TY***002 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.146 | 2.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.19846 | 0 |  | --> | C20 ex NENAGH | Nenagh: T42 | Nenagh |  | 52.8569 | -8.1918
MV/LV Substation TY***019 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.434 | 2.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0019 | 0.5 | 0 |  | --> | C18 ex TYCOR | Tycor: T41∥T42 | Waterford |  | 52.2565 | -7.1294
MV/LV Substation TY***071 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.194 | 4.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20096 | 0 |  | --> | C12 ex TYMON | Tymon: T42 | Cookstown |  | 53.3005 | -6.3432
MV/LV Substation TY***105 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.394 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.39496 | 0 |  | --> | C13 ex MOUNT MISERY | Mount Misery: T41 | Waterford |  | 52.2631 | -7.1014
MV/LV Substation TY***113X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 6.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.6kW. | --> | E18 ex RATHKEALE | Rathkeale: T421∥T422 | Rathkeale |  | 52.5266 | -8.9457
MV/LV Substation TY***137 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.9kW. | --> | C21 ex SWINFORD | Swinford: T41∥T42 | Castlebar |  | 53.9506 | -8.9689
MV/LV Substation TY***153X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 6.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | E21 ex ABBEYFEALE | Abbeyfeale: T421 | Trien |  | 52.3895 | -9.2837
MV/LV Substation TY***170X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.285 | 4.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41298 | 0 |  | --> | C20 ex TYMON | Tymon: T42 | Cookstown |  | 53.2984 | -6.3515
MV/LV Substation TY***171X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.319 | 4.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.40976 | 0 |  | --> | C20 ex TYMON | Tymon: T42 | Cookstown |  | 53.2988 | -6.3496
MV/LV Substation TY***172X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.323 | 4.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41214 | 0 |  | --> | C20 ex TYMON | Tymon: T42 | Cookstown |  | 53.3004 | -6.3503
MV/LV Substation TY***182X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =365kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40556 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central: T45 | Inchicore 110kv |  | 53.3375 | -6.322
MV/LV Substation TY***201 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.154 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20723 | 0 |  | --> | C15 ex COES ROAD | Coes Road: T41∥T42 | Dundalk |  | 53.9971 | -6.3788
MV/LV Substation TY***209Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.142 | 0.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20907 | 0 |  | --> | C25 ex NENAGH | Nenagh: T41 | Nenagh |  | 52.8578 | -8.1886
MV/LV Substation TY***210 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 0.3 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10315 | 0 |  | --> | C25 ex NENAGH | Nenagh: T41 | Nenagh |  | 52.8554 | -8.188
MV/LV Substation TY***220X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 4.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | E13 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.3097 | -7.1213
MV/LV Substation TY***226Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.142 | 0.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.01995 | 0.18807 | 0 |  | --> | C23 ex NENAGH | Nenagh: T41 | Nenagh |  | 52.8523 | -8.1901
MV/LV Substation TY***259Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0152 | 0.036037 | 0 |  | --> | C17 ex CURRA | Curra: T41 | Somerset |  | 53.1516 | -8.3775
MV/LV Substation TY***271 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C16 ex CREGG ROAD | Cregg Road: T41∥T42 | Ballydine |  | 52.3461 | -7.3356
MV/LV Substation TY***275X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =34kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052495 | 0 |  | --> | E20 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.3938 | -7.3874
MV/LV Substation TY***296Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =184kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20255 | 0 |  | --> | C41 ex COLLEGE PARK | College Park: T103 | College Park |  | 53.4132 | -6.3877
MV/LV Substation TY***306 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 3.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.038 | 0 | 0 | Constrained,otherwise capacity available =360kW. | --> | E17 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 51.9519 | -7.8662
MV/LV Substation TY***324Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | E16 ex LISDRUM | Lisdrum: T422 | Lisdrum |  | 54.2647 | -6.8945
MV/LV Substation TY***348 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.3 | 0.3 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C25 ex NENAGH | Nenagh: T41 | Nenagh |  | 52.8529 | -8.1864
MV/LV Substation TY***364 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =309kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex GLOUCESTER PLACE | Gloucester Place: T41 | Mcdermott |  | 53.3576 | -6.2549
MV/LV Substation TY***374 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CURRA | Curra: T41 | Somerset |  | 53.1534 | -8.3774
MV/LV Substation TY***385Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | C39 ex COLLEGE PARK | College Park: T103 | College Park |  | 53.4151 | -6.3963
MV/LV Substation TY***393 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | E20 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.3927 | -7.3706
MV/LV Substation TY***4006 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.19 | 0 | 0 | 0 | 0.02185 | 0.19238 | 0 |  | --> | C14 ex MACETOWN | Macetown: T102 | Macetown |  | 53.41 | -6.3981
MV/LV Substation TY***4008 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =315kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41338 | 0 |  | --> | C14 ex MACETOWN | Macetown: T102 | Macetown |  | 53.4109 | -6.401
MV/LV Substation TY***4035 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =364kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40572 | 0 |  | --> | C39 ex COLLEGE PARK | College Park: T103 | College Park |  | 53.4224 | -6.3818
MV/LV Substation TY***4090 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.336 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41012 | 0 |  | --> | C21 ex TYMON | Tymon: T41 | Cookstown |  | 53.2984 | -6.3456
MV/LV Substation TY***414Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C39 ex COLLEGE PARK | College Park: T103 | College Park |  | 53.4204 | -6.3845
MV/LV Substation TY***415Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =350kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40792 | 0 |  | --> | C39 ex COLLEGE PARK | College Park: T103 | College Park |  | 53.4194 | -6.3832
MV/LV Substation TY***416Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C39 ex COLLEGE PARK | College Park: T103 | College Park |  | 53.4207 | -6.3817
MV/LV Substation TY***417Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C39 ex COLLEGE PARK | College Park: T103 | College Park |  | 53.4194 | -6.3825
MV/LV Substation TY***420Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | E17 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.8886 | -6.6155
MV/LV Substation TY***4252 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =66kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.22034 | 0 |  | --> | E20 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.3901 | -7.3782
MV/LV Substation TY***4253 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =123kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21195 | 0 |  | --> | E20 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.3866 | -7.381
MV/LV Substation TY***4254 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =71kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21962 | 0 |  | --> | E20 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.3864 | -7.3811
MV/LV Substation TY***4266 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C11 ex LOUGHSHINNY | Loughshinny: T41 | Glasmore |  | 53.5322 | -6.1325
MV/LV Substation TY***4277 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex MACETOWN | Macetown: T102 | Macetown |  | 53.4108 | -6.4022
MV/LV Substation TY***4354 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =393kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40112 | 0 |  | --> | E18 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.3352 | -7.0478
MV/LV Substation TY***458Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.371 | 1.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40462 | 0 |  | --> | E14 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.1855 | -7.0807
MV/LV Substation TY***498X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.01045 | 0.04195 | 0 |  | --> | C16 ex CREGG ROAD | Cregg Road: T41∥T42 | Ballydine |  | 52.3453 | -7.3536
MV/LV Substation TY***498Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =396kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40064 | 0 |  | --> | C39 ex COLLEGE PARK | College Park: T103 | College Park |  | 53.4195 | -6.3805
MV/LV Substation TY***546 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.041 | 2.5 |  | --> | 0.095 | 0 | 0 | 0 | 0.01805 | 0.09001 | 0 |  | --> | C17 ex CURRA | Curra: T41 | Somerset |  | 53.1503 | -8.3734
MV/LV Substation TY***570 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.057 | 0.1 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C12 ex OLDBAWN | Oldbawn: T42 | Cookstown |  | 53.2771 | -6.3463
MV/LV Substation TY***572 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =387kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.01045 | 0.5 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central: T45 | Inchicore 110kv |  | 53.3359 | -6.3258
MV/LV Substation TY***602 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C13 ex POPPINTREE | Poppintree: T101 | Finglas |  | 53.4299 | -6.3034
MV/LV Substation TY***661Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C11 ex LOUGHSHINNY | Loughshinny: T41 | Glasmore |  | 53.535 | -6.1518
MV/LV Substation TY***670X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central: T45 | Inchicore 110kv |  | 53.3387 | -6.3219
MV/LV Substation TY***689X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex BALLYGAR | Ballygar: T41 | Athlone |  | 53.4908 | -8.4479
MV/LV Substation TY***727 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =28kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.0434 | 0 |  | --> | C11 ex LOUGHSHINNY | Loughshinny: T41 | Glasmore |  | 53.5335 | -6.1551
MV/LV Substation TY***728X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C16 ex CREGG ROAD | Cregg Road: T41∥T42 | Ballydine |  | 52.3482 | -7.3484
MV/LV Substation TY***744Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | E13 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.3002 | -7.1227
MV/LV Substation TY***766X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.144 | 10.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20876 | 0 |  | --> | C30 ex WATERFORD IND EST | Waterford Ind Est: T42∥T44 | Butlerstown |  | 52.2504 | -7.1386
MV/LV Substation TY***778X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.106 | 1.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0.21249 | 0 |  | --> | C17 ex TYMON | Tymon: T41 | Cookstown |  | 53.3074 | -6.3726
MV/LV Substation TY***780X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.057 | 0.1 | Constrained,otherwise capacity available =435kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.02565 | 0.5 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn: T42 | Cookstown |  | 53.279 | -6.3661
MV/LV Substation TY***858Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052345 | 0 |  | --> | C11 ex LOUGHSHINNY | Loughshinny: T41 | Glasmore |  | 53.5326 | -6.1367
MV/LV Substation TY***874 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.323 | 4.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41214 | 0 |  | --> | C22 ex TYMON | Tymon: T42 | Cookstown |  | 53.2955 | -6.3465
MV/LV Substation TY***875 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.105 | 4.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20964 | 0 |  | --> | C20 ex TYMON | Tymon: T42 | Cookstown |  | 53.2975 | -6.3474
MV/LV Substation TY***877X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 2.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =53.2kW. | --> | E16 ex LISDRUM | Lisdrum: T422 | Lisdrum |  | 54.2649 | -6.8929
MV/LV Substation TY***898Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 4.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.7kW. | --> | E13 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.2948 | -7.0169
MV/LV Substation TY***945Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.173 | 4.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20427 | 0 |  | --> | E11 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.1744 | -6.5891
MV/LV Substation TZ***245 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =53kVA. | --> | 0.095 | 0 | 0 | 0 | 0.00855 | 0.098245 | 0 |  | --> | C31 ex KILBARRY | Kilbarry: T101 | Kilbarry |  | 51.9303 | -8.4607
MV/LV Substation U ***014 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 10.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex SALTHILL | Salthill: T101 | Salthill |  | 53.2871 | -9.066
MV/LV Substation U ***015 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.457 | 10.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex SALTHILL | Salthill: T101 | Salthill |  | 53.2885 | -9.0658
MV/LV Substation U ***061Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C16 ex LEIXLIP | Leixlip: T42 | Griffinrath |  | 53.3402 | -6.5226
MV/LV Substation U ***146 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.387 | 10.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0057 | 0.5 | 0 |  | --> | C20 ex ENNIS | Ennis: T102 | Ennis |  | 52.8461 | -8.985
MV/LV Substation U ***440 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00285 | 0.5 | 0 |  | --> | C18 ex LIBERTY STREET | Liberty Street: T102 | Liberty Street |  | 51.8925 | -8.4934
MV/LV Substation U ***684Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C39 ex CASTLEVIEW | Castleview: T101 | Castleview |  | 51.9077 | -8.3466
MV/LV Substation U ***793X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =177kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.069851 | 0 | Constrained,otherwise capacity available =203.6kW. | --> | E24 ex BIRR | Birr: T422 | Dallow |  | 53.0925 | -7.8809
MV/LV Substation U.***246 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 10.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex SALTHILL | Salthill: T101 | Salthill |  | 53.2855 | -9.0652
MV/LV Substation U.***324 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 0.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex LEESON STREET | Leeson Street: T42 | Milltown (dr) |  | 53.3355 | -6.2584
MV/LV Substation U.***370 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.365 | 11.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40556 | 0 |  | --> | C36 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2915 | -9.0771
MV/LV Substation U.***4038 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =494kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0076 | 0.5 | 0 |  | --> | C06 ex PEMBROKE | Pembroke: T44 | Ringsend |  | 53.3305 | -6.2336
MV/LV Substation UA***020X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.246 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.4099 | 0 |  | --> | C20 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8794 | -8.5329
MV/LV Substation UA***748 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.286 | 5.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.41484 | 0 |  | --> | C17 ex OUGHTERARD | Oughterard: T41∥T42 | Galway 110kv |  | 53.4272 | -9.3268
MV/LV Substation UA***756 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.027 | 5.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.22085 | 0 |  | --> | C17 ex OUGHTERARD | Oughterard: T41∥T42 | Galway 110kv |  | 53.4275 | -9.3181
MV/LV Substation UC***110 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex DENNEHYS CROSS | Dennehys Cross: T41 | Trabeg |  | 51.8934 | -8.5011
MV/LV Substation UC***302Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =485kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex DENNEHYS CROSS | Dennehys Cross: T42 | Trabeg |  | 51.8944 | -8.5014
MV/LV Substation UC***321 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 5.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C21 ex BALLINCOLLIG | Ballincollig: T41 | Kilbarry |  | 51.8787 | -8.5891
MV/LV Substation UC***4054 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BELFIELD | Belfield: T41 | Blackrock |  | 53.3039 | -6.2222
MV/LV Substation UC***521Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C14 ex DENNEHYS CROSS | Dennehys Cross: T42 | Trabeg |  | 51.8953 | -8.5156
MV/LV Substation UD***030X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.01045 | 0.5 | 0 |  | --> | C16 ex MILFORD (NR) | Milford (nr): T41∥T42 | Letterkenny |  | 55.0508 | -7.8345
MV/LV Substation UD***128X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.377 | 1.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.39766 | 0 |  | --> | C15 ex SCREEB | Screeb: T41 | Screeb |  | 53.3213 | -9.8106
MV/LV Substation UD***150Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C23 ex TINAHASK | Tinahask: T41∥T42 | Arklow |  | 52.7842 | -6.1692
MV/LV Substation UD***191X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.177 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.00665 | 0 | 0 | Constrained,otherwise capacity available =196.6kW. | --> | E17 ex BELMULLET | Belmullet: T421 | Bellacorick |  | 54.1194 | -10.1021
MV/LV Substation UD***267X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05766 | 0 |  | --> | C18 ex DUNDALK | Dundalk: T41 | Dundalk |  | 54.0353 | -6.3862
MV/LV Substation UD***4055 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 7.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C13 ex ATHY | Athy: T101 | Athy |  | 52.9927 | -6.9932
MV/LV Substation UD***4131 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C12 ex CARRAROE | Carraroe: T42 | Screeb |  | 53.2909 | -9.5511
MV/LV Substation UD***614X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =181kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20302 | 0 |  | --> | C13 ex SPIDDAL | Spiddal: T42 | Screeb |  | 53.2494 | -9.2818
MV/LV Substation UD***617 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.364 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =405.7kW. | --> | E15 ex GWEEDORE | Gweedore: T421 | Ardnagappary |  | 55.1417 | -8.106
MV/LV Substation UD***639X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =197kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20048 | 0 |  | --> | C14 ex MILFORD (NR) | Milford (nr): T41∥T42 | Letterkenny |  | 55.244 | -7.7112
MV/LV Substation UD***644 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.182 | 0.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.19386 | 0 |  | --> | E15 ex DINGLE | Dingle: T421 | Oughtragh |  | 52.1437 | -10.2899
MV/LV Substation UD***719X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.197 | 0.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20048 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 51.8377 | -10.2625
MV/LV Substation UG***319 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 10.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052647 | 0 |  | --> | C27 ex SALTHILL | Salthill: T101 | Salthill |  | 53.3286 | -9.174
MV/LV Substation UG***4131 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.059 | 10.5 |  | --> | 0.095 | 0 | 0 | 0 | 0.00285 | 0.10335 | 0 |  | --> | C27 ex SALTHILL | Salthill: T101 | Salthill |  | 53.3303 | -9.1708
MV/LV Substation UG***566X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 10.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C27 ex SALTHILL | Salthill: T101 | Salthill |  | 53.326 | -9.1725
MV/LV Substation UG***912 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown: T41 | Tonroe |  | 53.9101 | -8.7268
MV/LV Substation UI***4166 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C18 ex NEWBROOK | Newbrook: T42 | Mullingar |  | 53.4849 | -7.5799
MV/LV Substation UI***927X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.347 | 10.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.3924 | 0 |  | --> | C27 ex SALTHILL | Salthill: T101 | Salthill |  | 53.3383 | -9.1767
MV/LV Substation UL***226Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.384 | 9.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40256 | 0 |  | --> | C17 ex SINGLAND | Singland: T101 | Singland |  | 52.6757 | -8.5819
MV/LV Substation UL***269 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.223 | 3.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0171 | 0.40936 | 0 |  | --> | C17 ex MOUNT MERRION | Mount Merrion: T41 | Carrickmines |  | 53.29 | -6.1925
MV/LV Substation UL***364 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.18 | 2.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.4237 | 0 |  | --> | C23 ex SALLYNOGGIN ROAD | Sallynoggin Road: T41 | Cherrywood |  | 53.2788 | -6.1082
MV/LV Substation UL***4345 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C12 ex GRANAGH | Granagh: T41∥T42 | Waterford |  | 52.3148 | -7.2025
MV/LV Substation UL***539X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.04 | 0 | Constrained,otherwise capacity available =78kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10346 | 0 |  | --> | C17 ex GRAIGUENAMANAGH | Graiguenamanagh: T41∥T42 | Kilkenny |  | 52.5859 | -6.9468
MV/LV Substation UL***628Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C12 ex GRANAGH | Granagh: T41∥T42 | Waterford |  | 52.3209 | -7.2032
MV/LV Substation UL***814 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 6.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10111 | 0 |  | --> | C20 ex COLLINSTOWN | Collinstown: T41∥T42 | Grange (dr) |  | 53.4315 | -6.2289
MV/LV Substation UM***033X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | C21 ex MILFORD (NR) | Milford (nr): T41∥T42 | Letterkenny |  | 55.1706 | -7.7988
MV/LV Substation UM***034X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.9kW. | --> | E17 ex CARNDONAGH | Carndonagh: T421∥T422 | Trillick |  | 55.3059 | -7.2352
MV/LV Substation UM***048X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =16kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.055157 | 0 |  | --> | C21 ex MILFORD (NR) | Milford (nr): T41∥T42 | Letterkenny |  | 55.1667 | -7.8004
MV/LV Substation UM***193X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C15 ex KILCAR | Kilcar: T41 | Binbane |  | 54.6453 | -8.5803
MV/LV Substation UM***200 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00855 | 0 | 0 | Constrained,otherwise capacity available =42.4kW. | --> | E14 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1585 | -7.4382
MV/LV Substation UM***258 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.1kW. | --> | E12 ex MACROOM | Macroom: T422 | Macroom |  | 51.9153 | -8.9157
MV/LV Substation UM***264Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =95kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.8kW. | --> | C11 ex PORTARLINGTON | Portarlington: T41∥T42 | Portlaoise |  | 53.1796 | -7.0718
MV/LV Substation UM***362X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E14 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1602 | -7.436
MV/LV Substation UM***419X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E19 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.7057 | -6.4967
MV/LV Substation UM***4281 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C11 ex LEE BRIDGE | Lee Bridge: T41 | Macroom |  | 51.9027 | -8.9412
MV/LV Substation UM***598Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C19 ex BALLYBAY | Ballybay: T41∥T42 | Lisdrum |  | 54.0227 | -6.8256
MV/LV Substation UM***741 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.18 | 1.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =193.2kW. | --> | E14 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1575 | -7.439
MV/LV Substation UN***044X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex MOY | Moy: T421∥T422 | Moy |  | 54.115 | -9.1703
MV/LV Substation UN***053Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 5.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10315 | 0 |  | --> | E13 ex CRANE | Crane: T122 | Crane |  | 52.4527 | -6.4005
MV/LV Substation UN***095Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =321kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41244 | 0 |  | --> | C18 ex DENNEHYS CROSS | Dennehys Cross: T42 | Trabeg |  | 51.8906 | -8.526
MV/LV Substation UN***096 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 7.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C05 ex AHANE | Ahane: T102 | Ahane |  | 52.6646 | -8.5023
MV/LV Substation UN***097 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.392 | 7.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40128 | 0 |  | --> | C05 ex AHANE | Ahane: T102 | Ahane |  | 52.6641 | -8.5036
MV/LV Substation UN***099 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.166 | 7.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20537 | 0 |  | --> | C05 ex AHANE | Ahane: T102 | Ahane |  | 52.6634 | -8.5048
MV/LV Substation UN***100 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.325 | 7.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0475 | 0.36182 | 0 |  | --> | C05 ex AHANE | Ahane: T102 | Ahane |  | 52.6647 | -8.503
MV/LV Substation UN***103 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C05 ex AHANE | Ahane: T102 | Ahane |  | 52.6638 | -8.5049
MV/LV Substation UN***108Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.349 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40808 | 0 |  | --> | C22 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8744 | -8.5414
MV/LV Substation UN***109 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex COES ROAD | Coes Road: T41∥T42 | Dundalk |  | 53.9999 | -6.3783
MV/LV Substation UN***113 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.199 | 3.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20016 | 0 |  | --> | C14 ex OAKFIELD | Oakfield: T42 | Sligo |  | 54.216 | -8.4697
MV/LV Substation UN***128 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =179kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20333 | 0 |  | --> | C16 ex SHANNON | Shannon: T42 | Drumline |  | 52.6989 | -8.9017
MV/LV Substation UN***130 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C05 ex AHANE | Ahane: T102 | Ahane |  | 52.6634 | -8.5057
MV/LV Substation UN***131 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.381 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =403kW. | --> | C12 ex FOYNES | Foynes: T42 | Rathkeale |  | 52.6124 | -9.0992
MV/LV Substation UN***256Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.39 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4016 | 0 |  | --> | C22 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8742 | -8.5426
MV/LV Substation UN***269 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.318 | 4.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.4069 | 0 |  | --> | C17 ex MONEENAGEISHA | Moneenageisha: T41 | Galway 110kv |  | 53.2764 | -9.0602
MV/LV Substation UN***274 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =86kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.21344 | 0 |  | --> | C17 ex SKIBBEREEN | Skibbereen: T41∥T42 | Dunmanway |  | 51.5577 | -9.1428
MV/LV Substation UN***298X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex OAKFIELD | Oakfield: T42 | Sligo |  | 54.273 | -8.4804
MV/LV Substation UN***313 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.371 | 4.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40462 | 0 |  | --> | C11 ex DUNMANWAY | Dunmanway: T43 | Dunmanway |  | 51.7155 | -9.1096
MV/LV Substation UN***314 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.165 | 4.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20552 | 0 |  | --> | C11 ex DUNMANWAY | Dunmanway: T43 | Dunmanway |  | 51.7156 | -9.1121
MV/LV Substation UN***395X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex ERRIGAL | Errigal: T41 | Shankill |  | 54.0519 | -7.1463
MV/LV Substation UN***419Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | C16 ex RATHDRUM | Rathdrum: T42 | Arklow |  | 52.9372 | -6.2408
MV/LV Substation UN***4259 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex COLLEGE PARK | College Park: T101 | College Park |  | 53.4194 | -6.3502
MV/LV Substation UN***4266 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.221 | 7.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C07 ex AHANE | Ahane: T102 | Ahane |  | 52.6661 | -8.503
MV/LV Substation UN***429 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =51kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0038 | 0.10354 | 0 |  | --> | C17 ex SKIBBEREEN | Skibbereen: T41∥T42 | Dunmanway |  | 51.5563 | -9.1429
MV/LV Substation UN***4294 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex COLLEGE PARK | College Park: T101 | College Park |  | 53.415 | -6.3472
MV/LV Substation UN***480Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CENTRE PARK ROAD | Marina: T106 | Marina |  | 51.8965 | -8.4674
MV/LV Substation UN***544 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =356kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40698 | 0 |  | --> | C12 ex TUAM SOUTH | Tuam South: T42 | Cloon |  | 53.5204 | -8.846
MV/LV Substation UN***581Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =272kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.41396 | 0 |  | --> | E11 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.3355 | -7.0621
MV/LV Substation UN***628Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex COLLEGE PARK | College Park: T101 | College Park |  | 53.4135 | -6.3471
MV/LV Substation UN***629Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C23 ex COLLEGE PARK | College Park: T101 | College Park |  | 53.4205 | -6.3425
MV/LV Substation UN***630X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.398 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.39632 | 0 |  | --> | C12 ex BELGARD | Belgard: T42 | Cookstown |  | 53.2914 | -6.3692
MV/LV Substation UN***708Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C14 ex DRYBRIDGE | Drybridge: T42 | Drybridge |  | 53.7361 | -6.403
MV/LV Substation UN***743 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.357 | 3.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =406.8kW. | --> | C15 ex DERRYBEG | Derrybeg: T41∥T42 | Ardnagappary |  | 55.0628 | -8.279
MV/LV Substation UN***880X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =156kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.42822 | 0 |  | --> | C22 ex TOGHER | Togher: T42 | Trabeg |  | 51.8703 | -8.508
MV/LV Substation UN***904 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10016 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 51.8599 | -10.2897
MV/LV Substation UN***908 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.329 | 1.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =411.2kW. | --> | E17 ex BELMULLET | Belmullet: T421 | Bellacorick |  | 54.2205 | -9.9829
MV/LV Substation UN***909 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.392 | 1.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =401.3kW. | --> | E17 ex BELMULLET | Belmullet: T421 | Bellacorick |  | 54.2199 | -9.982
MV/LV Substation UN***939 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C11 ex ROSSGEIR | Rossgeir: T41∥T42 | Letterkenny |  | 54.8153 | -7.5161
MV/LV Substation UP***003 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.453 | 2.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00285 | 0.5 | 0 |  | --> | C16 ex SPA ROAD | Spa Road: T41∥T42 | Doon |  | 52.3558 | -7.7026
MV/LV Substation UP***003 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.135 | 5.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21014 | 0 |  | --> | E18 ex CRANE | Crane: T122 | Crane |  | 52.5178 | -6.28
MV/LV Substation UP***024 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =83kVA. | --> | 0.19 | 0 | 0 | 0 | 0.019 | 0.19788 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.5184 | -6.1119
MV/LV Substation UP***034X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.209 | 0.2 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BISHOPSTOWN | Bishopstown: T41 | Kilbarry |  | 51.872 | -8.5253
MV/LV Substation UP***042 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.146 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.0076 | 0.20046 | 0 |  | --> | C17 ex GREYSTONES | Greystones: T41 | Fassaroe |  | 53.1445 | -6.0826
MV/LV Substation UP***056 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.155 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20707 | 0 |  | --> | C18 ex TYCOR | Tycor: T41∥T42 | Waterford |  | 52.2585 | -7.1283
MV/LV Substation UP***071 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.369 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.39494 | 0 |  | --> | C16 ex MANOR STREET | Manor Street: T42 | Waterford |  | 52.2478 | -7.1027
MV/LV Substation UP***080Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =26kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053697 | 0 |  | --> | C31 ex KILBARRY | Kilbarry: T101 | Kilbarry |  | 51.952 | -8.435
MV/LV Substation UP***081Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C17 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.6984 | -8.022
MV/LV Substation UP***084Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =75kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10392 | 0 |  | --> | C31 ex KILBARRY | Kilbarry: T101 | Kilbarry |  | 51.9515 | -8.4328
MV/LV Substation UP***094X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.292 | 0.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41692 | 0 |  | --> | C12 ex RIVERSTOWN | Riverstown: T41∥T42 | Kilbarry |  | 51.9572 | -8.4159
MV/LV Substation UP***250 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 5.6 |  | --> | 0.095 | 0 | 0 | 0 | 0.0076 | 0 | 0 | Constrained,otherwise capacity available =95.3kW. | --> | C18 ex BANDON | Bandon: T101 | Bandon |  | 51.7882 | -8.6712
MV/LV Substation UP***266 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =159kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =206.4kW. | --> | C11 ex TEMPLEMORE | Templemore: T41 | Ikerrin |  | 52.7531 | -7.9593
MV/LV Substation UP***282X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =148kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =208.1kW. | --> | C16 ex COOLCARRON | Coolcarron: T41 | Barrymore |  | 52.1324 | -8.2726
MV/LV Substation UP***332 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.068 | 5.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0.03135 | 0.5 | 0 |  | --> | C16 ex MILLTOWN (DR) | Milltown (dr): T102 | Inchicore 110kv |  | 53.32 | -6.2642
MV/LV Substation UP***356 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 5.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =103.9kW. | --> | C18 ex BANDON | Bandon: T101 | Bandon |  | 51.7969 | -8.6799
MV/LV Substation UP***4053 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =78kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10346 | 0 |  | --> | C31 ex KILBARRY | Kilbarry: T101 | Kilbarry |  | 51.9536 | -8.4363
MV/LV Substation UP***4213 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 5.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E18 ex CRANE | Crane: T122 | Crane |  | 52.5195 | -6.2753
MV/LV Substation UP***434X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | C12 ex MOUNTRATH | Mountrath: T41∥T42 | Portlaoise |  | 53.0194 | -7.4563
MV/LV Substation UP***617X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.32 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.02945 | 0.3816 | 0 |  | --> | C11 ex MALLOW | Mallow: T41 | Mallow |  | 52.1274 | -8.6533
MV/LV Substation UP***620Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C24 ex GORESBRIDGE | Goresbridge: T41∥T42 | Kilkenny |  | 52.626 | -7.0466
MV/LV Substation UP***665 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton: T422 | Sligo |  | 54.2856 | -7.9441
MV/LV Substation UP***732X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =170kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.19474 | 0 |  | --> | C17 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.7034 | -8.0188
MV/LV Substation UP***746X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.057 | 0.1 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex OLDBAWN | Oldbawn: T42 | Cookstown |  | 53.2882 | -6.3649
MV/LV Substation UP***789 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C21 ex LITTLE BRAY | Little Bray: T41 | Fassaroe |  | 53.2103 | -6.2176
MV/LV Substation UP***859 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =92kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10128 | 0 |  | --> | C17 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.6964 | -8.0148
MV/LV Substation UP***862Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =97kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.5kW. | --> | C18 ex MOUNTRATH | Mountrath: T41∥T42 | Portlaoise |  | 53.0517 | -7.4944
MV/LV Substation UP***939 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.272 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.41396 | 0 |  | --> | C14 ex LITTLE BRAY | Little Bray: T42 | Fassaroe |  | 53.205 | -6.1197
MV/LV Substation UP***987Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =313kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.40868 | 0 |  | --> | C19 ex CLONMINCH | Clonminch: T41 | Thornsberry |  | 53.2662 | -7.4856
MV/LV Substation UR***053 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.298 | 1.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.39433 | 0 | Constrained,otherwise capacity available =416kW. | --> | C17 ex LOUGHTAGALLA | Loughtagalla: T41∥T42 | Thurles |  | 52.6803 | -7.8125
MV/LV Substation UR***138 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 250 kVA :Building Structure | 0.25 | --> | 0.25 | 0.25 | 1.7 |  | --> | 0.2375 | 0 | 0 | 0 | 0 | 0.25001 | 0 |  | --> | C14 ex RINEANNA | Rineanna: T41 | Drumline |  | 52.7441 | -8.927
MV/LV Substation UR***168Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =155kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =207.1kW. | --> | C14 ex TEMPLEMORE | Templemore: T42 | Ikerrin |  | 52.7193 | -7.5861
MV/LV Substation UR***171 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.148 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.01235 | 0.19515 | 0 |  | --> | C15 ex GLENGOOLE | Glengoole: T41 | Thurles |  | 52.7214 | -7.5764
MV/LV Substation UR***181 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.13 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2109 | 0 |  | --> | C15 ex GLENGOOLE | Glengoole: T41 | Thurles |  | 52.747 | -7.5583
MV/LV Substation UR***230X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | C18 ex BALLYBAY | Ballybay: T41∥T42 | Lisdrum |  | 54.1715 | -6.9719
MV/LV Substation UR***274 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.131 | 2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21074 | 0 |  | --> | C12 ex GRANGE (SR) | Grange (sr): T41∥T42 | Butlerstown |  | 52.246 | -7.1158
MV/LV Substation UR***4076 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C20 ex DRUMBEAR | Drumbear: T41∥T42 | Lisdrum |  | 54.1986 | -6.951
MV/LV Substation UR***4082 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown: T41 | Tonroe |  | 53.8559 | -8.7323
MV/LV Substation UR***4094 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =162kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =206kW. | --> | C14 ex TEMPLEMORE | Templemore: T42 | Ikerrin |  | 52.7229 | -7.5799
MV/LV Substation UR***422Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | E13 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.2797 | -7.0655
MV/LV Substation UR***444 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E12 ex CARNDONAGH | Carndonagh: T421∥T422 | Trillick |  | 55.334 | -7.2843
MV/LV Substation UR***581 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.34 | 13.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.40548 | 0 |  | --> | C20 ex POTTERY ROAD | Pottery Road: T102 | Carrickmines |  | 53.2618 | -6.1447
MV/LV Substation UR***604X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.297 | 2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.40814 | 0 |  | --> | C12 ex GRANGE (SR) | Grange (sr): T41∥T42 | Butlerstown |  | 52.2466 | -7.1182
MV/LV Substation UR***643Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.8kW. | --> | C20 ex DRUMBEAR | Drumbear: T41∥T42 | Lisdrum |  | 54.2024 | -6.9591
MV/LV Substation UR***645 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | C18 ex PORTARLINGTON | Portarlington: T41∥T42 | Portlaoise |  | 53.2091 | -7.2917
MV/LV Substation UR***667X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =81kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =103kW. | --> | C20 ex DRUMBEAR | Drumbear: T41∥T42 | Lisdrum |  | 54.1995 | -6.9508
MV/LV Substation UR***738 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | E19 ex CAVAN | Cavan: T421 | Shankill |  | 53.9284 | -7.404
MV/LV Substation UR***743X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.321 | 2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.40844 | 0 |  | --> | C12 ex GRANGE (SR) | Grange (sr): T41∥T42 | Butlerstown |  | 52.244 | -7.1155
MV/LV Substation UR***860Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =472kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C19 ex DOUGLAS | Douglas: T42 | Trabeg |  | 51.892 | -8.412
MV/LV Substation UR***888 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C21 ex CASTLEISLAND | Castleisland: T41∥T42 | Tralee |  | 52.2012 | -9.56
MV/LV Substation UR***915 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10438 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown: T41 | Tonroe |  | 53.8458 | -8.7359
MV/LV Substation UR***937 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.027 | 1.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05355 | 0 |  | --> | E17 ex BALLYCONNELL | Ballyconnell: T421∥T422 | Gortawee |  | 54.189 | -7.6957
MV/LV Substation US***180X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex DUNDRUM | Dundrum: T42 | Blackrock |  | 53.2922 | -6.2452
MV/LV Substation US***329Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BALLINDERRY | Ballinderry: T41 | Mullingar |  | 53.5185 | -7.34
MV/LV Substation US***388Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.378 | 8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40352 | 0 |  | --> | C23 ex CENTRE PARK ROAD | Marina: T105 | Marina |  | 51.8959 | -8.4166
MV/LV Substation US***4123 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.254 | 0.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.11685 | 0.2997 | 0 |  | --> | C14 ex SWORDS | Swords: T42 | Glasmore |  | 53.4532 | -6.262
MV/LV Substation US***559Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.44613 | 0 | Constrained,otherwise capacity available =500kW. | --> | C20 ex BALLYCOOLIN | Ballycoolin: T42 | Finglas |  | 53.4096 | -6.3495
MV/LV Substation US***620Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =372kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40446 | 0 |  | --> | C23 ex COLLEGE PARK | College Park: T101 | College Park |  | 53.42 | -6.3502
MV/LV Substation US***637X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 14.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex HEUSTON SQUARE | Heuston Square: T102 | Inchicore 110kv |  | 53.3452 | -6.2797
MV/LV Substation US***935 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.347 | 3.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4084 | 0 |  | --> | C18 ex SANDYFORD | Sandyford: T42 | Carrickmines |  | 53.2734 | -6.2115
MV/LV Substation US***993 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 14.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex HEUSTON SQUARE | Heuston Square: T102 | Inchicore 110kv |  | 53.3459 | -6.2811
MV/LV Substation UT***902X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex GARRYCASTLE | Garrycastle: T42 | Athlone |  | 53.4146 | -7.8943
MV/LV Substation V ***059 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.023 | 4.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00285 | 0.05114 | 0 |  | --> | C13 ex DUNMANWAY | Dunmanway: T43 | Dunmanway |  | 51.7271 | -9.1155
MV/LV Substation V ***166Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.195 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2008 | 0 |  | --> | C19 ex RAMPARTS | Ramparts: T41 | Dundalk |  | 54.0154 | -6.3988
MV/LV Substation V ***662X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.362 | 6.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40604 | 0 |  | --> | C17 ex CAHIR | Cahir: T41 | Cahir |  | 52.3804 | -7.9168
MV/LV Substation VA***033 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 0.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.6kW. | --> | C16 ex GARRYSPILLANE | Garryspillane: T41 | Tipperary |  | 52.3621 | -8.4693
MV/LV Substation VA***036 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.098 | 25.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.21268 | 0 |  | --> | C21 ex ARKLOW | Arklow: T101∥T102 | Arklow |  | 52.7985 | -6.1655
MV/LV Substation VA***071Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.141 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20522 | 0 |  | --> | C22 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.341 | -6.5481
MV/LV Substation VA***076Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.138 | 0.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.00665 | 0.20268 | 0 |  | --> | C14 ex SWORDS | Swords: T42 | Glasmore |  | 53.461 | -6.2412
MV/LV Substation VA***080Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.265 | 3.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.03325 | 0.38604 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge: T41 | Griffinrath |  | 53.3439 | -6.5478
MV/LV Substation VA***105X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.014 | 0 | Constrained,otherwise capacity available =267kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42072 | 0 |  | --> | C15 ex CASTLETROY | Castletroy: T41∥T42 | Ardnacrusha |  | 52.6704 | -8.554
MV/LV Substation VA***125Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.173 | 1.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20427 | 0 |  | --> | C18 ex CARRICKMACROSS | Carrickmacross: T42 | Meath Hill |  | 53.9799 | -6.7195
MV/LV Substation VA***146X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.274 | 7.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.40966 | 0 |  | --> | C11 ex GARRYCASTLE | Garrycastle: T41 | Athlone |  | 53.4178 | -7.9142
MV/LV Substation VA***149 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.331 | 2.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.03895 | 0.5 | 0 |  | --> | C13 ex WHITEHALL | Whitehall: T41 | Finglas |  | 53.3754 | -6.2574
MV/LV Substation VA***178 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.161 | 0.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20614 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 51.8856 | -10.3632
MV/LV Substation VA***212X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CENTRAL PARK | Central Park: T101 | Carrickmines |  | 53.271 | -6.2028
MV/LV Substation VA***228X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CENTRAL PARK | Central Park: T101 | Carrickmines |  | 53.2706 | -6.2035
MV/LV Substation VA***241X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CENTRAL PARK | Central Park: T101 | Carrickmines |  | 53.2706 | -6.2034
MV/LV Substation VA***243X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10769 | 0 |  | --> | C18 ex LITTLE MILLS | Little Mills: T41 | Dundalk |  | 53.9341 | -6.3859
MV/LV Substation VA***250X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C22 ex CASTLEREA | Castlerea: T41∥T42 | Carrick On Shannon |  | 53.7769 | -8.4018
MV/LV Substation VA***278 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 51.9131 | -10.294
MV/LV Substation VA***289Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.181 | 6.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20302 | 0 |  | --> | C20 ex COLLINSTOWN | Collinstown: T41∥T42 | Grange (dr) |  | 53.4243 | -6.2234
MV/LV Substation VA***305 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex MERVILLE | Merville: T42 | Finglas |  | 53.3812 | -6.3084
MV/LV Substation VA***306 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C12 ex MERVILLE | Merville: T42 | Finglas |  | 53.3812 | -6.3058
MV/LV Substation VA***4029 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.28 | 0.3 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C21 ex BREWERY ROAD | Brewery Road: T41 | Carrickmines |  | 53.2768 | -6.199
MV/LV Substation VA***4107 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex GREYSTONES | Greystones: T41 | Fassaroe |  | 53.1513 | -6.0674
MV/LV Substation VA***4133 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.178 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20349 | 0 |  | --> | C13 ex OLDCASTLE | Oldcastle: T41 | Mullingar |  | 53.7621 | -7.1634
MV/LV Substation VA***4224 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C17 ex UNIDARE | Unidare: T41 | Finglas |  | 53.4143 | -6.3187
MV/LV Substation VA***4225 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C17 ex UNIDARE | Unidare: T41 | Finglas |  | 53.4152 | -6.3191
MV/LV Substation VA***4228 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C17 ex UNIDARE | Unidare: T41 | Finglas |  | 53.4168 | -6.32
MV/LV Substation VA***4235 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 8.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9944 | -6.0691
MV/LV Substation VA***4238 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =59kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex TUAM SOUTH | Tuam South: T42 | Cloon |  | 53.522 | -8.8446
MV/LV Substation VA***423Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =79kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1033 | 0 |  | --> | C12 ex LEIXLIP | Leixlip: T42 | Griffinrath |  | 53.3667 | -6.4807
MV/LV Substation VA***467Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.449 | 8.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 53.0123 | -6.1077
MV/LV Substation VA***533 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10454 | 0 |  | --> | E18 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 51.9289 | -10.3465
MV/LV Substation VA***553X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 25.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | C22 ex ARKLOW | Arklow: T101∥T102 | Arklow |  | 52.8054 | -6.1745
MV/LV Substation VA***560Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | C11 ex RATHDRUM | Rathdrum: T42 | Arklow |  | 52.8775 | -6.224
MV/LV Substation VA***593X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 2.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.8kW. | --> | C15 ex KILRUSH | Kilrush: T41∥T42 | Tullabrack |  | 52.6367 | -9.4734
MV/LV Substation VA***628 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 5.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053697 | 0 |  | --> | E17 ex BLESSINGTON | Blessington: T421 | Kilteel |  | 53.1058 | -6.5254
MV/LV Substation VA***730 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.264 | 0.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.02755 | 0.39218 | 0 |  | --> | C20 ex KILMARTIN | Kilmartin: T41 | Arklow |  | 53.0675 | -6.2261
MV/LV Substation VA***762 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052345 | 0 |  | --> | E17 ex ACHILL | Achill: T422 | Carrowbeg |  | 54.0131 | -9.9708
MV/LV Substation VA***772 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 5.6 |  | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0.095745 | 0 |  | --> | E17 ex BLESSINGTON | Blessington: T421 | Kilteel |  | 53.1075 | -6.526
MV/LV Substation VA***787X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =358kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40666 | 0 |  | --> | C15 ex CLONAKILTY | Clonakilty: T41∥T42 | Dunmanway |  | 51.6171 | -8.8949
MV/LV Substation VA***790X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 4.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10174 | 0 |  | --> | E15 ex JENKINSTOWN | Jenkinstown: T421∥T422 | Dundalk |  | 54.0512 | -6.346
MV/LV Substation VA***823X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =397kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400.5kW. | --> | C22 ex TEMPLEMORE | Templemore: T42 | Ikerrin |  | 52.7954 | -7.8293
MV/LV Substation VA***863X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E15 ex RATHMORE | Rathmore: T421 | Knockearagh |  | 52.118 | -9.2198
MV/LV Substation VA***870X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | C20 ex KNOCKAPHUNTA | Knockaphunta: T41∥T42 | Castlebar |  | 53.8151 | -9.1972
MV/LV Substation VA***871 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.7 |  | --> | 0.095 | 0 | 0 | 0 | 0.05985 | 0.037005 | 0 |  | --> | C15 ex KILMARTIN | Kilmartin: T41 | Arklow |  | 53.05 | -6.1866
MV/LV Substation VA***876X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | E17 ex WINDSOR | Windsor: T421∥T422 | Castlebar |  | 53.8198 | -9.1691
MV/LV Substation VA***937X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C17 ex ATHBOY | Athboy: T42 | Navan |  | 53.7119 | -7.0206
MV/LV Substation VE***023 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =92kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.20756 | 0 |  | --> | C12 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8557 | -8.2796
MV/LV Substation VE***032 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.305 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.01995 | 0.39392 | 0 |  | --> | C20 ex HOWTH JUNCTION | Howth Junction: T42 | Grange (dr) |  | 53.389 | -6.1464
MV/LV Substation VE***035 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =122kVA. | --> | 0.19 | 0 | 0 | 0 | 0.06555 | 0.1431 | 0 |  | --> | C22 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8448 | -8.3156
MV/LV Substation VE***043 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.366 | 3.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0228 | 0.5 | 0 |  | --> | C20 ex BOGHALL ROAD | Boghall Road: T42 | Fassaroe |  | 53.1915 | -6.1045
MV/LV Substation VE***050 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.047 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0.0247 | 0.082135 | 0 |  | --> | E15 ex DINGLE | Dingle: T421 | Oughtragh |  | 52.1327 | -10.3576
MV/LV Substation VE***055 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 8.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9876 | -6.0471
MV/LV Substation VE***089 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | E15 ex DINGLE | Dingle: T421 | Oughtragh |  | 52.1345 | -10.3647
MV/LV Substation VE***108Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 9.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C18 ex TRABEG | Trabeg: T101 | Trabeg |  | 51.8721 | -8.4574
MV/LV Substation VE***117 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.267 | 3.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.40572 | 0 |  | --> | C14 ex MCDONAGH | Mcdonagh: T42 | Kilkenny |  | 52.6556 | -7.2332
MV/LV Substation VE***125 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =283kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0 | 0 | Constrained,otherwise capacity available =415.3kW. | --> | C11 ex BELLFIELD | Bellfield: T41∥T42 | Crane |  | 52.5094 | -6.5854
MV/LV Substation VE***164Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.05 | 0.1 | Constrained,otherwise capacity available =490kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.44613 | 0 | Constrained,otherwise capacity available =500kW. | --> | C12 ex COOLMINE | Coolmine: T42 | Finglas |  | 53.3889 | -6.3943
MV/LV Substation VE***186X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.28 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.03325 | 0.38376 | 0 |  | --> | C14 ex HOWTH JUNCTION | Howth Junction: T42 | Grange (dr) |  | 53.3913 | -6.1475
MV/LV Substation VE***223 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =300kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0 | 0 | Constrained,otherwise capacity available =412.7kW. | --> | E12 ex BUNCLODY | Bunclody: T421∥T422 | Crane |  | 52.6531 | -6.6515
MV/LV Substation VE***376X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =131kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0399 | 0.5 | 0 |  | --> | C12 ex CLONTARF | Clontarf: T42 | Finglas |  | 53.3588 | -6.1964
MV/LV Substation VE***4130 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex LEESON STREET | Leeson Street: T41 | Milltown (dr) |  | 53.3329 | -6.2458
MV/LV Substation VE***4297 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E12 ex KILCOCK | Kilcock: T422 | Griffinrath |  | 53.4454 | -6.5332
MV/LV Substation VE***434X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E14 ex CHARLEVILLE | Charleville: T422 | Charleville |  | 52.3786 | -8.679
MV/LV Substation VE***4428 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3.1 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex BEDFORD ROW | Bedford Row: T43 | Francis Street |  | 53.3463 | -6.2569
MV/LV Substation VE***4436 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex CLONTARF | Clontarf: T42 | Finglas |  | 53.3697 | -6.1996
MV/LV Substation VE***4441 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex CLONTARF | Clontarf: T42 | Finglas |  | 53.3751 | -6.199
MV/LV Substation VE***445 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 0.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101kW. | --> | C18 ex DUNGLOE | Dungloe: T42 | Ardnagappary |  | 54.9855 | -8.4942
MV/LV Substation VE***4511 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 6.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | E12 ex RATHKEALE | Rathkeale: T421∥T422 | Rathkeale |  | 52.4822 | -8.8693
MV/LV Substation VE***464 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.044795 | 0 |  | --> | E11 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.6255 | -6.55
MV/LV Substation VE***504 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =326kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.40266 | 0 |  | --> | C12 ex LUCAN EAST | Lucan East: T41∥T42 | Grange Castle |  | 53.3513 | -6.4486
MV/LV Substation VE***523 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.416 | 3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex MERRION SQUARE | Merrion Square: T42 | Ringsend |  | 53.3382 | -6.2432
MV/LV Substation VE***549 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.444 | 3.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex CABRA | Cabra: T101 | Finglas |  | 53.3716 | -6.3053
MV/LV Substation VE***625 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =306kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0209 | 0.39276 | 0 |  | --> | C12 ex CLONTARF | Clontarf: T42 | Finglas |  | 53.3682 | -6.195
MV/LV Substation VE***657 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =26kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053697 | 0 |  | --> | C18 ex BUTTEVANT | Buttevant: T41∥T42 | Mallow |  | 52.2623 | -8.6615
MV/LV Substation VE***766 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.04642 | 0 |  | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham: T41∥T42 | Letterkenny |  | 54.9757 | -7.5743
MV/LV Substation VE***808X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =288kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.40652 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown: T102 | Inchicore 110kv |  | 53.279 | -6.424
MV/LV Substation VE***815X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =291kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0.40406 | 0 |  | --> | C20 ex FORTUNESTOWN | Fortunestown: T102 | Inchicore 110kv |  | 53.2806 | -6.4242
MV/LV Substation VE***816 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | E15 ex DINGLE | Dingle: T421 | Oughtragh |  | 52.1259 | -10.3825
MV/LV Substation VE***876X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C24 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.5532 | -9.9501
MV/LV Substation VE***910 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =153kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20738 | 0 |  | --> | C11 ex CLONTARF | Clontarf: T42 | Finglas |  | 53.3777 | -6.1998
MV/LV Substation VE***910Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex TOGHER | Togher: T41 | Trabeg |  | 51.8703 | -8.4824
MV/LV Substation VE***915X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05142 | 0 |  | --> | E17 ex RATHMORE | Rathmore: T421 | Knockearagh |  | 52.0568 | -9.0591
MV/LV Substation VE***947 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.311 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0399 | 0.372 | 0 |  | --> | C19 ex BRAY | Bray: T41 | Fassaroe |  | 53.1982 | -6.1072
MV/LV Substation VE***985 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05142 | 0 |  | --> | E17 ex DULEEK | Duleek: T421∥T422 | Drybridge |  | 53.6314 | -6.5484
MV/LV Substation VH***012X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.038 | 0.5 | 0 |  | --> | C27 ex WOLFE TONE STREET | Wolfe Tone Street: T101 | Finglas |  | 53.3486 | -6.2556
MV/LV Substation VH***029 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.377 | 5.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.38366 | 0 |  | --> | C18 ex PURCELLS INCH | Purcells Inch: T42 | Kilkenny |  | 52.646 | -7.2146
MV/LV Substation VH***488 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.8kW. | --> | E12 ex CARNDONAGH | Carndonagh: T421∥T422 | Trillick |  | 55.3546 | -7.2749
MV/LV Substation VI***003 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.149 | 2.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0247 | 0 | 0 | Constrained,otherwise capacity available =412.2kW. | --> | E15 ex BALLYMACARRY | Ballymacarry: T421 | Trillick |  | 55.1297 | -7.4578
MV/LV Substation VI***015 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.349 | 1.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0 | 0 | Constrained,otherwise capacity available =405.1kW. | --> | C25 ex KILKEE | Kilkee: T41 | Tullabrack |  | 52.6769 | -9.6528
MV/LV Substation VI***016 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.01615 | 0.5 | 0 |  | --> | C17 ex TOGHER | Togher: T41 | Trabeg |  | 51.8774 | -8.4765
MV/LV Substation VI***017Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.4kW. | --> | C15 ex KILCLOHER | Kilcloher: T42 | Dungarvan |  | 52.0853 | -7.8571
MV/LV Substation VI***023 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.071 | 1.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21962 | 0 |  | --> | C18 ex KINGSCOURT | Kingscourt: T42 | Meath Hill |  | 53.9051 | -6.8034
MV/LV Substation VI***032X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.272 | 14.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41996 | 0 |  | --> | C26 ex HEUSTON SQUARE | Heuston Square: T102 | Inchicore 110kv |  | 53.3461 | -6.2832
MV/LV Substation VI***035 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.066 | 2.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.22034 | 0 |  | --> | C11 ex HEADFORD ROAD | Headford Road: T41 | Galway 110kv |  | 53.2724 | -9.0494
MV/LV Substation VI***036 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.117 | 2.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21285 | 0 |  | --> | C17 ex VIRGINIA | Virginia: T41∥T42 | Meath Hill |  | 53.8357 | -7.0816
MV/LV Substation VI***041X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.122 | 4.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.01615 | 0.1951 | 0 |  | --> | C16 ex WHITESTOWN | Whitestown: T42 | Cookstown |  | 53.2881 | -6.3798
MV/LV Substation VI***047 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.3 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =415.7kW. | --> | C19 ex TURLOUGH ROAD | Turlough Road: T43 | Castlebar |  | 53.8608 | -9.3052
MV/LV Substation VI***089 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.054 | 1.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.02375 | 0.19705 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North: T41∥T42 | Ennis |  | 52.8501 | -8.9975
MV/LV Substation VI***090 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.244 | 3.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.4212 | 0 |  | --> | C20 ex CENTRE PARK ROAD | Marina: T106 | Marina |  | 51.8917 | -8.4541
MV/LV Substation VI***092X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C44 ex BEDFORD ROW | Bedford Row: T41 | Francis Street |  | 53.3449 | -6.2693
MV/LV Substation VI***102X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 6.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex LIBERTY STREET | Liberty Street: T101 | Liberty Street |  | 51.8979 | -8.4727
MV/LV Substation VI***119Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.056 | 2.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1068 | 0 |  | --> | C17 ex VIRGINIA | Virginia: T41∥T42 | Meath Hill |  | 53.8306 | -7.0816
MV/LV Substation VI***119Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.456 | 8 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00855 | 0.5 | 0 |  | --> | C25 ex CENTRE PARK ROAD | Marina: T105 | Marina |  | 51.8978 | -8.4597
MV/LV Substation VI***144 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.077 | 2.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10361 | 0 |  | --> | C17 ex VIRGINIA | Virginia: T41∥T42 | Meath Hill |  | 53.8385 | -7.0902
MV/LV Substation VI***146 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =374kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40414 | 0 |  | --> | C18 ex NAAS | Naas: T42 | Newbridge |  | 53.1697 | -6.7026
MV/LV Substation VI***146X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =351kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40776 | 0 |  | --> | C12 ex CAHERDAVIN | Caherdavin: T42 | Ardnacrusha |  | 52.6605 | -8.6569
MV/LV Substation VI***164Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =251kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02185 | 0.40016 | 0 |  | --> | C20 ex TOGHER | Togher: T42 | Trabeg |  | 51.8798 | -8.4868
MV/LV Substation VI***174X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.31 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.03325 | 0.37914 | 0 |  | --> | C19 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3253 | -6.4958
MV/LV Substation VI***175X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.356 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.03705 | 0.36798 | 0 |  | --> | C19 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3251 | -6.4954
MV/LV Substation VI***179Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.44613 | 0 | Constrained,otherwise capacity available =500kW. | --> | C17 ex BALLYCOOLIN | Ballycoolin: T41 | Finglas |  | 53.3989 | -6.343
MV/LV Substation VI***186X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.381 | 4.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0.01615 | 0.5 | 0 |  | --> | C14 ex RAMPARTS | Ramparts: T42 | Dundalk |  | 53.9992 | -6.4076
MV/LV Substation VI***189Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.199 | 4.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20016 | 0 |  | --> | C18 ex GLEBE | Glebe: T41∥T42 | Richmond |  | 53.7214 | -7.7696
MV/LV Substation VI***196Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.18 | 3.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =203.2kW. | --> | E18 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 52.0069 | -7.8176
MV/LV Substation VI***198 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 8.3 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10392 | 0 |  | --> | C25 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9869 | -6.0451
MV/LV Substation VI***213X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.409 | 0.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CAMDEN ROW | Camden Row: T41 | Francis Street |  | 53.3422 | -6.2779
MV/LV Substation VI***215 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.403 | 2.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0247 | 0.5 | 0 |  | --> | C11 ex DODDER ROAD | Dodder Road: T42 | Milltown (dr) |  | 53.3084 | -6.2749
MV/LV Substation VI***224X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex LOUGHLINSTOWN | Loughlinstown: T41 | Carrickmines |  | 53.2413 | -6.1409
MV/LV Substation VI***231Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8643 | -8.5269
MV/LV Substation VI***252 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =397kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40048 | 0 |  | --> | C18 ex WOODFORD | Woodford: T41∥T42 | Knockearagh |  | 52.0438 | -9.4998
MV/LV Substation VI***252Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.149 | 2.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.208 | 0 |  | --> | C17 ex VIRGINIA | Virginia: T41∥T42 | Meath Hill |  | 53.8377 | -7.0872
MV/LV Substation VI***254 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.361 | 3.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0532 | 0.5 | 0 |  | --> | C11 ex CABRA | Cabra: T101 | Finglas |  | 53.3656 | -6.3144
MV/LV Substation VI***270X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.451 | 1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0418 | 0.5 | 0 |  | --> | C17 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5521 | -6.7657
MV/LV Substation VI***273Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.353 | 4.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =407.5kW. | --> | E19 ex TELAYDON | Telaydon: T421 | Lisdrum |  | 54.3157 | -6.8958
MV/LV Substation VI***292 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.16 | 4.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.2023 | 0 |  | --> | C15 ex BALLINCLEA | Ballinclea: T41 | Cherrywood |  | 53.2706 | -6.0966
MV/LV Substation VI***296 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =339kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40964 | 0 |  | --> | C12 ex MERVILLE | Merville: T42 | Finglas |  | 53.3829 | -6.3144
MV/LV Substation VI***316 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =211kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02565 | 0.40214 | 0 |  | --> | C14 ex MERVILLE | Merville: T42 | Finglas |  | 53.3771 | -6.2855
MV/LV Substation VI***321 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex NAAS | Naas: T42 | Newbridge |  | 53.2103 | -6.6641
MV/LV Substation VI***326 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =393kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex MARROWBONE LANE | Marrowbone Lane: T42 | Inchicore 110kv |  | 53.3384 | -6.3185
MV/LV Substation VI***333Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.149 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.198 | 0 |  | --> | E18 ex JENKINSTOWN | Jenkinstown: T421∥T422 | Dundalk |  | 54.0866 | -6.2546
MV/LV Substation VI***337Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =173kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20427 | 0 |  | --> | C21 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4691 | -6.5349
MV/LV Substation VI***339 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.15 | 3.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0 | 0 | Constrained,otherwise capacity available =198.8kW. | --> | C16 ex TURLOUGH ROAD | Turlough Road: T41∥T42 | Castlebar |  | 53.8604 | -9.3152
MV/LV Substation VI***366X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E21 ex STRANORLAR | Stranorlar: T421 | Letterkenny |  | 54.8007 | -7.7812
MV/LV Substation VI***377Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.059 | 2.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.22134 | 0 |  | --> | C17 ex TULLYNAMALRA | Tullynamalra: T41∥T42 | Meath Hill |  | 54.0586 | -6.8148
MV/LV Substation VI***379 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C15 ex KILCLOHER | Kilcloher: T42 | Dungarvan |  | 52.0935 | -7.857
MV/LV Substation VI***4008 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.01995 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | E11 ex MACROOM | Macroom: T422 | Macroom |  | 51.9111 | -8.7896
MV/LV Substation VI***4032 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E18 ex BALTRASNA | Baltrasna: T122 | Baltrasna |  | 53.5052 | -6.4591
MV/LV Substation VI***4032 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex VIRGINIA | Virginia: T41∥T42 | Meath Hill |  | 53.8381 | -7.0884
MV/LV Substation VI***4090 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.162 | 5.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.43634 | 0 |  | --> | C22 ex CLOON | Cloon: T42 | Cloon |  | 53.514 | -8.8517
MV/LV Substation VI***4127 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.17 | 8.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =204.7kW. | --> | E12 ex BELLACORICK | Bellacorick: T122 | Bellacorick |  | 54.1252 | -9.5582
MV/LV Substation VI***4135 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =340kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40948 | 0 |  | --> | C12 ex MERVILLE | Merville: T42 | Finglas |  | 53.3819 | -6.3113
MV/LV Substation VI***4153 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.177 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | C11 ex LLOYD | Lloyd: T41∥T42 | Navan |  | 53.7394 | -6.9039
MV/LV Substation VI***4187 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =383kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40272 | 0 |  | --> | E15 ex WHITECHURCH | Whitechurch: T421 | Kilbarry |  | 51.9813 | -8.5131
MV/LV Substation VI***4214 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.359 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4065 | 0 |  | --> | C15 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3304 | -6.486
MV/LV Substation VI***4257 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.263 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42134 | 0 |  | --> | C16 ex VIRGINIA | Virginia: T41∥T42 | Meath Hill |  | 53.8012 | -7.0345
MV/LV Substation VI***4316 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0627 | 0.5 | 0 |  | --> | C15 ex MAYFIELD | Mayfield: T41 | Kilbarry |  | 51.912 | -8.4035
MV/LV Substation VI***434 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.05 | 0.1 | Constrained,otherwise capacity available =133kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.20744 | 0 |  | --> | C14 ex COOLMINE | Coolmine: T42 | Finglas |  | 53.3812 | -6.4102
MV/LV Substation VI***4435 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C16 ex ATHLONE | Athlone: T42 | Athlone |  | 53.4283 | -7.9496
MV/LV Substation VI***470Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.173 | 8.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20427 | 0 |  | --> | E18 ex BALTRASNA | Baltrasna: T122 | Baltrasna |  | 53.5054 | -6.4572
MV/LV Substation VI***471 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.282 | 3.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41844 | 0 |  | --> | C24 ex CENTRE PARK ROAD | Marina: T106 | Marina |  | 51.8929 | -8.4655
MV/LV Substation VI***488Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 8.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E18 ex BALTRASNA | Baltrasna: T122 | Baltrasna |  | 53.5052 | -6.4579
MV/LV Substation VI***497 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.018 | 4.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =54.9kW. | --> | E13 ex MOVILLE | Moville: T421∥T422 | Trillick |  | 55.2812 | -7.2299
MV/LV Substation VI***520Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =361kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4062 | 0 |  | --> | C16 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6571 | -7.255
MV/LV Substation VI***524Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.172 | 7.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0.20243 | 0 |  | --> | E41 ex KINSALE | Kinsale: T423 | Bandon |  | 51.6979 | -8.5201
MV/LV Substation VI***531 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 4.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05219 | 0 |  | --> | C14 ex BALLYJAMESDUFF | Ballyjamesduff: T42 | Shankill |  | 53.8399 | -7.0939
MV/LV Substation VI***547Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =470kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex DENNEHYS CROSS | Dennehys Cross: T41 | Trabeg |  | 51.892 | -8.5071
MV/LV Substation VI***554Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.123 | 0.1 | Constrained,otherwise capacity available =237kVA. | --> | 0.38 | 0 | 0 | 0 | 0.05985 | 0 | 0 | Constrained,otherwise capacity available =362.3kW. | --> | C16 ex RATHDRUM | Rathdrum: T42 | Arklow |  | 52.9329 | -6.2495
MV/LV Substation VI***568X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =202kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.43048 | 0 |  | --> | C12 ex LUCAN EAST | Lucan East: T41∥T42 | Grange Castle |  | 53.3562 | -6.4495
MV/LV Substation VI***588 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.127 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21135 | 0 |  | --> | C19 ex GLENGOOLE | Glengoole: T41 | Thurles |  | 52.5868 | -7.5405
MV/LV Substation VI***589Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | C20 ex ROSCOMMON | Roscommon: T42 | Lanesboro |  | 53.7794 | -8.2528
MV/LV Substation VI***590 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 3.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52kW. | --> | C13 ex DERRYBEG | Derrybeg: T41∥T42 | Ardnagappary |  | 55.0136 | -8.3994
MV/LV Substation VI***593Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.177 | 1.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | C14 ex ROSEHILL | Rosehill: T42 | Kilkenny |  | 52.6466 | -7.2496
MV/LV Substation VI***595Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.399 | 7.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40016 | 0 |  | --> | C22 ex KILLOTERAN | Killoteran: T102 | Killoteran |  | 52.2422 | -7.165
MV/LV Substation VI***625X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex WATLING STREET | Watling Street: T41 | Francis Street |  | 53.3497 | -6.282
MV/LV Substation VI***643Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =450kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex DENNEHYS CROSS | Dennehys Cross: T42 | Trabeg |  | 51.8928 | -8.5027
MV/LV Substation VI***706Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =324kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.39598 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.7031 | -6.2565
MV/LV Substation VI***708X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =288kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.41352 | 0 |  | --> | C21 ex BELGARD | Belgard: T41 | Cookstown |  | 53.2865 | -6.363
MV/LV Substation VI***716Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | E64 ex ATHY | Athy: T102 | Athy |  | 53.0633 | -7.0861
MV/LV Substation VI***726X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.038 | 0.5 | 0 |  | --> | E18 ex NEWPORT | Newport: T421 | Carrowbeg |  | 53.8856 | -9.5447
MV/LV Substation VI***771X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown: T101 | Inchicore 110kv |  | 53.2899 | -6.4242
MV/LV Substation VI***781 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.149 | 4.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.208 | 0 |  | --> | C15 ex BALLINCLEA | Ballinclea: T41 | Cherrywood |  | 53.272 | -6.0969
MV/LV Substation VI***795 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E15 ex CLONROCHE | Clonroche: T421∥T422 | Wexford |  | 52.4629 | -6.837
MV/LV Substation VI***796 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.042345 | 0 |  | --> | C26 ex DUNDALK | Dundalk: T41 | Dundalk |  | 54.0029 | -6.58
MV/LV Substation VI***800 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.132 | 4.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21059 | 0 |  | --> | C15 ex BALLINCLEA | Ballinclea: T41 | Cherrywood |  | 53.2753 | -6.1062
MV/LV Substation VI***809Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex DENNEHYS CROSS | Dennehys Cross: T42 | Trabeg |  | 51.8926 | -8.5043
MV/LV Substation VI***810Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex DENNEHYS CROSS | Dennehys Cross: T42 | Trabeg |  | 51.8925 | -8.5052
MV/LV Substation VI***828 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0152 | 0 | 0 | Constrained,otherwise capacity available =35.9kW. | --> | C15 ex KILCLOHER | Kilcloher: T42 | Dungarvan |  | 52.0872 | -7.8491
MV/LV Substation VI***833 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.37 | 5.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40478 | 0 |  | --> | E18 ex BALLYBUNION | Ballybunion: T421∥T422 | Trien |  | 52.5072 | -9.6758
MV/LV Substation VI***869X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.061 | 3.6 |  | --> | 0.095 | 0 | 0 | 0 | 0.00285 | 0.10305 | 0 |  | --> | E64 ex ATHY | Athy: T102 | Athy |  | 53.0518 | -7.0855
MV/LV Substation VI***876Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E13 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9095 | -6.8481
MV/LV Substation VI***888X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 3.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10032 | 0 |  | --> | E64 ex ATHY | Athy: T102 | Athy |  | 53.0668 | -7.069
MV/LV Substation VI***890X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0.01045 | 0.041345 | 0 |  | --> | E64 ex ATHY | Athy: T102 | Athy |  | 53.0586 | -7.0891
MV/LV Substation VI***909Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.295 | 2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.40246 | 0 |  | --> | C17 ex GRANGE (SR) | Grange (sr): T41∥T42 | Butlerstown |  | 52.2459 | -7.0783
MV/LV Substation VI***910Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.334 | 2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.39442 | 0 |  | --> | C17 ex GRANGE (SR) | Grange (sr): T41∥T42 | Butlerstown |  | 52.2448 | -7.0734
MV/LV Substation VI***969Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =361kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.3962 | 0 |  | --> | E18 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.513 | -7.1399
MV/LV Substation VI***970Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | E18 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.5141 | -7.1398
MV/LV Substation VI***972 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.178 | 7.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20349 | 0 |  | --> | C13 ex KILLYBEGS | Killybegs: T41 | Binbane |  | 54.6328 | -8.3585
MV/LV Substation VI***975 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =150kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0285 | 0.17784 | 0 |  | --> | C12 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8559 | -8.2751
MV/LV Substation VI***994Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.058 | 1.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1065 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8592 | -8.5261
MV/LV Substation VI***995 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex WATLING STREET | Watling Street: T42 | Francis Street |  | 53.3462 | -6.2836
MV/LV Substation VO***008 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =161kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20614 | 0 |  | --> | C18 ex HOLYCROSS ROAD | Holycross Road: T41∥T42 | Thurles |  | 52.6843 | -7.8263
MV/LV Substation VO***012 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.272 | 1.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0 | 0 | Constrained,otherwise capacity available =412kW. | --> | E16 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1353 | -7.458
MV/LV Substation VO***034X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =69kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0.09884 | 0 |  | --> | C21 ex MILFORD (NR) | Milford (nr): T41∥T42 | Letterkenny |  | 55.0932 | -7.7037
MV/LV Substation VO***054 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex GLEBE | Glebe: T41∥T42 | Richmond |  | 53.7318 | -7.7859
MV/LV Substation VO***057 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.127 | 5.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21135 | 0 |  | --> | C14 ex ARDNAREE | Ardnaree: T42 | Moy |  | 54.1133 | -9.1481
MV/LV Substation VO***058Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.062 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.1009 | 0 |  | --> | C12 ex BALLYHALE | Ballyhale: T42 | Kilkenny |  | 52.4788 | -7.2118
MV/LV Substation VO***066 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.496 | 3.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00285 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C13 ex TURLOUGH ROAD | Turlough Road: T41∥T42 | Castlebar |  | 53.8575 | -9.2892
MV/LV Substation VO***071 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.363 | 1.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40588 | 0 |  | --> | E17 ex GARRANACANTY | Garranacanty: T421 | Tipperary |  | 52.478 | -8.1565
MV/LV Substation VO***077 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.163 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.0228 | 0.18183 | 0 |  | --> | C16 ex CARRAROE | Carraroe: T42 | Screeb |  | 53.1256 | -9.672
MV/LV Substation VO***092 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 6.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C40 ex INCHICORE CENTRAL | Inchicore Central: T43 | Inchicore 110kv |  | 53.3254 | -6.3433
MV/LV Substation VO***104 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 7.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.8kW. | --> | E12 ex ARIGNA | Arigna: T121 | Arigna |  | 54.1699 | -8.1366
MV/LV Substation VO***124 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E11 ex BALLYHALE | Ballyhale: T421 | Kilkenny |  | 52.5289 | -7.1434
MV/LV Substation VO***141 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.047 | 2 |  | --> | 0.095 | 0 | 0 | 0 | 0.0152 | 0.092135 | 0 |  | --> | C12 ex CAPPAMORE | Cappamore: T41∥T42 | Ardnacrusha |  | 52.6128 | -8.3482
MV/LV Substation VO***148X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052495 | 0 |  | --> | C16 ex DUNLEER | Dunleer: T41∥T42 | Drybridge |  | 53.8304 | -6.3915
MV/LV Substation VO***160 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.167 | 1.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20521 | 0 |  | --> | C11 ex BALLYTIVNAN | Ballytivnan: T41 | Sligo |  | 54.2788 | -8.4582
MV/LV Substation VO***160 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.1009 | 0.1 | Constrained,otherwise capacity available =372kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40446 | 0 |  | --> | C16 ex COOLCORCORAN | Coolcorcoran: T41∥T42 | Knockearagh |  | 52.0626 | -9.5192
MV/LV Substation VO***190 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =370kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40478 | 0 |  | --> | C19 ex SEMPERIT | Semperit: T41 | Grange Castle |  | 53.3452 | -6.3522
MV/LV Substation VO***194 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 2.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101.1kW. | --> | C15 ex KILTIMAGH | Kiltimagh: T41 | Castlebar |  | 53.8437 | -9.0059
MV/LV Substation VO***198 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =85kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10237 | 0 |  | --> | C15 ex SAGGART | Saggart: T41∥T42 | Grange Castle |  | 53.2686 | -6.3936
MV/LV Substation VO***320Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.178 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20349 | 0 |  | --> | C25 ex TRAMORE | Tramore: T41 | Butlerstown |  | 52.1637 | -7.1596
MV/LV Substation VO***341X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.195 | 3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.1948 | 0 |  | --> | C11 ex CROSSMOLINA | Crossmolina: T41∥T42 | Moy |  | 54.0972 | -9.317
MV/LV Substation VO***345X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.365 | 3.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40556 | 0 |  | --> | E19 ex STRANORLAR | Stranorlar: T421 | Letterkenny |  | 54.807 | -7.7737
MV/LV Substation VO***4052 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.18 | 2.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20318 | 0 |  | --> | C17 ex CARRIGLAWN | Carriglawn: T41∥T42 | Wexford |  | 52.3429 | -6.4853
MV/LV Substation VO***4094 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52kW. | --> | E11 ex MACROOM | Macroom: T422 | Macroom |  | 51.9114 | -8.7752
MV/LV Substation VO***492Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E13 ex AGHADA | Aghada: T721 | N/A |  | 51.8201 | -8.2386
MV/LV Substation VO***515Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =23kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05414 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin: T41 | Inchicore 110kv |  | 53.2977 | -6.4137
MV/LV Substation VO***521X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.244 | 8.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.4192 | 0 |  | --> | C14 ex GORTLEE | Gortlee: T41∥T42 | Letterkenny |  | 54.9633 | -7.7319
MV/LV Substation VO***531X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.191 | 1.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20144 | 0 |  | --> | E11 ex KILCULLEN | Kilcullen: T424 | Stratford |  | 53.0537 | -6.6976
MV/LV Substation VO***532X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =24kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053992 | 0 |  | --> | C15 ex DELVIN | Delvin: T42 | Mullingar |  | 53.5173 | -7.1396
MV/LV Substation VO***631X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | E16 ex WINDSOR | Windsor: T421∥T422 | Castlebar |  | 53.8508 | -9.2811
MV/LV Substation VO***654Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 1.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10253 | 0 |  | --> | E15 ex BALLYCONNELL | Ballyconnell: T421∥T422 | Gortawee |  | 54.0991 | -7.4743
MV/LV Substation VO***736 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.394 | 9.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40096 | 0 |  | --> | C18 ex KILLYBEGS | Killybegs: T42 | Binbane |  | 54.6395 | -8.4368
MV/LV Substation VO***750Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0531 | 0 |  | --> | C11 ex SRAH | Srah: T41∥T42 | Thornsberry |  | 53.2715 | -7.5022
MV/LV Substation VO***792X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.1 | 1.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21538 | 0 |  | --> | C12 ex ROSCOMMON | Roscommon: T42 | Lanesboro |  | 53.6246 | -8.1996
MV/LV Substation VO***818 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =140kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =209.4kW. | --> | C13 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.648 | -8.1136
MV/LV Substation VO***824Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C11 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1405 | -7.0574
MV/LV Substation VO***826 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.178 | 1.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20349 | 0 |  | --> | E17 ex BALLYCONNELL | Ballyconnell: T421∥T422 | Gortawee |  | 54.1234 | -7.6766
MV/LV Substation VO***860 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.178 | 2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.19749 | 0 |  | --> | C17 ex KILCAR | Kilcar: T41 | Binbane |  | 54.6561 | -8.6326
MV/LV Substation VO***863Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.1kW. | --> | E12 ex EMYVALE | Emyvale: T422 | Lisdrum |  | 54.3339 | -7.0935
MV/LV Substation VO***866Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C19 ex CALLAN | Callan: T41∥T42 | Kilkenny |  | 52.5489 | -7.3927
MV/LV Substation VO***897X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =88kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0171 | 0.0839 | 0 |  | --> | C12 ex BRUFF | Bruff: T42 | Limerick |  | 52.5219 | -8.3977
MV/LV Substation VO***906Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =34kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.5kW. | --> | E13 ex ABBEYLEIX | Abbeyleix: T422 | Portlaoise |  | 52.9091 | -7.3244
MV/LV Substation VO***936Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.152 | 2.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20754 | 0 |  | --> | C17 ex VIRGINIA | Virginia: T41∥T42 | Meath Hill |  | 53.8319 | -7.0832
MV/LV Substation VO***939 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0528 | 0 |  | --> | C19 ex KINGSCOURT | Kingscourt: T41 | Meath Hill |  | 53.7982 | -6.7319
MV/LV Substation W ***102 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E11 ex CARRIGALLEN | Carrigallen: T421 | Carrick On Shannon |  | 54.0891 | -7.7813
MV/LV Substation W ***437X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.174 | 11.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.19312 | 0 |  | --> | C34 ex SALTHILL | Salthill: T102 | Salthill |  | 53.278 | -9.0736
MV/LV Substation W ***479Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E15 ex TULLOW | Tullow: T421 | Carlow |  | 52.8021 | -6.7505
MV/LV Substation W ***754X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C13 ex FERMOY NORTH | Fermoy North: T41∥T42 | Barrymore |  | 52.1402 | -8.2607
MV/LV Substation W ***822Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1772 | -6.7979
MV/LV Substation W ***824Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1771 | -6.7979
MV/LV Substation W ***970Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1775 | -6.7964
MV/LV Substation W.***4115 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 5.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E13 ex BLESSINGTON | Blessington: T421 | Kilteel |  | 53.139 | -6.6266
MV/LV Substation W/***489 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 1.9 |  | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0.091745 | 0 |  | --> | C17 ex BALLYTIVNAN | Ballytivnan: T41 | Sligo |  | 54.3026 | -8.5199
MV/LV Substation W/***826 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | E17 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1228 | -7.2039
MV/LV Substation W/***921 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | E12 ex BIRR | Birr: T422 | Dallow |  | 53.1025 | -7.802
MV/LV Substation W+***4181 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C11 ex BRAY | Bray: T41 | Fassaroe |  | 53.1985 | -6.1369
MV/LV Substation W+***663X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1733 | -6.7981
MV/LV Substation WA***002 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.088 | 2.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21715 | 0 |  | --> | C17 ex SPA ROAD | Spa Road: T41∥T42 | Doon |  | 52.3537 | -7.6943
MV/LV Substation WA***005 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.056 | 3.8 |  | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =96.8kW. | --> | C16 ex TURLOUGH ROAD | Turlough Road: T41∥T42 | Castlebar |  | 53.8643 | -9.3003
MV/LV Substation WA***007 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 4.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1033 | 0 |  | --> | E15 ex MOHILL | Mohill: T421∥T422 | Carrick On Shannon |  | 54.0395 | -7.8301
MV/LV Substation WA***007 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.382 | 3.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40288 | 0 |  | --> | C14 ex MONEENAGEISHA | Moneenageisha: T42 | Galway 110kv |  | 53.2837 | -9.0575
MV/LV Substation WA***013Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | E12 ex KILCOCK | Kilcock: T422 | Griffinrath |  | 53.4381 | -6.5453
MV/LV Substation WA***014X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.323 | 3.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41214 | 0 |  | --> | C21 ex BOGHALL ROAD | Boghall Road: T41 | Fassaroe |  | 53.202 | -6.0978
MV/LV Substation WA***015X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.197 | 26.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20048 | 0 |  | --> | E21 ex WEXFORD | Wexford: T121∥T122 | Wexford |  | 52.3645 | -6.5147
MV/LV Substation WA***015Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.175 | 5.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20396 | 0 |  | --> | C13 ex PURCELLS INCH | Purcells Inch: T42 | Kilkenny |  | 52.6145 | -7.2084
MV/LV Substation WA***019 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.051 | 8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.22248 | 0 |  | --> | C17 ex CENTRE PARK ROAD | Marina: T105 | Marina |  | 51.9027 | -8.4495
MV/LV Substation WA***024Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C15 ex GLENGOOLE | Glengoole: T41 | Thurles |  | 52.7326 | -7.5649
MV/LV Substation WA***025 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.435 | 5.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C11 ex BANDON | Bandon: T101 | Bandon |  | 51.7473 | -8.7323
MV/LV Substation WA***025 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.27075 | 0.34853 | 0 |  | --> | C14 ex DENNEHYS CROSS | Dennehys Cross: T42 | Trabeg |  | 51.895 | -8.5111
MV/LV Substation WA***025Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 4.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.019 | 0.0328 | 0 |  | --> | E18 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.2697 | -6.3977
MV/LV Substation WA***027 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.196 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20064 | 0 |  | --> | C26 ex ATHY | Athy: T102 | Athy |  | 53.0089 | -6.9919
MV/LV Substation WA***028X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | C13 ex ATHGARVAN | Athgarvan: T41 | Newbridge |  | 53.1588 | -6.7981
MV/LV Substation WA***030 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.339 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0 | 0 | Constrained,otherwise capacity available =405.6kW. | --> | C16 ex BUNDORAN | Bundoran: T41∥T42 | Cathaleens Fall |  | 54.4807 | -8.2787
MV/LV Substation WA***031X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.318 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.4099 | 0 |  | --> | C17 ex TYMON | Tymon: T41 | Cookstown |  | 53.3078 | -6.3656
MV/LV Substation WA***034Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =332kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41074 | 0 |  | --> | C21 ex PORTARLINGTON | Portarlington: T43 | Blake |  | 53.1388 | -7.0629
MV/LV Substation WA***035Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Building Structure | 0.1 | --> | 0.1 | 0.073 | 10.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10423 | 0 |  | --> | C30 ex WATERFORD IND EST | Waterford Ind Est: T42∥T44 | Butlerstown |  | 52.247 | -7.1417
MV/LV Substation WA***036 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =344kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C20 ex BALLYBEGGAN | Ballybeggan: T43∥T44 | Tralee |  | 52.2694 | -9.7012
MV/LV Substation WA***037 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.363 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40588 | 0 |  | --> | C15 ex RINEANNA | Rineanna: T42 | Drumline |  | 52.6997 | -8.8963
MV/LV Substation WA***041Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.318 | 3.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0019 | 0.4109 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge: T41 | Griffinrath |  | 53.3481 | -6.5393
MV/LV Substation WA***041Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.34 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.40148 | 0 |  | --> | C18 ex SUTTON | Sutton: T42 | Grange (dr) |  | 53.3943 | -6.1239
MV/LV Substation WA***044Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | E16 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.5972 | -6.6386
MV/LV Substation WA***045 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 2.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E13 ex KILCOCK | Kilcock: T421 | Griffinrath |  | 53.5242 | -6.6112
MV/LV Substation WA***046Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =260kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0019 | 0.4198 | 0 |  | --> | C24 ex BALLYCOOLIN | Ballycoolin: T42 | Finglas |  | 53.4011 | -6.3862
MV/LV Substation WA***047 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =417kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0038 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C16 ex COOLCARRON | Coolcarron: T41 | Barrymore |  | 52.1376 | -8.2722
MV/LV Substation WA***057 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.5156 | -6.1246
MV/LV Substation WA***057Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =101kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0209 | 0.19324 | 0 |  | --> | C21 ex DOUGLAS | Douglas: T42 | Trabeg |  | 51.8764 | -8.4171
MV/LV Substation WA***059Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =177kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20365 | 0 |  | --> | C13 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8588 | -8.3146
MV/LV Substation WA***065X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.346 | 3.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40854 | 0 |  | --> | C19 ex BOGHALL ROAD | Boghall Road: T41 | Fassaroe |  | 53.1834 | -6.1295
MV/LV Substation WA***067Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 10.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C12 ex WATERFORD IND EST | Waterford Ind Est: T42∥T44 | Butlerstown |  | 52.2445 | -7.1643
MV/LV Substation WA***068Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.2 | 0.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C14 ex SWORDS | Swords: T42 | Glasmore |  | 53.4639 | -6.2201
MV/LV Substation WA***070 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10408 | 0 |  | --> | C16 ex CARRAROE | Carraroe: T42 | Screeb |  | 53.1146 | -9.6894
MV/LV Substation WA***070Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.309 | 3.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.4003 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge: T41 | Griffinrath |  | 53.349 | -6.5404
MV/LV Substation WA***073X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex MANORHAMILTON | Manorhamilton: T422 | Sligo |  | 54.2539 | -8.2979
MV/LV Substation WA***077X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex PEMBROKE | Pembroke: T44 | Ringsend |  | 53.3421 | -6.2351
MV/LV Substation WA***079X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =27kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.45042 | 0 |  | --> | C19 ex LOUGHLINSTOWN | Loughlinstown: T41 | Carrickmines |  | 53.2433 | -6.1394
MV/LV Substation WA***080Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.477 | 2.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex COOLOCK | Coolock: T41 | Finglas |  | 53.3962 | -6.1955
MV/LV Substation WA***081 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0 | 2.8 |  | --> | 0.0285 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =36.1kW. | --> | C15 ex KILTIMAGH | Kiltimagh: T41 | Castlebar |  | 53.8673 | -8.9818
MV/LV Substation WA***083Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin: T41 | Inchicore 110kv |  | 53.3218 | -6.3623
MV/LV Substation WA***086X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =133kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21044 | 0 |  | --> | E25 ex PATRICKSWELL | Patrickswell: T421∥T422 | Limerick |  | 52.6231 | -8.8088
MV/LV Substation WA***090X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.161 | 5.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20114 | 0 |  | --> | E17 ex MOY | Moy: T421∥T422 | Moy |  | 54.1023 | -9.1626
MV/LV Substation WA***090Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.393 | 3.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00285 | 0.5 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge: T41 | Griffinrath |  | 53.3395 | -6.5381
MV/LV Substation WA***094 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C15 ex WATLING STREET | Watling Street: T41 | Francis Street |  | 53.346 | -6.2845
MV/LV Substation WA***098Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 2.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400kW. | --> | E16 ex WINDSOR | Windsor: T421∥T422 | Castlebar |  | 53.8598 | -9.2708
MV/LV Substation WA***099X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BALLYRICKARD | Ballyrickard: T41∥T42 | Tralee |  | 52.2652 | -9.7179
MV/LV Substation WA***099Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex POPPINTREE | Poppintree: T101 | Finglas |  | 53.4027 | -6.29
MV/LV Substation WA***107 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 6.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | E17 ex SPRINGS | Springs: T421∥T422 | Dungarvan |  | 52.1069 | -7.5815
MV/LV Substation WA***110Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.395 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4008 | 0 |  | --> | C11 ex MANOR STREET | Manor Street: T41 | Waterford |  | 52.2498 | -7.0735
MV/LV Substation WA***110Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.6kW. | --> | C16 ex MOUNTMELLICK | Mountmellick: T41∥T42 | Portlaoise |  | 53.1182 | -7.3113
MV/LV Substation WA***112 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.379 | 4.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.04085 | 0.5 | 0 |  | --> | C15 ex KIMMAGE | Kimmage: T41 | Inchicore 110kv |  | 53.3068 | -6.3054
MV/LV Substation WA***112X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.179 | 2.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =203.3kW. | --> | C15 ex KILRUSH | Kilrush: T41∥T42 | Tullabrack |  | 52.643 | -9.4804
MV/LV Substation WA***116X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =18kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.054867 | 0 |  | --> | C19 ex MILFORD (NR) | Milford (nr): T41∥T42 | Letterkenny |  | 55.1007 | -7.5699
MV/LV Substation WA***119Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =99kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10016 | 0 |  | --> | E30 ex LOUGHREA | Loughrea: T41∥T42 | Somerset |  | 53.2437 | -8.6755
MV/LV Substation WA***125 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.309 | 6.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex LIBERTY STREET | Liberty Street: T101 | Liberty Street |  | 51.8971 | -8.4815
MV/LV Substation WA***126 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.065 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10545 | 0 |  | --> | E16 ex DINGLE | Dingle: T422 | Oughtragh |  | 52.1513 | -10.2412
MV/LV Substation WA***128Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | C11 ex TEMPLEMORE | Templemore: T41 | Ikerrin |  | 52.7589 | -7.8244
MV/LV Substation WA***129X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C13 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6546 | -8.107
MV/LV Substation WA***129Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.33 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.40504 | 0 |  | --> | C11 ex RAMPARTS | Ramparts: T41 | Dundalk |  | 53.9926 | -6.398
MV/LV Substation WA***131Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =270kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02375 | 0.39528 | 0 |  | --> | C11 ex GARRYOWEN | Garryowen: T41 | Limerick |  | 52.6517 | -8.6002
MV/LV Substation WA***133 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0475 | 0.050005 | 0 |  | --> | E16 ex BEALISTOWN | Bealistown: | N/A |  | 52.2983 | -6.9567
MV/LV Substation WA***140X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0531 | 0 |  | --> | E16 ex BALLYCROSSAUN | Ballycrossaun: T421∥T422 | Somerset |  | 53.0945 | -8.2271
MV/LV Substation WA***148X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =77kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0.097615 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis: T41∥T42 | Dalton |  | 53.7662 | -8.7671
MV/LV Substation WA***150Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C19 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 53.1043 | -9.1614
MV/LV Substation WA***163 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.095 | 0.1 | Constrained,otherwise capacity available =169kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0114 | 0.1929 | 0 |  | --> | C22 ex CASTLEISLAND | Castleisland: T41∥T42 | Tralee |  | 52.2319 | -9.4427
MV/LV Substation WA***165Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | C18 ex PORTARLINGTON | Portarlington: T41∥T42 | Portlaoise |  | 53.1557 | -7.2731
MV/LV Substation WA***167 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 4.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.3kW. | --> | E14 ex MOVILLE | Moville: T421∥T422 | Trillick |  | 55.1806 | -7.1606
MV/LV Substation WA***168Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =36kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00285 | 0.04919 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.5196 | -6.1062
MV/LV Substation WA***174 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0.015 | 2.7 |  | --> | 0.0285 | 0 | 0 | 0 | 0 | 0.032307 | 0 |  | --> | C15 ex GLENGOOLE | Glengoole: T41 | Thurles |  | 52.7311 | -7.5695
MV/LV Substation WA***176 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0.025 | 2.7 |  | --> | 0.0285 | 0 | 0 | 0 | 0 | 0.030789 | 0 |  | --> | C15 ex GLENGOOLE | Glengoole: T41 | Thurles |  | 52.7389 | -7.5659
MV/LV Substation WA***184 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C12 ex ABBEYFEALE | Abbeyfeale: T42 | Trien |  | 52.3745 | -9.303
MV/LV Substation WA***184 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.269 | 2.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0228 | 0.39642 | 0 |  | --> | C19 ex COOLOCK | Coolock: T41 | Finglas |  | 53.3774 | -6.1769
MV/LV Substation WA***187Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05219 | 0 |  | --> | C12 ex ROSCOMMON | Roscommon: T42 | Lanesboro |  | 53.6388 | -8.1733
MV/LV Substation WA***188 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C20 ex KILMEADEN | Kilmeaden: T42 | Butlerstown |  | 52.2327 | -7.2315
MV/LV Substation WA***188X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 3.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | C16 ex BALLYSHANNON | Ballyshannon: T41∥T42 | Cathaleens Fall |  | 54.5133 | -8.2377
MV/LV Substation WA***189Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =356kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40698 | 0 |  | --> | C13 ex DOUGLAS | Douglas: T42 | Trabeg |  | 51.8775 | -8.4334
MV/LV Substation WA***198 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.198 | 3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20032 | 0 |  | --> | C20 ex KILMEADEN | Kilmeaden: T42 | Butlerstown |  | 52.2292 | -7.2266
MV/LV Substation WA***200 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.062 | 11.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.1026 | 0.11291 | 0 |  | --> | C20 ex BALLYBEG | Ballybeg: T102 | Carrickmines |  | 52.9735 | -6.0367
MV/LV Substation WA***202X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =97kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10048 | 0 |  | --> | E20 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.4435 | -7.3715
MV/LV Substation WA***206 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.073 | 9.9 |  | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0.09423 | 0 |  | --> | C11 ex KILCOOLE | Kilcoole: T41∥T42 | Fassaroe |  | 53.0666 | -6.0619
MV/LV Substation WA***207Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =72kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =104.4kW. | --> | E12 ex CASTLELYONS | Castlelyons: T421∥T422 | Barrymore |  | 52.0211 | -8.3344
MV/LV Substation WA***217Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =352kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4076 | 0 |  | --> | C20 ex COLLEGE PARK | College Park: T102 | College Park |  | 53.3923 | -6.3756
MV/LV Substation WA***218Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =333kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41058 | 0 |  | --> | C20 ex COLLEGE PARK | College Park: T102 | College Park |  | 53.3926 | -6.3736
MV/LV Substation WA***219 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =248kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.4086 | 0 |  | --> | C13 ex CAHERDAVIN | Caherdavin: T41 | Ardnacrusha |  | 52.6769 | -8.6603
MV/LV Substation WA***220 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.485 | 1.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.03705 | 0.5 | 0 |  | --> | C22 ex KIMMAGE | Kimmage: T42 | Inchicore 110kv |  | 53.3096 | -6.3069
MV/LV Substation WA***220 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C18 ex BALLYMOTE | Ballymote: T41 | Sligo |  | 54.0886 | -8.4927
MV/LV Substation WA***223X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C11 ex KILSARAN | Kilsaran: T42 | Drybridge |  | 53.9157 | -6.4047
MV/LV Substation WA***227Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00855 | 0.04242 | 0 |  | --> | E18 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.5158 | -7.1014
MV/LV Substation WA***228Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.058192 | 0 |  | --> | C12 ex BALBRIGGAN | Balbriggan: T42 | Glasmore |  | 53.5802 | -6.2282
MV/LV Substation WA***229Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C12 ex BALBRIGGAN | Balbriggan: T42 | Glasmore |  | 53.5833 | -6.2338
MV/LV Substation WA***231X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.369 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.39894 | 0 |  | --> | E11 ex BALLYHALE | Ballyhale: T421 | Kilkenny |  | 52.5335 | -7.1966
MV/LV Substation WA***231Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.058457 | 0 |  | --> | C12 ex BALBRIGGAN | Balbriggan: T42 | Glasmore |  | 53.5782 | -6.2227
MV/LV Substation WA***246Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | C16 ex KANTURK | Kanturk: T41∥T42 | Glenlara |  | 52.2729 | -8.8882
MV/LV Substation WA***246Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =163kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20583 | 0 |  | --> | C13 ex TUAM SOUTH | Tuam South: T42 | Cloon |  | 53.5166 | -8.8513
MV/LV Substation WA***248 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.073 | 7.5 |  | --> | 0.95 | 0 | 0 | 0 | 0.0076 | 0.5 | 0 |  | --> | C23 ex MILLTOWN (DR) | Milltown (dr): T101 | Poolbeg |  | 53.3325 | -6.2441
MV/LV Substation WA***248X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 3.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | C16 ex BALLYSHANNON | Ballyshannon: T41∥T42 | Cathaleens Fall |  | 54.5094 | -8.2413
MV/LV Substation WA***248Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =75kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10392 | 0 |  | --> | E17 ex CREAGH | Creagh: T421∥T422 | Athlone |  | 53.3145 | -8.2225
MV/LV Substation WA***250X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.376 | 9.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40382 | 0 |  | --> | C18 ex KILLYBEGS | Killybegs: T42 | Binbane |  | 54.6293 | -8.4455
MV/LV Substation WA***255 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.243 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.0323 | 0.39036 | 0 |  | --> | C18 ex MOUNT MERRION | Mount Merrion: T42 | Carrickmines |  | 53.2977 | -6.1883
MV/LV Substation WA***259 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =388kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =401.9kW. | --> | C13 ex KNOCKAPHUNTA | Knockaphunta: T41∥T42 | Castlebar |  | 53.8409 | -9.2926
MV/LV Substation WA***262X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.131 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0.20874 | 0 |  | --> | C22 ex HOWTH JUNCTION | Howth Junction: T42 | Grange (dr) |  | 53.3842 | -6.1761
MV/LV Substation WA***282 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.431 | 4.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.03895 | 0.5 | 0 |  | --> | C15 ex KIMMAGE | Kimmage: T41 | Inchicore 110kv |  | 53.309 | -6.303
MV/LV Substation WA***284Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =242kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4245 | 0 |  | --> | C20 ex COLLEGE PARK | College Park: T102 | College Park |  | 53.3927 | -6.3719
MV/LV Substation WA***287 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.085 | 0.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21759 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 51.8287 | -10.1715
MV/LV Substation WA***287Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1645 | -6.7857
MV/LV Substation WA***298X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | C11 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6674 | -8.1285
MV/LV Substation WA***299Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =318kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4129 | 0 |  | --> | C13 ex CASTLEVIEW | Castleview: T101 | Castleview |  | 51.8937 | -8.3638
MV/LV Substation WA***301X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central: T45 | Inchicore 110kv |  | 53.3396 | -6.3051
MV/LV Substation WA***313 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.427 | 7.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0114 | 0.5 | 0 |  | --> | C23 ex MILLTOWN (DR) | Milltown (dr): T101 | Poolbeg |  | 53.3311 | -6.2456
MV/LV Substation WA***314X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1 |  | --> | 0.95 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C11 ex TRIMMS LANE | Trimms Lane: T41 | Salthill |  | 53.2589 | -9.079
MV/LV Substation WA***315X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.341 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.39934 | 0 |  | --> | C14 ex SUTTON | Sutton: T42 | Grange (dr) |  | 53.3892 | -6.1205
MV/LV Substation WA***326 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | C16 ex KANTURK | Kanturk: T41∥T42 | Glenlara |  | 52.2725 | -8.8898
MV/LV Substation WA***334 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.249 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42346 | 0 |  | --> | C20 ex LITTLE BRAY | Little Bray: T42 | Fassaroe |  | 53.2113 | -6.1123
MV/LV Substation WA***335 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.155 | 3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20707 | 0 |  | --> | C20 ex GREENHILLS | Greenhills: T42 | Inchicore 110kv |  | 53.3075 | -6.3357
MV/LV Substation WA***335Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =80kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10315 | 0 |  | --> | E20 ex COLLOONEY | Collooney: T422 | Sligo |  | 54.2126 | -8.5125
MV/LV Substation WA***341 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 1.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052345 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8677 | -8.5465
MV/LV Substation WA***350X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.181 | 9.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20302 | 0 |  | --> | C18 ex CONVOY | Convoy: T41∥T42 | Letterkenny |  | 54.8585 | -7.6525
MV/LV Substation WA***352X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =379kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40336 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines: T41 | Carrickmines |  | 53.2412 | -6.1889
MV/LV Substation WA***353Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 7.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =47.2kW. | --> | E12 ex DUNFIRTH | Dunfirth: T122 | Dunfirth |  | 53.4554 | -6.9014
MV/LV Substation WA***356Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C24 ex GORESBRIDGE | Goresbridge: T41∥T42 | Kilkenny |  | 52.6196 | -7.0717
MV/LV Substation WA***367 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 7.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10064 | 0 |  | --> | E22 ex BANOGE | Banoge: T122 | Banoge |  | 52.6276 | -6.4187
MV/LV Substation WA***371Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.1 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C27 ex ROSBERCON | Rosbercon: T42 | Waterford |  | 52.3971 | -6.9481
MV/LV Substation WA***372X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex FAIRVIEW | Fairview: T41 | Mcdermott |  | 53.3659 | -6.2485
MV/LV Substation WA***373Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E15 ex KILMAGIG | Kilmagig: T42 | Arklow |  | 52.8298 | -6.2685
MV/LV Substation WA***373Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 8.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex STEPHENSTOWN | Stephenstown: T101 | Finglas |  | 53.5819 | -6.1368
MV/LV Substation WA***381Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C20 ex COLLEGE PARK | College Park: T102 | College Park |  | 53.3929 | -6.3705
MV/LV Substation WA***382 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.174 | 1.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20412 | 0 |  | --> | E14 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.1889 | -7.0809
MV/LV Substation WA***384X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C02 ex PEMBROKE | Pembroke: T44 | Ringsend |  | 53.3412 | -6.2314
MV/LV Substation WA***385 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.185 | 1.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20239 | 0 |  | --> | C21 ex WATERFORD IND EST | Waterford Ind Est: T41 | Butlerstown |  | 52.2359 | -7.139
MV/LV Substation WA***398 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.175 | 7.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20396 | 0 |  | --> | C17 ex KILLYBEGS | Killybegs: T41 | Binbane |  | 54.6487 | -8.4491
MV/LV Substation WA***4002 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex LEESON STREET | Leeson Street: T41 | Milltown (dr) |  | 53.3321 | -6.2452
MV/LV Substation WA***4015 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C22 ex ATHLONE | Athlone: T41 | Athlone |  | 53.4497 | -8.057
MV/LV Substation WA***4016 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 2.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E12 ex KILCOCK | Kilcock: T422 | Griffinrath |  | 53.4392 | -6.545
MV/LV Substation WA***4022 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 7.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0534 | 0 |  | --> | C17 ex KILLYBEGS | Killybegs: T41 | Binbane |  | 54.6475 | -8.4488
MV/LV Substation WA***403 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.083 | 0.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21788 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 51.8272 | -10.1705
MV/LV Substation WA***403 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | C18 ex BUNDORAN | Bundoran: T41∥T42 | Cathaleens Fall |  | 54.465 | -8.2818
MV/LV Substation WA***4035 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E19 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.4962 | -7.1281
MV/LV Substation WA***4036 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex GREYSTONES | Greystones: T41 | Fassaroe |  | 53.1498 | -6.0864
MV/LV Substation WA***4057 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.166 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20537 | 0 |  | --> | E11 ex ARDFINNAN | Ardfinnan: T421 | Cahir |  | 52.3249 | -8.1036
MV/LV Substation WA***4058 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E11 ex ARDFINNAN | Ardfinnan: T421 | Cahir |  | 52.3352 | -8.1132
MV/LV Substation WA***4062 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown: T101 | Inchicore 110kv |  | 53.2949 | -6.4257
MV/LV Substation WA***406X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | C16 ex CAPPAMORE | Cappamore: T41∥T42 | Ardnacrusha |  | 52.6071 | -8.2674
MV/LV Substation WA***4075 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 1.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10095 | 0 |  | --> | C18 ex KINGSCOURT | Kingscourt: T42 | Meath Hill |  | 53.8989 | -6.8136
MV/LV Substation WA***408 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | C18 ex BUNDORAN | Bundoran: T41∥T42 | Cathaleens Fall |  | 54.4532 | -8.2103
MV/LV Substation WA***4087 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052345 | 0 |  | --> | C24 ex MULLAGH | Mullagh: T44 | Meath Hill |  | 53.7918 | -6.8684
MV/LV Substation WA***408X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E11 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.6182 | -6.5604
MV/LV Substation WA***408X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =175kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20396 | 0 |  | --> | E18 ex CREAGH | Creagh: T421∥T422 | Athlone |  | 53.344 | -8.2437
MV/LV Substation WA***4093 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =352kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.4026 | 0 |  | --> | E11 ex KILCOLGAN | Kilcolgan: T421 | Galway 110kv |  | 53.1437 | -8.9446
MV/LV Substation WA***4098 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.315 | 3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0361 | 0.5 | 0 |  | --> | C14 ex GREENHILLS | Greenhills: T42 | Inchicore 110kv |  | 53.3199 | -6.3359
MV/LV Substation WA***4099 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | C11 ex MOUNTMELLICK | Mountmellick: T41∥T42 | Portlaoise |  | 53.155 | -7.5218
MV/LV Substation WA***409X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =14kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.055442 | 0 |  | --> | E18 ex CREAGH | Creagh: T421∥T422 | Athlone |  | 53.3927 | -8.3313
MV/LV Substation WA***4115 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =188kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20191 | 0 |  | --> | C31 ex CASTLEVIEW | Castleview: T101 | Castleview |  | 51.8942 | -8.3681
MV/LV Substation WA***412 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =72kVA. | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =99.4kW. | --> | C11 ex PORTARLINGTON | Portarlington: T41∥T42 | Portlaoise |  | 53.2334 | -7.2215
MV/LV Substation WA***4127 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =131kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BELGARD | Belgard: T41 | Cookstown |  | 53.2976 | -6.3627
MV/LV Substation WA***4130 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C30 ex TANEY | Taney: T102 | Carrickmines |  | 53.281 | -6.2407
MV/LV Substation WA***4140 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 6.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | E12 ex RATHKEALE | Rathkeale: T421∥T422 | Rathkeale |  | 52.4628 | -8.9233
MV/LV Substation WA***4140 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 6.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | E28 ex MILFORD (MWR) | Milford (mwr): T422 | Charleville |  | 52.3558 | -8.8566
MV/LV Substation WA***4142 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E11 ex BAGENALSTOWN | Bagenalstown: T421∥T422 | Carlow |  | 52.7019 | -6.9805
MV/LV Substation WA***4147 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.376 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40382 | 0 |  | --> | C21 ex WATERFORD IND EST | Waterford Ind Est: T41 | Butlerstown |  | 52.2422 | -7.1338
MV/LV Substation WA***416 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =178kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20349 | 0 |  | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7377 | -6.3453
MV/LV Substation WA***4160 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.476 | 4.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0.01805 | 0.5 | 0 |  | --> | C28 ex KILMORE | Kilmore: T102 | Finglas |  | 53.4071 | -6.1814
MV/LV Substation WA***4161 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =366kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =405.4kW. | --> | C17 ex KILMALLOCK | Kilmallock: T42 | Charleville |  | 52.4039 | -8.5885
MV/LV Substation WA***4162 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.329 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4112 | 0 |  | --> | C15 ex GORT | Gort: T41∥T42 | Ennis |  | 53.0625 | -8.811
MV/LV Substation WA***4163 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | C14 ex TEMPLEMORE | Templemore: T42 | Ikerrin |  | 52.7471 | -7.7217
MV/LV Substation WA***4164 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 2.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05142 | 0 |  | --> | C19 ex CASTLETOWNROCHE | Castletownroche: T41 | Mallow |  | 52.2105 | -8.5015
MV/LV Substation WA***4165 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.386 | 3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40224 | 0 |  | --> | C11 ex GREENHILLS | Greenhills: T42 | Inchicore 110kv |  | 53.3174 | -6.3374
MV/LV Substation WA***4166 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E23 ex LAWLESSTOWN | Lawlesstown: T421 | Doon |  | 52.2809 | -7.7375
MV/LV Substation WA***4171 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BALLYBODEN | Ballyboden: T41 | Cookstown |  | 53.2877 | -6.3043
MV/LV Substation WA***4176 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0532 | 0.5 | 0 |  | --> | C22 ex GRANGE (DR) | Grange (dr): T42 | Grange (dr) |  | 53.4036 | -6.1663
MV/LV Substation WA***4183 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C16 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 52.9413 | -9.3908
MV/LV Substation WA***4183 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E30 ex LOUGHREA | Loughrea: T41∥T42 | Somerset |  | 53.2044 | -8.6893
MV/LV Substation WA***4184 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | E17 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.6267 | -6.8581
MV/LV Substation WA***4184 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =303kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41522 | 0 |  | --> | C11 ex NAAS | Naas: T41 | Newbridge |  | 53.1844 | -6.606
MV/LV Substation WA***4185 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 8.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9854 | -6.0788
MV/LV Substation WA***4187 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex KILMORE | Kilmore: T102 | Finglas |  | 53.4073 | -6.1846
MV/LV Substation WA***4194 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray: T41 | Fassaroe |  | 53.2249 | -6.1217
MV/LV Substation WA***4195 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C16 ex MANOR STREET | Manor Street: T42 | Waterford |  | 52.2577 | -7.107
MV/LV Substation WA***4206 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1644 | -6.7859
MV/LV Substation WA***4229 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =110kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex PEMBROKE | Pembroke: T44 | Ringsend |  | 53.3412 | -6.239
MV/LV Substation WA***423 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =97kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10048 | 0 |  | --> | C12 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8591 | -8.2853
MV/LV Substation WA***4231 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =30kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.0481 | 0 |  | --> | C18 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1447 | -6.9178
MV/LV Substation WA***4232 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex ROOSKY | Roosky: T41 | Richmond |  | 53.7917 | -8.0312
MV/LV Substation WA***4232 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =388kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40192 | 0 |  | --> | C11 ex GARRYOWEN | Garryowen: T41 | Limerick |  | 52.6541 | -8.6184
MV/LV Substation WA***4243 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C31 ex CASTLEVIEW | Castleview: T101 | Castleview |  | 51.8999 | -8.3684
MV/LV Substation WA***4245 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 0.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C17 ex MONEYCOOLEY | Moneycooley: T41 | Griffinrath |  | 53.4159 | -6.4819
MV/LV Substation WA***4248 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C14 ex FERMOY NORTH | Fermoy North: T41∥T42 | Barrymore |  | 52.1611 | -8.2689
MV/LV Substation WA***4250 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.048 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C19 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 53.1194 | -9.1586
MV/LV Substation WA***4251 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E18 ex CREAGH | Creagh: T421∥T422 | Athlone |  | 53.3926 | -8.3285
MV/LV Substation WA***4252 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =31kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.9kW. | --> | C15 ex DRUMBEAR | Drumbear: T41∥T42 | Lisdrum |  | 54.2161 | -6.9229
MV/LV Substation WA***4285 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 7.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E19 ex BANOGE | Banoge: T122 | Banoge |  | 52.6382 | -6.2977
MV/LV Substation WA***4303 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.44 | 0.4 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex RIVERSTOWN | Riverstown: T41∥T42 | Kilbarry |  | 52.0074 | -8.3241
MV/LV Substation WA***4305 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 7.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E19 ex BANOGE | Banoge: T122 | Banoge |  | 52.6408 | -6.2956
MV/LV Substation WA***431Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E13 ex LONGFORD | Longford: T421 | Richmond |  | 53.9193 | -7.6098
MV/LV Substation WA***4326 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.351 | 3.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40776 | 0 |  | --> | C21 ex MARSHES | Marshes: T41 | Dundalk |  | 53.9625 | -6.3944
MV/LV Substation WA***4331 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =298kVA. | --> | 0.38 | 0 | 0 | 0 | 0.1596 | 0.248 | 0 |  | --> | C19 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1635 | -6.9214
MV/LV Substation WA***4332 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.19665 | 0.43897 | 0 |  | --> | C19 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1645 | -6.9239
MV/LV Substation WA***434 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0.01425 | 0.035477 | 0 |  | --> | C20 ex KNOCKMULLEN | Knockmullen: T42 | Great Island |  | 52.3235 | -6.9669
MV/LV Substation WA***4345 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex ROSCOMMON | Roscommon: T41 | Lanesboro |  | 53.6187 | -8.3631
MV/LV Substation WA***4349 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex MONEYCOOLEY | Moneycooley: T41 | Griffinrath |  | 53.3918 | -6.4957
MV/LV Substation WA***4350 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.3 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex WATLING STREET | Watling Street: T42 | Francis Street |  | 53.3459 | -6.284
MV/LV Substation WA***4371 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.291 | 0.3 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C14 ex SWORDS | Swords: T42 | Glasmore |  | 53.4631 | -6.2221
MV/LV Substation WA***4430 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C17 ex CARRIGALINE | Carrigaline: T41∥T42 | Barnahely |  | 51.8151 | -8.3722
MV/LV Substation WA***4432 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex PELLETSTOWN | Pelletstown: T102 | Finglas |  | 53.3762 | -6.3102
MV/LV Substation WA***4447 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8715 | -8.5308
MV/LV Substation WA***4448 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8705 | -8.5321
MV/LV Substation WA***4449 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8706 | -8.5347
MV/LV Substation WA***4467 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 7.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C11 ex GARRYCASTLE | Garrycastle: T41 | Athlone |  | 53.4178 | -7.9358
MV/LV Substation WA***449 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.104 | 0.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20979 | 0 |  | --> | C11 ex RIVERSTOWN | Riverstown: T41∥T42 | Kilbarry |  | 52.0122 | -8.344
MV/LV Substation WA***450 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =28kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.0434 | 0 |  | --> | C21 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4408 | -6.5102
MV/LV Substation WA***4538 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E17 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.8862 | -6.6848
MV/LV Substation WA***453Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.183 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2027 | 0 |  | --> | C11 ex MANOR STREET | Manor Street: T41 | Waterford |  | 52.249 | -7.0741
MV/LV Substation WA***457Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C18 ex MIDLETON | Midleton: T102 | Midleton |  | 51.976 | -8.1593
MV/LV Substation WA***458Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C16 ex LEIXLIP | Leixlip: T42 | Griffinrath |  | 53.3466 | -6.4956
MV/LV Substation WA***466Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.38 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4032 | 0 |  | --> | C11 ex PALMERSTOWN | Palmerstown: T41 | Finglas |  | 53.3576 | -6.3718
MV/LV Substation WA***468Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex GRAIGUE | Graigue: T41 | Carlow |  | 52.8358 | -6.9371
MV/LV Substation WA***474Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =198kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20032 | 0 |  | --> | C19 ex ROSEHILL | Rosehill: T41 | Kilkenny |  | 52.6411 | -7.248
MV/LV Substation WA***479 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.16 | 1.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.00095 | 0.2053 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.8268 | -6.8987
MV/LV Substation WA***479X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 4.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C18 ex BALLYJAMESDUFF | Ballyjamesduff: T42 | Shankill |  | 53.8766 | -7.1888
MV/LV Substation WA***481 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 6.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | C20 ex COLLINSTOWN | Collinstown: T41∥T42 | Grange (dr) |  | 53.4288 | -6.2275
MV/LV Substation WA***481X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.356 | 1.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =407kW. | --> | C16 ex KILKEE | Kilkee: T41 | Tullabrack |  | 52.6829 | -9.6458
MV/LV Substation WA***482Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =388kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40192 | 0 |  | --> | C31 ex CASTLEVIEW | Castleview: T101 | Castleview |  | 51.893 | -8.3708
MV/LV Substation WA***485X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C21 ex TYMON | Tymon: T41 | Cookstown |  | 53.2958 | -6.3554
MV/LV Substation WA***485Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex POPPINTREE | Poppintree: T101 | Finglas |  | 53.4089 | -6.2877
MV/LV Substation WA***488X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 10.7 |  | --> | 0.95 | 0 | 0 | 0 | 0.0057 | 0.5 | 0 |  | --> | C12 ex CABRA | Cabra: T102 | Finglas |  | 53.3759 | -6.3169
MV/LV Substation WA***498 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.297 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.40214 | 0 |  | --> | C19 ex SWORDS | Swords: T41 | Glasmore |  | 53.4635 | -6.2241
MV/LV Substation WA***499 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =199kVA. | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.41092 | 0 |  | --> | C11 ex NEWMARKET (DR) | Newmarket (dr): T41 | Francis Street |  | 53.3375 | -6.2749
MV/LV Substation WA***505Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.123 | 0.1 | Constrained,otherwise capacity available =171kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =204.6kW. | --> | C11 ex RATHDRUM | Rathdrum: T42 | Arklow |  | 52.9298 | -6.2232
MV/LV Substation WA***507Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =384kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40256 | 0 |  | --> | C18 ex MOUNTGORRY | Mountgorry: T42 | Grange (dr) |  | 53.4522 | -6.1977
MV/LV Substation WA***508X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052037 | 0 |  | --> | C19 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.726 | -6.3831
MV/LV Substation WA***508Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =303kVA. | --> | 0.38 | 0 | 0 | 0 | 0.08455 | 0.32622 | 0 |  | --> | C18 ex MOUNTGORRY | Mountgorry: T42 | Grange (dr) |  | 53.4525 | -6.2004
MV/LV Substation WA***509 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 4.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.043992 | 0 |  | --> | E20 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.2593 | -6.4837
MV/LV Substation WA***509Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =376kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40382 | 0 |  | --> | C16 ex MOUNTGORRY | Mountgorry: T42 | Grange (dr) |  | 53.451 | -6.2001
MV/LV Substation WA***510Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C16 ex COOLCARRON | Coolcarron: T41 | Barrymore |  | 52.1383 | -8.2768
MV/LV Substation WA***510Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =341kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0836 | 0.32134 | 0 |  | --> | C16 ex MOUNTGORRY | Mountgorry: T42 | Grange (dr) |  | 53.4506 | -6.202
MV/LV Substation WA***512 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3.8 |  | --> | 0.95 | 0 | 0 | 0 | 0.02185 | 0.5 | 0 |  | --> | C14 ex CRUMLIN | Crumlin: T42 | Inchicore 110kv |  | 53.3213 | -6.3301
MV/LV Substation WA***519Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E13 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4742 | -6.2327
MV/LV Substation WA***524Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.376 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40382 | 0 |  | --> | C11 ex MANOR STREET | Manor Street: T41 | Waterford |  | 52.248 | -7.072
MV/LV Substation WA***529 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =74kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0076 | 0 | 0 | Constrained,otherwise capacity available =211.2kW. | --> | C14 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6562 | -8.1121
MV/LV Substation WA***531Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =73kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =104.2kW. | --> | E14 ex BEALNABLATH | Bealnablath: T421 | Bandon |  | 51.8618 | -8.8392
MV/LV Substation WA***534X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin: T44 | Inchicore 110kv |  | 53.3247 | -6.3705
MV/LV Substation WA***536Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.383 | 0.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40272 | 0 |  | --> | C12 ex AGHAMORE | Aghamore: T42 | Lanesboro |  | 53.6749 | -7.9987
MV/LV Substation WA***569 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.293 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.02185 | 0.39376 | 0 |  | --> | C14 ex LOUGHLINSTOWN | Loughlinstown: T42 | Carrickmines |  | 53.2612 | -6.1376
MV/LV Substation WA***570 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.218 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0855 | 0.3381 | 0 |  | --> | C14 ex LOUGHLINSTOWN | Loughlinstown: T42 | Carrickmines |  | 53.2598 | -6.1339
MV/LV Substation WA***570Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C23 ex CLONMINCH | Clonminch: T41 | Thornsberry |  | 53.2766 | -7.4598
MV/LV Substation WA***572 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 5.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052037 | 0 |  | --> | C13 ex PURCELLS INCH | Purcells Inch: T42 | Kilkenny |  | 52.6324 | -7.2224
MV/LV Substation WA***577X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C21 ex PORTARLINGTON | Portarlington: T43 | Blake |  | 53.1534 | -7.1597
MV/LV Substation WA***588 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 2.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10095 | 0 |  | --> | C19 ex CASTLETOWNROCHE | Castletownroche: T41 | Mallow |  | 52.2154 | -8.4956
MV/LV Substation WA***593X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.1009 | 0.1 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C18 ex COOLCORCORAN | Coolcorcoran: T41∥T42 | Knockearagh |  | 52.0874 | -9.5517
MV/LV Substation WA***595Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex ATHGARVAN | Athgarvan: T41 | Newbridge |  | 53.1813 | -6.798
MV/LV Substation WA***598 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 2.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10454 | 0 |  | --> | C17 ex GALWAY 110KV | Galway 110kv: T103 | Galway 110kv |  | 53.2943 | -9.0172
MV/LV Substation WA***602 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 5.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10032 | 0 |  | --> | E16 ex BALLYBUNION | Ballybunion: T421∥T422 | Trien |  | 52.468 | -9.5357
MV/LV Substation WA***602Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C39 ex COLLEGE PARK | College Park: T103 | College Park |  | 53.4144 | -6.406
MV/LV Substation WA***603Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =122kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0399 | 0.1701 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1631 | -6.7849
MV/LV Substation WA***604 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.302 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.40038 | 0 |  | --> | C17 ex WHITEHALL | Whitehall: T41 | Finglas |  | 53.3774 | -6.2542
MV/LV Substation WA***605 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.271 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.03515 | 0.38312 | 0 |  | --> | C17 ex WHITEHALL | Whitehall: T41 | Finglas |  | 53.379 | -6.2524
MV/LV Substation WA***605X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 5.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.045107 | 0 |  | --> | C13 ex PURCELLS INCH | Purcells Inch: T42 | Kilkenny |  | 52.628 | -7.2156
MV/LV Substation WA***609X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 1.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10268 | 0 |  | --> | E11 ex CURRALEIGH | Curraleigh: T421∥T422 | Kilbarry |  | 51.9025 | -8.6687
MV/LV Substation WA***614Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.019 | 3 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00285 | 0.051725 | 0 |  | --> | C17 ex LOUGHANALLA | Loughanalla: T41∥T42 | Mullingar |  | 53.6842 | -7.2965
MV/LV Substation WA***625X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.15 | 0.2 | Constrained,otherwise capacity available =289kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0361 | 0.37938 | 0 |  | --> | C11 ex COOLMINE | Coolmine: T41 | Finglas |  | 53.3734 | -6.3912
MV/LV Substation WA***630X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C12 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.9391 | -7.7576
MV/LV Substation WA***635Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =36kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05219 | 0 |  | --> | C18 ex BLAKE | Blake: T41∥T42 | Blake |  | 53.277 | -6.8531
MV/LV Substation WA***636 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =183kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.1967 | 0 |  | --> | C14 ex MACETOWN | Macetown: T102 | Macetown |  | 53.4068 | -6.4131
MV/LV Substation WA***636Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.44 | 0.4 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex RIVERSTOWN | Riverstown: T41∥T42 | Kilbarry |  | 52.006 | -8.3237
MV/LV Substation WA***637Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.042345 | 0 |  | --> | C15 ex BLAKE | Blake: T41∥T42 | Blake |  | 53.2917 | -6.8486
MV/LV Substation WA***637Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.44 | 0.4 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex RIVERSTOWN | Riverstown: T41∥T42 | Kilbarry |  | 52.0066 | -8.323
MV/LV Substation WA***640 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C19 ex BUSHFIELD | Bushfield: T41 | Athlone |  | 53.4288 | -7.9464
MV/LV Substation WA***646X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.023 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05414 | 0 |  | --> | C20 ex CASHEL | Cashel: T42 | Cahir |  | 52.5116 | -7.875
MV/LV Substation WA***648X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =25kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053845 | 0 |  | --> | E11 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.6081 | -6.5564
MV/LV Substation WA***660Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.262 | 10.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0171 | 0.40348 | 0 |  | --> | E11 ex COOLROE | Coolroe: T121 | Coolroe |  | 51.8898 | -8.5965
MV/LV Substation WA***662Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.338 | 4.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4098 | 0 |  | --> | E12 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.2451 | -6.3477
MV/LV Substation WA***663X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.366 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.3964 | 0 |  | --> | C19 ex MANOR STREET | Manor Street: T41 | Waterford |  | 52.2541 | -7.105
MV/LV Substation WA***676 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.009 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.056147 | 0 |  | --> | E16 ex BALLYCROSSAUN | Ballycrossaun: T421∥T422 | Somerset |  | 53.0843 | -8.2204
MV/LV Substation WA***682Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =149kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0 | 0 | Constrained,otherwise capacity available =204kW. | --> | C11 ex PORTARLINGTON | Portarlington: T41∥T42 | Portlaoise |  | 53.2299 | -7.224
MV/LV Substation WA***683 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.375 | 4.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.02375 | 0.5 | 0 |  | --> | C15 ex KIMMAGE | Kimmage: T41 | Inchicore 110kv |  | 53.3069 | -6.3109
MV/LV Substation WA***688Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =45.3kW. | --> | E12 ex CASTLELYONS | Castlelyons: T421∥T422 | Barrymore |  | 52.0317 | -8.3256
MV/LV Substation WA***692Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =180kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0285 | 0.17318 | 0 |  | --> | E20 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.3247 | -7.0984
MV/LV Substation WA***693X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 3.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C24 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.5459 | -10.0199
MV/LV Substation WA***699 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | E11 ex LUMCLOON | Lumcloon: T421∥T422 | Dallow |  | 53.2243 | -7.9533
MV/LV Substation WA***699Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 9.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex MIDLETON | Midleton: T101 | Midleton |  | 51.9122 | -8.1769
MV/LV Substation WA***707 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | E17 ex CREESLOUGH | Creeslough: T421 | Ardnagappary |  | 55.1942 | -7.9676
MV/LV Substation WA***708 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 1.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =104.8kW. | --> | E14 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1496 | -7.4462
MV/LV Substation WA***713X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.366 | 0.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4054 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 51.834 | -10.1733
MV/LV Substation WA***722Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =167kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20521 | 0 |  | --> | E12 ex CARRIGSHANE | Carrigshane: T422 | Midleton |  | 51.9096 | -8.0737
MV/LV Substation WA***727Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex CLONMINCH | Clonminch: T41 | Thornsberry |  | 53.2748 | -7.4972
MV/LV Substation WA***729X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CASTLEVIEW | Castleview: T101 | Castleview |  | 51.8966 | -8.3782
MV/LV Substation WA***736Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.9 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex SALLINS | Sallins: T41 | Griffinrath |  | 53.2458 | -6.664
MV/LV Substation WA***737Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex SALLINS | Sallins: T41 | Griffinrath |  | 53.2464 | -6.6615
MV/LV Substation WA***738X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C12 ex CROSSMOLINA | Crossmolina: T41∥T42 | Moy |  | 54.1666 | -9.3459
MV/LV Substation WA***738Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex SALLINS | Sallins: T41 | Griffinrath |  | 53.2472 | -6.6592
MV/LV Substation WA***744X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.048 | 0 | Constrained,otherwise capacity available =173kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20427 | 0 |  | --> | C19 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 53.0245 | -9.3102
MV/LV Substation WA***752X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex PEMBROKE | Pembroke: T41∥T43 | Ringsend |  | 53.3374 | -6.2414
MV/LV Substation WA***752Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 9.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C19 ex MIDLETON | Midleton: T101 | Midleton |  | 51.9191 | -8.1985
MV/LV Substation WA***754 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.073 | 2.6 |  | --> | 0.095 | 0 | 0 | 0 | 0.0456 | 0.05623 | 0 |  | --> | E13 ex KILCOCK | Kilcock: T421 | Griffinrath |  | 53.5231 | -6.614
MV/LV Substation WA***754Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =372kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02565 | 0.37746 | 0 |  | --> | C22 ex ATHLONE | Athlone: T41 | Athlone |  | 53.4263 | -8.0053
MV/LV Substation WA***755Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.311 | 4.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.411 | 0 |  | --> | E20 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.26 | -6.4798
MV/LV Substation WA***763X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 7.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.18901 | 0 |  | --> | E24 ex BANOGE | Banoge: T122 | Banoge |  | 52.649 | -6.229
MV/LV Substation WA***783 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 11.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =57.7kW. | --> | E16 ex WESTPORT | Westport: T421∥T422 | Castlebar |  | 53.7551 | -9.5557
MV/LV Substation WA***787 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central: T45 | Inchicore 110kv |  | 53.3352 | -6.334
MV/LV Substation WA***789 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C19 ex BALLYBAILIE | Ballybailie: T41 | Dundalk |  | 53.8534 | -6.5554
MV/LV Substation WA***794X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =83kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10268 | 0 |  | --> | E11 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.4458 | -6.3395
MV/LV Substation WA***797 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.05 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0.02565 | 0.08069 | 0 |  | --> | C11 ex DRUMQUIN | Drumquin: T42 | Ennis |  | 52.8261 | -9.1179
MV/LV Substation WA***797X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =396kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40064 | 0 |  | --> | E13 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.936 | -6.6941
MV/LV Substation WA***801X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.057 | 0.1 | Constrained,otherwise capacity available =468kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.03515 | 0.5 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn: T42 | Cookstown |  | 53.2796 | -6.3618
MV/LV Substation WA***810Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =111kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0152 | 0.19775 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1628 | -6.7917
MV/LV Substation WA***812 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =65kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0285 | 0.07545 | 0 |  | --> | C15 ex CARRIGALINE | Carrigaline: T41∥T42 | Barnahely |  | 51.8164 | -8.3808
MV/LV Substation WA***813X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.179 | 2.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20333 | 0 |  | --> | C22 ex BUSHFIELD | Bushfield: T42 | Athlone |  | 53.4634 | -7.8038
MV/LV Substation WA***819Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.17 | 4.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20474 | 0 |  | --> | E12 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.2452 | -6.3309
MV/LV Substation WA***830 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.3kW. | --> | E23 ex ATHBOY | Athboy: T423 | Navan |  | 53.525 | -6.8889
MV/LV Substation WA***832 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4.1 |  | --> | 0.95 | 0 | 0 | 0 | 0.01425 | 0.5 | 0 |  | --> | C15 ex KIMMAGE | Kimmage: T41 | Inchicore 110kv |  | 53.3074 | -6.3094
MV/LV Substation WA***832 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.412 | 3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex MERRION SQUARE | Merrion Square: T42 | Ringsend |  | 53.3367 | -6.2427
MV/LV Substation WA***836 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 3.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.2kW. | --> | C15 ex DERRYBEG | Derrybeg: T41∥T42 | Ardnagappary |  | 55.0632 | -8.2767
MV/LV Substation WA***837 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.312 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41384 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.8283 | -6.8991
MV/LV Substation WA***837X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0 | 0 | Constrained,otherwise capacity available =44.8kW. | --> | C20 ex TEMPLEMORE | Templemore: T42 | Ikerrin |  | 52.8072 | -7.8303
MV/LV Substation WA***845 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.073 | 7.4 |  | --> | 0.095 | 0 | 0 | 0 | 0.00665 | 0.09723 | 0 |  | --> | E22 ex BANOGE | Banoge: T122 | Banoge |  | 52.6233 | -6.4212
MV/LV Substation WA***863Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.169 | 3.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.2009 | 0 |  | --> | C14 ex WATERFORD | Waterford: T42 | Waterford |  | 52.2697 | -7.1372
MV/LV Substation WA***864 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =198kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200.3kW. | --> | C14 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.662 | -8.0931
MV/LV Substation WA***881X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.308 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0019 | 0.41246 | 0 |  | --> | C17 ex CARRIGLAWN | Carriglawn: T41∥T42 | Wexford |  | 52.3424 | -6.4771
MV/LV Substation WA***884X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C02 ex PEMBROKE | Pembroke: T44 | Ringsend |  | 53.3412 | -6.2314
MV/LV Substation WA***899X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C22 ex ATHLONE | Athlone: T41 | Athlone |  | 53.4482 | -8.06
MV/LV Substation WA***902Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =134kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01995 | 0.18929 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1622 | -6.788
MV/LV Substation WA***918X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.048 | 0 | Constrained,otherwise capacity available =380kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4032 | 0 |  | --> | C20 ex ENNISTYMON | Ennistymon: T41∥T42 | Ennis |  | 52.8692 | -9.1545
MV/LV Substation WA***920Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.153 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.01425 | 0.19238 | 0 |  | --> | C17 ex ROOSKY | Roosky: T41 | Richmond |  | 53.8306 | -7.9307
MV/LV Substation WA***921Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.189 | 6.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20176 | 0 |  | --> | C17 ex CASHEL | Cashel: T41 | Cahir |  | 52.5113 | -7.8807
MV/LV Substation WA***924 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.077 | 3.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =103.6kW. | --> | C17 ex BALLYSHANNON | Ballyshannon: T41∥T42 | Cathaleens Fall |  | 54.518 | -8.1689
MV/LV Substation WA***925Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =80kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10315 | 0 |  | --> | C24 ex GORESBRIDGE | Goresbridge: T41∥T42 | Kilkenny |  | 52.6245 | -7.0568
MV/LV Substation WA***927 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.108 | 0.1 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen: T41∥T42 | Tonroe |  | 53.9086 | -8.464
MV/LV Substation WA***932 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00285 | 0.04873 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8553 | -8.5431
MV/LV Substation WA***934Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =317kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41306 | 0 |  | --> | C14 ex MOYLISH | Moylish: T41∥T42 | Ardnacrusha |  | 52.6781 | -8.6391
MV/LV Substation WA***934Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C18 ex NAAS | Naas: T42 | Newbridge |  | 53.1535 | -6.7089
MV/LV Substation WA***935 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E17 ex DRUMLINE | Drumline: T421∥T422 | Drumline |  | 52.7929 | -8.7702
MV/LV Substation WA***937 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C13 ex BUTTEVANT | Buttevant: T41∥T42 | Mallow |  | 52.2312 | -8.6633
MV/LV Substation WA***938 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.143 | 3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20492 | 0 |  | --> | C16 ex LOUGHANALLA | Loughanalla: T41∥T42 | Mullingar |  | 53.6811 | -7.2963
MV/LV Substation WA***939 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =297kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41614 | 0 |  | --> | C11 ex GARDEN CITY | Garden City: T41∥T42 | Arklow |  | 52.682 | -6.2944
MV/LV Substation WA***942X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =360kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40636 | 0 |  | --> | E12 ex BALLINROBE | Ballinrobe: T421∥T422 | Dalton |  | 53.6267 | -9.2213
MV/LV Substation WA***953X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 9.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C19 ex MIDLETON | Midleton: T101 | Midleton |  | 51.9287 | -8.1953
MV/LV Substation WA***954 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North: T41∥T42 | Ennis |  | 52.8584 | -8.9953
MV/LV Substation WA***957Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 5.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C11 ex BALLINCOLLIG | Ballincollig: T41 | Kilbarry |  | 51.8316 | -8.5805
MV/LV Substation WA***958X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =175kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20396 | 0 |  | --> | C15 ex CLONAKILTY | Clonakilty: T41∥T42 | Dunmanway |  | 51.6231 | -8.8994
MV/LV Substation WA***976 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.057 | 0.1 | Constrained,otherwise capacity available =287kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.40668 | 0 |  | --> | C16 ex OLDBAWN | Oldbawn: T42 | Cookstown |  | 53.2829 | -6.3646
MV/LV Substation WA***978X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =354kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4073 | 0 |  | --> | C15 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8506 | -8.2897
MV/LV Substation WA***981X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.19 | 7.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.1916 | 0 |  | --> | C22 ex KILLOTERAN | Killoteran: T102 | Killoteran |  | 52.2291 | -7.1452
MV/LV Substation WA***990X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =343kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40902 | 0 |  | --> | C15 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.849 | -8.2985
MV/LV Substation WA***991Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.19 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.1906 | 0 |  | --> | C20 ex CASHEL | Cashel: T42 | Cahir |  | 52.512 | -7.8751
MV/LV Substation WA***992Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =36kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05219 | 0 |  | --> | E11 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.6252 | -6.6104
MV/LV Substation WA***995X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | E18 ex BIRR | Birr: T422 | Dallow |  | 53.1011 | -8.0088
MV/LV Substation WC***082X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 3.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C20 ex BOGHALL ROAD | Boghall Road: T42 | Fassaroe |  | 53.1795 | -6.0935
MV/LV Substation WC***4357 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C13 ex MOUNT MISERY | Mount Misery: T41 | Waterford |  | 52.2635 | -7.1028
MV/LV Substation WD***224X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E12 ex CARNDONAGH | Carndonagh: T421∥T422 | Trillick |  | 55.3378 | -7.2423
MV/LV Substation WE***001 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0171 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C16 ex BALLYSHANNON | Ballyshannon: T41∥T42 | Cathaleens Fall |  | 54.5003 | -8.196
MV/LV Substation WE***002 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =210kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0038 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C23 ex PORTLAOISE | Portlaoise: T41 | Portlaoise |  | 53.0334 | -7.2949
MV/LV Substation WE***003Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.133 | 2.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.19944 | 0 |  | --> | E20 ex BLESSINGTON | Blessington: T422 | Kilteel |  | 53.1685 | -6.5408
MV/LV Substation WE***004 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =53kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.2172 | 0 |  | --> | C13 ex TUAM SOUTH | Tuam South: T42 | Cloon |  | 53.5128 | -8.8593
MV/LV Substation WE***004 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.446 | 9.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.7976 | -9.5125
MV/LV Substation WE***005 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.055 | 1.2 |  | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =96.9kW. | --> | E16 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.1401 | -7.454
MV/LV Substation WE***009 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.047 | 2.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.21805 | 0 |  | --> | C19 ex CALLAN | Callan: T41∥T42 | Kilkenny |  | 52.5455 | -7.3953
MV/LV Substation WE***009Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C12 ex CARRIGLAWN | Carriglawn: T41∥T42 | Wexford |  | 52.3568 | -6.447
MV/LV Substation WE***012 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.28 | 2.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.01425 | 0.5 | 0 |  | --> | C16 ex SPA ROAD | Spa Road: T41∥T42 | Doon |  | 52.3528 | -7.6978
MV/LV Substation WE***014 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.322 | 4.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41228 | 0 |  | --> | C18 ex BALLYRICKARD | Ballyrickard: T41∥T42 | Tralee |  | 52.2736 | -9.7143
MV/LV Substation WE***015 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00665 | 0.20897 | 0 |  | --> | E13 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9401 | -6.7058
MV/LV Substation WE***017Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.246 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.03325 | 0.3889 | 0 |  | --> | C12 ex BALBRIGGAN | Balbriggan: T42 | Glasmore |  | 53.6101 | -6.1956
MV/LV Substation WE***018 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.344 | 7.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex MILLTOWN (DR) | Milltown (dr): T101 | Poolbeg |  | 53.3278 | -6.2436
MV/LV Substation WE***018 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.173 | 3.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.20127 | 0 |  | --> | C17 ex CASTLEREA | Castlerea: T41∥T42 | Carrick On Shannon |  | 53.7617 | -8.4808
MV/LV Substation WE***018 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.355 | 9.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.40114 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.7965 | -9.5382
MV/LV Substation WE***020 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.123 | 3.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.0361 | 0.40396 | 0 |  | --> | C21 ex DEANSGRANGE | Deansgrange: T41 | Carrickmines |  | 53.2701 | -6.1741
MV/LV Substation WE***021 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =282kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0.40544 | 0 |  | --> | C15 ex CLONAKILTY | Clonakilty: T41∥T42 | Dunmanway |  | 51.6218 | -8.9007
MV/LV Substation WE***022 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =69kVA. | --> | 0.095 | 0 | 0 | 0 | 0.01615 | 0 | 0 | Constrained,otherwise capacity available =87.8kW. | --> | C19 ex KNOCKAPHUNTA | Knockaphunta: T41∥T42 | Castlebar |  | 53.848 | -9.3139
MV/LV Substation WE***025 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.3 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0 | 0 | Constrained,otherwise capacity available =409.7kW. | --> | C15 ex BUNDORAN | Bundoran: T41∥T42 | Cathaleens Fall |  | 54.4757 | -8.2981
MV/LV Substation WE***026Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =409kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex DENNEHYS CROSS | Dennehys Cross: T41 | Trabeg |  | 51.8939 | -8.4973
MV/LV Substation WE***027Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.294 | 9.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.4126 | 0 |  | --> | C12 ex TRABEG | Trabeg: T101 | Trabeg |  | 51.8863 | -8.4625
MV/LV Substation WE***030 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =163kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.4322 | 0 |  | --> | C17 ex RATHMULLAN | Rathmullan: T41 | Drybridge |  | 53.716 | -6.3583
MV/LV Substation WE***036Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.045107 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.3042 | -6.4801
MV/LV Substation WE***038 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 5.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E13 ex CRANE | Crane: T122 | Crane |  | 52.4268 | -6.3778
MV/LV Substation WE***041 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.343 | 4.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.40102 | 0 |  | --> | C16 ex LAWLESSTOWN | Lawlesstown: T42 | Doon |  | 52.3543 | -7.7113
MV/LV Substation WE***044 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0475 | 0.5 | 0 |  | --> | C14 ex SANDYFORD | Sandyford: T42 | Carrickmines |  | 53.2776 | -6.2431
MV/LV Substation WE***044X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.11 | 0.1 | Constrained,otherwise capacity available =189kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20176 | 0 |  | --> | C23 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.6189 | -8.9144
MV/LV Substation WE***045X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.359 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4065 | 0 |  | --> | C18 ex DUN LAOGHAIRE | Dun Laoghaire: T42 | Blackrock |  | 53.2955 | -6.1447
MV/LV Substation WE***046Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =167kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.19421 | 0 |  | --> | C24 ex ATHLONE | Athlone: T41 | Athlone |  | 53.4076 | -7.9829
MV/LV Substation WE***048 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =75kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =93.9kW. | --> | C24 ex RAMSTOWN | Ramstown: T41∥T42 | Crane |  | 52.6733 | -6.311
MV/LV Substation WE***052Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CASTLEVIEW | Castleview: T101 | Castleview |  | 51.8941 | -8.3612
MV/LV Substation WE***056X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0475 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C18 ex RAMSTOWN | Ramstown: T41∥T42 | Crane |  | 52.6714 | -6.296
MV/LV Substation WE***059 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.346 | 5.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.0285 | 0 | 0 | Constrained,otherwise capacity available =378.5kW. | --> | C17 ex BANDON | Bandon: T101 | Bandon |  | 51.7672 | -8.6639
MV/LV Substation WE***059X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.149 | 10.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.02565 | 0.181 | 0 |  | --> | E11 ex COOLROE | Coolroe: T121 | Coolroe |  | 51.8869 | -8.6187
MV/LV Substation WE***061X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =176kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2038 | 0 |  | --> | C22 ex ROCHES STREET | Roches Street: T42 | Limerick |  | 52.6666 | -8.6311
MV/LV Substation WE***063 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =221kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.41764 | 0 |  | --> | C12 ex MERVILLE | Merville: T42 | Finglas |  | 53.3853 | -6.3097
MV/LV Substation WE***077Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C19 ex CALLAN | Callan: T41∥T42 | Kilkenny |  | 52.5488 | -7.3966
MV/LV Substation WE***085X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.11 | 0.1 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C15 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.5158 | -8.8641
MV/LV Substation WE***089X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.391 | 5.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40144 | 0 |  | --> | E19 ex ARDNAREE | Ardnaree: T421 | Moy |  | 54.1193 | -9.13
MV/LV Substation WE***092Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COLLEGE PARK | College Park: T102 | College Park |  | 53.3916 | -6.384
MV/LV Substation WE***093Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COLLEGE PARK | College Park: T102 | College Park |  | 53.3901 | -6.3859
MV/LV Substation WE***095Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =382kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =402.9kW. | --> | C19 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.0884 | -7.6233
MV/LV Substation WE***097Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C18 ex TELAYDON | Telaydon: T42 | Lisdrum |  | 54.2493 | -6.9696
MV/LV Substation WE***099 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.176 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.0209 | 0.1818 | 0 |  | --> | C17 ex BALLINASLOE | Ballinasloe: T41∥T42 | Somerset |  | 53.321 | -8.2186
MV/LV Substation WE***104Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =280kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.40376 | 0 |  | --> | C19 ex GRANGE (DR) | Grange (dr): T41 | Grange (dr) |  | 53.399 | -6.1648
MV/LV Substation WE***110 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =465kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CLONDALKIN | Clondalkin: T41 | Inchicore 110kv |  | 53.3317 | -6.3976
MV/LV Substation WE***113 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C17 ex RINEANNA | Rineanna: T42 | Drumline |  | 52.7118 | -8.8886
MV/LV Substation WE***114 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 5.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E11 ex CRANE | Crane: T122 | Crane |  | 52.5199 | -6.5572
MV/LV Substation WE***120 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =365kVA. | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.38556 | 0 |  | --> | C11 ex DOCK ROAD | Dock Road: T41∥T42 | Limerick |  | 52.6488 | -8.6448
MV/LV Substation WE***123X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =267kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42072 | 0 |  | --> | C14 ex NEWMARKET (DR) | Newmarket (dr): T41 | Francis Street |  | 53.3372 | -6.283
MV/LV Substation WE***123Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.289 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.038 | 0.37738 | 0 |  | --> | C12 ex BALBRIGGAN | Balbriggan: T42 | Glasmore |  | 53.6093 | -6.1987
MV/LV Substation WE***125X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =440kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex LOUGHLINSTOWN | Loughlinstown: T41 | Carrickmines |  | 53.2488 | -6.1447
MV/LV Substation WE***128Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.165 | 5.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20552 | 0 |  | --> | C21 ex BALLINCOLLIG | Ballincollig: T41 | Kilbarry |  | 51.8859 | -8.5877
MV/LV Substation WE***152 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.28 | 0.3 | Constrained,otherwise capacity available =287kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0342 | 0.38168 | 0 |  | --> | C21 ex BREWERY ROAD | Brewery Road: T41 | Carrickmines |  | 53.276 | -6.2276
MV/LV Substation WE***153 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.267 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42072 | 0 |  | --> | C12 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8903 | -8.535
MV/LV Substation WE***157 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =345kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.4037 | 0 |  | --> | C20 ex BALLYBEGGAN | Ballybeggan: T43∥T44 | Tralee |  | 52.2721 | -9.6972
MV/LV Substation WE***162 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.185 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.41398 | 0 |  | --> | C20 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8789 | -8.5215
MV/LV Substation WE***168 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.28 | 0.3 | Constrained,otherwise capacity available =304kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.41208 | 0 |  | --> | C21 ex BREWERY ROAD | Brewery Road: T41 | Carrickmines |  | 53.278 | -6.2256
MV/LV Substation WE***169X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3294 | -6.4919
MV/LV Substation WE***170X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3294 | -6.4929
MV/LV Substation WE***171X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3288 | -6.4922
MV/LV Substation WE***172X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3282 | -6.493
MV/LV Substation WE***177 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.28 | 0.3 | Constrained,otherwise capacity available =336kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0285 | 0.38012 | 0 |  | --> | C21 ex BREWERY ROAD | Brewery Road: T41 | Carrickmines |  | 53.2804 | -6.2258
MV/LV Substation WE***178Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COLLEGE PARK | College Park: T102 | College Park |  | 53.39 | -6.3894
MV/LV Substation WE***185X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C44 ex BEDFORD ROW | Bedford Row: T41 | Francis Street |  | 53.3445 | -6.2691
MV/LV Substation WE***188Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin: T41 | Inchicore 110kv |  | 53.326 | -6.3628
MV/LV Substation WE***192 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.222 | 8 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.4245 | 0 |  | --> | C17 ex CENTRE PARK ROAD | Marina: T105 | Marina |  | 51.9022 | -8.4653
MV/LV Substation WE***196Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =382kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40288 | 0 |  | --> | C17 ex RATHMULLAN | Rathmullan: T41 | Drybridge |  | 53.7146 | -6.3535
MV/LV Substation WE***201 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =357kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40682 | 0 |  | --> | C15 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8494 | -8.2975
MV/LV Substation WE***201Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 9.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.8012 | -9.5201
MV/LV Substation WE***202 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.054 | 0.1 | Constrained,otherwise capacity available =124kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2118 | 0 |  | --> | C12 ex SANTRY | Santry: T42 | Finglas |  | 53.3945 | -6.2465
MV/LV Substation WE***202X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C23 ex KILMORE | Kilmore: T101 | Finglas |  | 53.4022 | -6.2278
MV/LV Substation WE***204 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.114 | 9.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.019 | 0.1933 | 0 |  | --> | C30 ex TANEY | Taney: T102 | Carrickmines |  | 53.2786 | -6.239
MV/LV Substation WE***211Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex KILBARRY | Kilbarry: T43 | Kilbarry |  | 51.9243 | -8.487
MV/LV Substation WE***211Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =173kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20427 | 0 |  | --> | C17 ex MORRISTOWN | Morristown: T41∥T42 | Newbridge |  | 53.1774 | -6.8028
MV/LV Substation WE***214 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.1259 | 0.1 | Constrained,otherwise capacity available =382kVA. | --> | 0.95 | 0 | 0 | 0 | 0.0418 | 0.5 | 0 |  | --> | C18 ex WOLFE TONE STREET | Wolfe Tone Street: T102 | Finglas |  | 53.3557 | -6.2666
MV/LV Substation WE***216 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.286 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.39884 | 0 |  | --> | C18 ex SUTTON | Sutton: T42 | Grange (dr) |  | 53.3989 | -6.1295
MV/LV Substation WE***221X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.321 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.40244 | 0 |  | --> | C13 ex INCHICORE NORTH | Inchicore North: T41 | Inchicore 110kv |  | 53.3375 | -6.3448
MV/LV Substation WE***222Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.343 | 9.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40902 | 0 |  | --> | C17 ex ENNIS | Ennis: T101 | Ennis |  | 52.8504 | -8.9876
MV/LV Substation WE***225 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =73kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0038 | 0.10023 | 0 |  | --> | C12 ex CAHERDAVIN | Caherdavin: T42 | Ardnacrusha |  | 52.6628 | -8.6472
MV/LV Substation WE***240X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.103 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.43282 | 0 |  | --> | C16 ex GILLOGUE | Gillogue: T41∥T42 | Ardnacrusha |  | 52.6832 | -8.6024
MV/LV Substation WE***242Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C24 ex ATHLONE | Athlone: T41 | Athlone |  | 53.4056 | -7.9837
MV/LV Substation WE***245X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex MISERY HILL | Misery Hill: T101 | Poolbeg |  | 53.3456 | -6.2579
MV/LV Substation WE***247X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =168kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20506 | 0 |  | --> | C13 ex TUAM SOUTH | Tuam South: T42 | Cloon |  | 53.5136 | -8.8612
MV/LV Substation WE***249X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Building Structure | 0.1 | --> | 0.1 | 0.1 | 1.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | C17 ex MILLTOWN MALBAY | Milltown Malbay: T42 | Tullabrack |  | 52.7981 | -9.3399
MV/LV Substation WE***256X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =498kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CRANMORE | Cranmore: T41∥T42 | Sligo |  | 54.2697 | -8.4739
MV/LV Substation WE***270X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis: T41∥T42 | Dalton |  | 53.7502 | -8.7714
MV/LV Substation WE***271 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.113 | 3.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20945 | 0 |  | --> | C18 ex MONEENAGEISHA | Moneenageisha: T42 | Galway 110kv |  | 53.2818 | -9.0263
MV/LV Substation WE***273Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =253kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42284 | 0 |  | --> | C19 ex SEMPERIT | Semperit: T41 | Grange Castle |  | 53.3487 | -6.3452
MV/LV Substation WE***274Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex SEMPERIT | Semperit: T41 | Grange Castle |  | 53.3487 | -6.3452
MV/LV Substation WE***293 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.297 | 6.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.41314 | 0 |  | --> | C20 ex PELLETSTOWN | Pelletstown: T102 | Finglas |  | 53.3828 | -6.3186
MV/LV Substation WE***301Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.397 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40048 | 0 |  | --> | E11 ex LONGFORD | Longford: T421 | Richmond |  | 53.7149 | -7.8119
MV/LV Substation WE***302 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =316kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.40522 | 0 |  | --> | C24 ex BALLYCOOLIN | Ballycoolin: T42 | Finglas |  | 53.4003 | -6.3696
MV/LV Substation WE***305X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 3.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C12 ex BOYLE | Boyle: T41∥T42 | Carrick On Shannon |  | 53.8777 | -8.396
MV/LV Substation WE***313 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E18 ex NEWPORT | Newport: T421 | Carrowbeg |  | 53.8926 | -9.5472
MV/LV Substation WE***327Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COLLEGE PARK | College Park: T102 | College Park |  | 53.3917 | -6.384
MV/LV Substation WE***336Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =297kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02565 | 0.38914 | 0 |  | --> | C15 ex CARRIGALINE | Carrigaline: T41∥T42 | Barnahely |  | 51.8192 | -8.4042
MV/LV Substation WE***347Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =277kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =419.2kW. | --> | C20 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.0955 | -7.6319
MV/LV Substation WE***350Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.453 | 8.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex KILLOTERAN | Killoteran: T101 | Killoteran |  | 52.2489 | -7.1633
MV/LV Substation WE***350Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =303kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0342 | 0.37922 | 0 |  | --> | C11 ex LOUGHSHINNY | Loughshinny: T41 | Glasmore |  | 53.5264 | -6.1589
MV/LV Substation WE***351Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 8.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex KILLOTERAN | Killoteran: T101 | Killoteran |  | 52.2492 | -7.1625
MV/LV Substation WE***355X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.354 | 3.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4073 | 0 |  | --> | C14 ex SANDYFORD | Sandyford: T42 | Carrickmines |  | 53.2754 | -6.2421
MV/LV Substation WE***356Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.146 | 2.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20846 | 0 |  | --> | C19 ex CALLAN | Callan: T41∥T42 | Kilkenny |  | 52.5485 | -7.3926
MV/LV Substation WE***361Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =315kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0.40038 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1782 | -6.7808
MV/LV Substation WE***368 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | C21 ex TRAMORE | Tramore: T41 | Butlerstown |  | 52.1392 | -7.1818
MV/LV Substation WE***373 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4.1 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E18 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.2704 | -6.423
MV/LV Substation WE***382Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.331 | 4.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4109 | 0 |  | --> | C18 ex LIFFEY VALLEY | Liffey Valley: T42 | Inchicore 110kv |  | 53.3461 | -6.3988
MV/LV Substation WE***383 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 10.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0.07315 | 0.5 | 0 |  | --> | C33 ex SALTHILL | Salthill: T101 | Salthill |  | 53.2611 | -9.1195
MV/LV Substation WE***383 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C22 ex JOHNSTOWN | Johnstown: T42 | Kilteel |  | 53.2295 | -6.6168
MV/LV Substation WE***385Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =277kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0361 | 0.3812 | 0 |  | --> | C21 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6744 | -7.2554
MV/LV Substation WE***387X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =167kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20521 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis: T41∥T42 | Dalton |  | 53.6907 | -8.7551
MV/LV Substation WE***398Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.5522 | -6.3626
MV/LV Substation WE***4004 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.3 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex RINEANNA | Rineanna: T42 | Drumline |  | 52.7098 | -8.8956
MV/LV Substation WE***4012 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | E23 ex BALTRASNA | Baltrasna: T121 | Baltrasna |  | 53.5807 | -6.3054
MV/LV Substation WE***4019 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.11 | 0.1 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.5215 | -8.8823
MV/LV Substation WE***4031 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E23 ex BALTRASNA | Baltrasna: T121 | Baltrasna |  | 53.5764 | -6.31
MV/LV Substation WE***4033 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex RINEANNA | Rineanna: T41 | Drumline |  | 52.7132 | -8.8926
MV/LV Substation WE***4037 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex TYMON | Tymon: T42 | Cookstown |  | 53.3102 | -6.3578
MV/LV Substation WE***4052 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 0.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10253 | 0 |  | --> | C15 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.5189 | -8.876
MV/LV Substation WE***4078 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard: T41 | Cookstown |  | 53.2963 | -6.373
MV/LV Substation WE***407Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex COLLEGE PARK | College Park: T102 | College Park |  | 53.3923 | -6.3842
MV/LV Substation WE***409 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.305 | 5.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.40592 | 0 |  | --> | C12 ex BALLINCOLLIG | Ballincollig: T42 | Kilbarry |  | 51.886 | -8.6151
MV/LV Substation WE***409X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =108kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0437 | 0.1682 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.7031 | -6.2599
MV/LV Substation WE***4100 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 3.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C21 ex DEANSGRANGE | Deansgrange: T41 | Carrickmines |  | 53.2732 | -6.1736
MV/LV Substation WE***411Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C16 ex LEIXLIP | Leixlip: T42 | Griffinrath |  | 53.3567 | -6.4903
MV/LV Substation WE***4123 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 26.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E21 ex WEXFORD | Wexford: T121∥T122 | Wexford |  | 52.3419 | -6.5379
MV/LV Substation WE***4124 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 8.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex KILLOTERAN | Killoteran: T101 | Killoteran |  | 52.2496 | -7.1628
MV/LV Substation WE***4134 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =392kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =401.3kW. | --> | C14 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6585 | -8.1159
MV/LV Substation WE***4135 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.05 | 0.1 | Constrained,otherwise capacity available =350kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40792 | 0 |  | --> | C14 ex COOLMINE | Coolmine: T42 | Finglas |  | 53.3823 | -6.4182
MV/LV Substation WE***4136 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.1259 | 0.1 | Constrained,otherwise capacity available =399kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex WOLFE TONE STREET | Wolfe Tone Street: T102 | Finglas |  | 53.3557 | -6.2667
MV/LV Substation WE***415 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =225kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.42306 | 0 |  | --> | C14 ex MACETOWN | Macetown: T102 | Macetown |  | 53.4093 | -6.3956
MV/LV Substation WE***4150 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.354 | 1.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.11305 | 0.5 | 0 |  | --> | C12 ex MONEYCOOLEY | Moneycooley: T42 | Griffinrath |  | 53.3668 | -6.5222
MV/LV Substation WE***4158 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E11 ex KILCOLGAN | Kilcolgan: T421 | Galway 110kv |  | 53.1401 | -8.9239
MV/LV Substation WE***415Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.11 | 0.1 | Constrained,otherwise capacity available =397kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40048 | 0 |  | --> | C15 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.5074 | -8.874
MV/LV Substation WE***4162 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E16 ex KILMACTHOMAS | Kilmacthomas: T421∥T422 | Dungarvan |  | 52.1541 | -7.4242
MV/LV Substation WE***416Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.368 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4051 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.8214 | -6.8946
MV/LV Substation WE***4178 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 8.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown: T102 | Carrickmines |  | 53.282 | -6.372
MV/LV Substation WE***4179 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex GRANGE (DR) | Grange (dr): T41 | Grange (dr) |  | 53.408 | -6.1664
MV/LV Substation WE***417Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.209 | 0.2 | Constrained,otherwise capacity available =361kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4062 | 0 |  | --> | C17 ex BISHOPSTOWN | Bishopstown: T41 | Kilbarry |  | 51.8848 | -8.5805
MV/LV Substation WE***4180 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex GRANGE (DR) | Grange (dr): T41 | Grange (dr) |  | 53.4083 | -6.1651
MV/LV Substation WE***4183 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.17 | 11.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20474 | 0 |  | --> | C34 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2772 | -9.0754
MV/LV Substation WE***418Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.209 | 0.2 | Constrained,otherwise capacity available =398kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40032 | 0 |  | --> | C17 ex BISHOPSTOWN | Bishopstown: T41 | Kilbarry |  | 51.8859 | -8.581
MV/LV Substation WE***418Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.393 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40112 | 0 |  | --> | C17 ex ROOSKY | Roosky: T41 | Richmond |  | 53.7743 | -8.1029
MV/LV Substation WE***4193 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.396 | 3.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40064 | 0 |  | --> | E16 ex ASHBOURNE | Ashbourne: T422 | Finglas |  | 53.5187 | -6.4085
MV/LV Substation WE***4203 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 3.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C17 ex BALLINASLOE | Ballinasloe: T41∥T42 | Somerset |  | 53.3189 | -8.2222
MV/LV Substation WE***420Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.209 | 0.2 | Constrained,otherwise capacity available =352kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4076 | 0 |  | --> | C17 ex BISHOPSTOWN | Bishopstown: T41 | Kilbarry |  | 51.8841 | -8.5827
MV/LV Substation WE***421Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C16 ex LEIXLIP | Leixlip: T42 | Griffinrath |  | 53.3533 | -6.4936
MV/LV Substation WE***4243 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0528 | 0 |  | --> | C21 ex CASTLEREA | Castlerea: T41∥T42 | Carrick On Shannon |  | 53.7412 | -8.4002
MV/LV Substation WE***425Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex WATERFORD | Waterford: T41 | Waterford |  | 52.2612 | -7.1167
MV/LV Substation WE***4275 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.362 | 12.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40604 | 0 |  | --> | E18 ex COOLROE | Coolroe: T122 | Coolroe |  | 51.8867 | -8.6086
MV/LV Substation WE***4288 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 5.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C14 ex CLOON | Cloon: T42 | Cloon |  | 53.4784 | -8.8306
MV/LV Substation WE***4296 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0741 | 0.5 | 0 |  | --> | E13 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.474 | -6.2451
MV/LV Substation WE***4302 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.373 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.3993 | 0 |  | --> | C12 ex MONEYCOOLEY | Moneycooley: T42 | Griffinrath |  | 53.3653 | -6.5255
MV/LV Substation WE***431 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052037 | 0 |  | --> | C17 ex ROSEHILL | Rosehill: T41 | Kilkenny |  | 52.642 | -7.2687
MV/LV Substation WE***434 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.127 | 1.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =206.3kW. | --> | E15 ex CASTLETOWNBERE | Castletownbere: T421 | Ballylicky |  | 51.6512 | -9.9147
MV/LV Substation WE***436 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C17 ex ROSEHILL | Rosehill: T41 | Kilkenny |  | 52.6419 | -7.267
MV/LV Substation WE***4392 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C19 ex CALLAN | Callan: T41∥T42 | Kilkenny |  | 52.5552 | -7.4084
MV/LV Substation WE***4404 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.483 | 12.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | E18 ex COOLROE | Coolroe: T122 | Coolroe |  | 51.8885 | -8.5995
MV/LV Substation WE***4442 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.181 | 10.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20302 | 0 |  | --> | E11 ex COOLROE | Coolroe: T121 | Coolroe |  | 51.8876 | -8.6173
MV/LV Substation WE***454Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.5263 | -6.3025
MV/LV Substation WE***455X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.313 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.40768 | 0 |  | --> | C18 ex PALMERSTOWN | Palmerstown: T42 | Finglas |  | 53.3521 | -6.3565
MV/LV Substation WE***468Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =271kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41512 | 0 |  | --> | C15 ex CARRIGALINE | Carrigaline: T41∥T42 | Barnahely |  | 51.8198 | -8.3984
MV/LV Substation WE***471 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =71kVA. | --> | 0.095 | 0 | 0 | 0 | 0.00285 | 0.10154 | 0 |  | --> | C17 ex ROSEHILL | Rosehill: T41 | Kilkenny |  | 52.6422 | -7.2658
MV/LV Substation WE***478Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COLLEGE PARK | College Park: T102 | College Park |  | 53.3895 | -6.3872
MV/LV Substation WE***480 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.307 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.3946 | 0 |  | --> | C20 ex POLLERTON | Pollerton: T42 | Carlow |  | 52.8212 | -6.8964
MV/LV Substation WE***480 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 9.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0534 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.8022 | -9.5356
MV/LV Substation WE***481 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 9.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.8061 | -9.5397
MV/LV Substation WE***485 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.098 | 3.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.21068 | 0 |  | --> | C26 ex CLIFDEN | Clifden: T41∥T42 | Galway 110kv |  | 53.4902 | -10.0192
MV/LV Substation WE***489X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052495 | 0 |  | --> | C24 ex MULLAGH | Mullagh: T44 | Meath Hill |  | 53.8112 | -6.9151
MV/LV Substation WE***494Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C21 ex TRAMORE | Tramore: T41 | Butlerstown |  | 52.146 | -7.1824
MV/LV Substation WE***495X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =384kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40256 | 0 |  | --> | C14 ex GARDEN CITY | Garden City: T41∥T42 | Arklow |  | 52.6804 | -6.276
MV/LV Substation WE***500X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.1 |  | --> | 0.95 | 0 | 0 | 0 | 0.0152 | 0.5 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount: T42 | Inchicore 110kv |  | 53.3224 | -6.3694
MV/LV Substation WE***500X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.158 | 3.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20661 | 0 |  | --> | C12 ex TRAMORE | Tramore: T42 | Butlerstown |  | 52.1618 | -7.1674
MV/LV Substation WE***500Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.086 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0.03895 | 0.17644 | 0 |  | --> | C15 ex LEIXLIP | Leixlip: T41 | Griffinrath |  | 53.3572 | -6.4716
MV/LV Substation WE***503Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.173 | 9.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.19927 | 0 |  | --> | C17 ex MIDLETON | Midleton: T101 | Midleton |  | 51.9133 | -8.1799
MV/LV Substation WE***508X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.13 | 5.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2109 | 0 |  | --> | E11 ex CRANE | Crane: T122 | Crane |  | 52.521 | -6.5584
MV/LV Substation WE***509 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.319 | 0.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.02565 | 0.38576 | 0 |  | --> | C15 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.8302 | -8.9766
MV/LV Substation WE***509X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =340kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.39448 | 0 |  | --> | C17 ex DOUGLAS | Douglas: T42 | Trabeg |  | 51.8619 | -8.4339
MV/LV Substation WE***515X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex LUCAN EAST | Lucan East: T41∥T42 | Grange Castle |  | 53.3798 | -6.4427
MV/LV Substation WE***516X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.388 | 1.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40192 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount: T42 | Inchicore 110kv |  | 53.3222 | -6.3686
MV/LV Substation WE***521Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =170kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20474 | 0 |  | --> | C21 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6762 | -7.2544
MV/LV Substation WE***523X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =324kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0114 | 0.5 | 0 |  | --> | C17 ex BALGADDY | Balgaddy: T41 | Grange Castle |  | 53.3223 | -6.4192
MV/LV Substation WE***523Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =248kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4236 | 0 |  | --> | C16 ex TOGHER | Togher: T42 | Trabeg |  | 51.8738 | -8.5105
MV/LV Substation WE***533 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C16 ex RINEANNA | Rineanna: T41 | Drumline |  | 52.7135 | -8.8916
MV/LV Substation WE***545X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.183 | 9.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2027 | 0 |  | --> | C14 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.8128 | -9.5633
MV/LV Substation WE***546 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =24kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0152 | 0.037992 | 0 |  | --> | C17 ex CARRIGALINE | Carrigaline: T41∥T42 | Barnahely |  | 51.7978 | -8.2768
MV/LV Substation WE***550 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex RINEANNA | Rineanna: T42 | Drumline |  | 52.7092 | -8.8935
MV/LV Substation WE***555Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =324kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.40198 | 0 |  | --> | C18 ex DOUGLAS | Douglas: T41 | Trabeg |  | 51.8697 | -8.4302
MV/LV Substation WE***556 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.266 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.40888 | 0 |  | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham: T41∥T42 | Letterkenny |  | 54.9961 | -7.5174
MV/LV Substation WE***562Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =309kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =409.3kW. | --> | C14 ex BELLFIELD | Bellfield: T41∥T42 | Crane |  | 52.5132 | -6.5763
MV/LV Substation WE***563Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.163 | 5.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.01235 | 0.19283 | 0 |  | --> | C12 ex BALLINCOLLIG | Ballincollig: T42 | Kilbarry |  | 51.8867 | -8.6146
MV/LV Substation WE***567X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.344 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40886 | 0 |  | --> | C13 ex INCHICORE NORTH | Inchicore North: T41 | Inchicore 110kv |  | 53.3362 | -6.3424
MV/LV Substation WE***568 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =95kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.8kW. | --> | E18 ex BEALNABLATH | Bealnablath: T421 | Bandon |  | 51.8798 | -8.7632
MV/LV Substation WE***569Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.083 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0.01615 | 0.20088 | 0 |  | --> | C15 ex LEIXLIP | Leixlip: T41 | Griffinrath |  | 53.3561 | -6.4717
MV/LV Substation WE***570 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex RINEANNA | Rineanna: T42 | Drumline |  | 52.71 | -8.8932
MV/LV Substation WE***570Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.114 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0.0285 | 0.1833 | 0 |  | --> | C15 ex LEIXLIP | Leixlip: T41 | Griffinrath |  | 53.355 | -6.4736
MV/LV Substation WE***576Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.392 | 11.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40128 | 0 |  | --> | C22 ex BALLYBEG | Ballybeg: T102 | Carrickmines |  | 52.982 | -6.0451
MV/LV Substation WE***582 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 11.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | E11 ex WESTPORT | Westport: T421∥T422 | Castlebar |  | 53.7653 | -9.8067
MV/LV Substation WE***590Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =115kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0209 | 0.19115 | 0 |  | --> | C21 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6723 | -7.2564
MV/LV Substation WE***596 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.266 | 5.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.40188 | 0 |  | --> | C20 ex TEMPLEOGUE | Templeogue: T41 | Milltown (dr) |  | 53.2875 | -6.3179
MV/LV Substation WE***597X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | E17 ex ACHILL | Achill: T422 | Carrowbeg |  | 53.9777 | -10.0842
MV/LV Substation WE***597Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 4.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10253 | 0 |  | --> | C12 ex CASTLEKNOCK | Castleknock: T41∥T42 | Finglas |  | 53.3691 | -6.3777
MV/LV Substation WE***598Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.112 | 1.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =213.6kW. | --> | E15 ex CASTLETOWNBERE | Castletownbere: T421 | Ballylicky |  | 51.6484 | -9.9151
MV/LV Substation WE***612X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =82kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.8kW. | --> | E12 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 53.0228 | -7.287
MV/LV Substation WE***630X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 8.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C23 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9642 | -6.099
MV/LV Substation WE***631 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.281 | 3.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0551 | 0.3606 | 0 |  | --> | C21 ex MONKSTOWN | Monkstown: T41 | Blackrock |  | 53.2766 | -6.1893
MV/LV Substation WE***632X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.155 | 10.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.0114 | 0.19507 | 0 |  | --> | E11 ex COOLROE | Coolroe: T121 | Coolroe |  | 51.8873 | -8.6211
MV/LV Substation WE***638X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =315kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41338 | 0 |  | --> | C14 ex DENNEHYS CROSS | Dennehys Cross: T42 | Trabeg |  | 51.8946 | -8.504
MV/LV Substation WE***644Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =196kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20064 | 0 |  | --> | C16 ex LEIXLIP | Leixlip: T42 | Griffinrath |  | 53.3499 | -6.4923
MV/LV Substation WE***645Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =168kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20106 | 0 |  | --> | C17 ex NAAS | Naas: T41 | Newbridge |  | 53.2131 | -6.6868
MV/LV Substation WE***647X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 0.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | E16 ex MILLTOWN (SR) | Milltown (sr): T422 | Oughtragh |  | 52.1072 | -9.7902
MV/LV Substation WE***647X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.315 | 10.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.01995 | 0.39238 | 0 |  | --> | E13 ex COOLROE | Coolroe: T121 | Coolroe |  | 51.8818 | -8.6221
MV/LV Substation WE***654X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =274kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.41666 | 0 |  | --> | C22 ex TOGHER | Togher: T42 | Trabeg |  | 51.8733 | -8.5024
MV/LV Substation WE***665 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =114kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2133 | 0 |  | --> | C16 ex LUCAN EAST | Lucan East: T41∥T42 | Grange Castle |  | 53.374 | -6.44
MV/LV Substation WE***670Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.209 | 0.2 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BISHOPSTOWN | Bishopstown: T41 | Kilbarry |  | 51.8853 | -8.5824
MV/LV Substation WE***671 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =179kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C46 ex BEDFORD ROW | Bedford Row: T41 | Francis Street |  | 53.3453 | -6.2672
MV/LV Substation WE***683X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =388kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.39692 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.5286 | -6.303
MV/LV Substation WE***688Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex TOGHER | Togher: T42 | Trabeg |  | 51.869 | -8.4923
MV/LV Substation WE***702 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.48 | 0.5 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex ORANMORE | Oranmore: T44 | Galway 110kv |  | 53.2771 | -8.9246
MV/LV Substation WE***706X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.217 | 0.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.41624 | 0 |  | --> | C20 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.8306 | -8.9968
MV/LV Substation WE***721Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =376kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.39882 | 0 |  | --> | C20 ex CAHERDAVIN | Caherdavin: T42 | Ardnacrusha |  | 52.6748 | -8.6875
MV/LV Substation WE***722X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.443 | 2.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.01045 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount: T41 | Inchicore 110kv |  | 53.3134 | -6.3479
MV/LV Substation WE***731X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1093 | 0 |  | --> | C17 ex KINSALE | Kinsale: T41∥T42 | Bandon |  | 51.7803 | -8.6372
MV/LV Substation WE***734X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3.5 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MONEENAGEISHA | Moneenageisha: T42 | Galway 110kv |  | 53.2813 | -9.0319
MV/LV Substation WE***735X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3.5 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MONEENAGEISHA | Moneenageisha: T42 | Galway 110kv |  | 53.2813 | -9.0319
MV/LV Substation WE***737 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =215.4kW. | --> | E15 ex BEALISTOWN | Bealistown: T421 | Great Island |  | 52.2652 | -6.7479
MV/LV Substation WE***738 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 5.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1019 | 0 |  | --> | E13 ex BLESSINGTON | Blessington: T421 | Kilteel |  | 53.1476 | -6.6235
MV/LV Substation WE***739Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =166kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0114 | 0.19337 | 0 |  | --> | C21 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.6754 | -7.2567
MV/LV Substation WE***743X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 4.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | E12 ex BAGENALSTOWN | Bagenalstown: T421∥T422 | Carlow |  | 52.6956 | -6.9874
MV/LV Substation WE***760 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.087 | 0.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21729 | 0 |  | --> | C23 ex GLENTIES | Glenties: T41 | Binbane |  | 54.7619 | -8.4157
MV/LV Substation WE***760X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 5.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | C17 ex OUGHTERARD | Oughterard: T41∥T42 | Galway 110kv |  | 53.4236 | -9.3102
MV/LV Substation WE***762X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 5.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1033 | 0 |  | --> | C16 ex ABBEYLAND | Abbeyland: T42 | Navan |  | 53.6553 | -6.696
MV/LV Substation WE***763X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex TRINITY | Trinity: T101 | Poolbeg |  | 53.3438 | -6.2505
MV/LV Substation WE***765 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =151kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.20169 | 0 |  | --> | C11 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4007 | -6.4178
MV/LV Substation WE***777X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.329 | 2.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4112 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount: T41 | Inchicore 110kv |  | 53.3143 | -6.349
MV/LV Substation WE***778 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.174 | 1.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.19912 | 0 |  | --> | E13 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.1455 | -6.9935
MV/LV Substation WE***779Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.381 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40304 | 0 |  | --> | C13 ex MULGANNON | Mulgannon: T41 | Wexford |  | 52.3076 | -6.4593
MV/LV Substation WE***783Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CENTRE PARK ROAD | Marina: T106 | Marina |  | 51.8976 | -8.4643
MV/LV Substation WE***785 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C17 ex DONNYBROOK | Donnybrook: T41 | Milltown (dr) |  | 53.3258 | -6.2088
MV/LV Substation WE***789X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.336 | 0.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.00095 | 0.40912 | 0 |  | --> | C16 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.8418 | -8.9947
MV/LV Substation WE***793Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =379kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40336 | 0 |  | --> | E12 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.6417 | -6.662
MV/LV Substation WE***796X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =468kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0019 | 0.5 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown: T101 | Inchicore 110kv |  | 53.29 | -6.4385
MV/LV Substation WE***798Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =371kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.40162 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.5203 | -6.3156
MV/LV Substation WE***804Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400kW. | --> | E17 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 52.9129 | -7.3484
MV/LV Substation WE***805Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E18 ex FINEA | Finea: T421∥T422 | Shankill |  | 53.7739 | -7.2991
MV/LV Substation WE***805Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.373 | 4.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.095 | 0.3043 | 0 |  | --> | E12 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.2422 | -6.3421
MV/LV Substation WE***806Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 3.6 |  | --> | 0.095 | 0 | 0 | 0 | 0.00855 | 0.09538 | 0 |  | --> | C14 ex CASHEL | Cashel: T42 | Cahir |  | 52.5676 | -7.8889
MV/LV Substation WE***810 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4.2 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex DUN LAOGHAIRE | Dun Laoghaire: T42 | Blackrock |  | 53.2962 | -6.1488
MV/LV Substation WE***810X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 0.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.39502 | 0 |  | --> | C15 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.8311 | -8.9807
MV/LV Substation WE***821X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3.5 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MONEENAGEISHA | Moneenageisha: T42 | Galway 110kv |  | 53.2812 | -9.0318
MV/LV Substation WE***837Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex GLEBE | Glebe: T41∥T42 | Richmond |  | 53.7258 | -7.8005
MV/LV Substation WE***837Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C13 ex MULGANNON | Mulgannon: T41 | Wexford |  | 52.3181 | -6.468
MV/LV Substation WE***839X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.2 | 1.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C11 ex ORANMORE | Oranmore: T41 | Galway 110kv |  | 53.2823 | -8.9751
MV/LV Substation WE***857 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 4.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.041107 | 0 |  | --> | E12 ex BAGENALSTOWN | Bagenalstown: T421∥T422 | Carlow |  | 52.6856 | -6.9943
MV/LV Substation WE***860Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.161 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.0114 | 0.19414 | 0 |  | --> | C12 ex MORNINGTON ROAD | Mornington Road: T42 | Drybridge |  | 53.7077 | -6.3231
MV/LV Substation WE***869Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex MULGANNON | Mulgannon: T41 | Wexford |  | 52.3368 | -6.4733
MV/LV Substation WE***870Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.334 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41042 | 0 |  | --> | C15 ex CARRIGLAWN | Carriglawn: T41∥T42 | Wexford |  | 52.341 | -6.4684
MV/LV Substation WE***881 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex SOUTH KING STREET | South King Street: T42 | Francis Street |  | 53.3417 | -6.2609
MV/LV Substation WE***883 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.484 | 11.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C34 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2766 | -9.0772
MV/LV Substation WE***889 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C22 ex ROSS CARBERY | Ross Carbery: T41∥T42 | Dunmanway |  | 51.593 | -9.0749
MV/LV Substation WE***893 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.364 | 9.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.39472 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole: T41∥T42 | Fassaroe |  | 53.1077 | -6.0613
MV/LV Substation WE***893X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.236 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.4224 | 0 |  | --> | C21 ex SCARTEEN | Scarteen: T41∥T42 | Mallow |  | 52.1376 | -8.6504
MV/LV Substation WE***905 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.377 | 0.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =403.7kW. | --> | C16 ex BANTRY | Bantry: T41∥T42 | Ballylicky |  | 51.672 | -9.4738
MV/LV Substation WE***907 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =283kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4183 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin: T41 | Inchicore 110kv |  | 53.3242 | -6.3628
MV/LV Substation WE***908 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =274kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41966 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin: T41 | Inchicore 110kv |  | 53.3232 | -6.3642
MV/LV Substation WE***909 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.174 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.43458 | 0 |  | --> | C25 ex HAROLDS CROSS | Harolds Cross: T101 | Poolbeg |  | 53.3309 | -6.2761
MV/LV Substation WE***919 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount: T42 | Inchicore 110kv |  | 53.3221 | -6.3663
MV/LV Substation WE***926X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.49 | 9.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.06365 | 0.5 | 0 |  | --> | C14 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.8097 | -9.5393
MV/LV Substation WE***929X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =194kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =201kW. | --> | E15 ex BEALISTOWN | Bealistown: T421 | Great Island |  | 52.268 | -6.7558
MV/LV Substation WE***934X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =79kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0038 | 0.069851 | 0 | Constrained,otherwise capacity available =99.3kW. | --> | E20 ex BIRR | Birr: T422 | Dallow |  | 53.0884 | -7.9105
MV/LV Substation WE***940 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.065 | 2.5 |  | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0.09945 | 0 |  | --> | C18 ex KILCOLGAN | Kilcolgan: T42 | Galway 110kv |  | 53.2119 | -8.8963
MV/LV Substation WE***942 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 4.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E16 ex MOHILL | Mohill: T421∥T422 | Carrick On Shannon |  | 53.8617 | -7.9192
MV/LV Substation WE***943 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.354 | 1.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4073 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount: T42 | Inchicore 110kv |  | 53.3233 | -6.3659
MV/LV Substation WE***944 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =189kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.43238 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin: T41 | Inchicore 110kv |  | 53.3216 | -6.3619
MV/LV Substation WE***950 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E17 ex CRANE | Crane: T122 | Crane |  | 52.5408 | -6.3512
MV/LV Substation WE***955 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex TRINITY | Trinity: T101 | Poolbeg |  | 53.3439 | -6.247
MV/LV Substation WE***958X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =292kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0304 | 0.38492 | 0 |  | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7217 | -6.3326
MV/LV Substation WE***968 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 5.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10206 | 0 |  | --> | E17 ex CRANE | Crane: T122 | Crane |  | 52.5296 | -6.3454
MV/LV Substation WE***972 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 1 |  | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0.09975 | 0 |  | --> | C11 ex MULGANNON | Mulgannon: T41 | Wexford |  | 52.3268 | -6.4657
MV/LV Substation WE***984X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =362kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40604 | 0 |  | --> | C13 ex BELGARD | Belgard: T41 | Cookstown |  | 53.291 | -6.3573
MV/LV Substation WE***985X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.125 | 0.1 | Constrained,otherwise capacity available =129kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21105 | 0 |  | --> | C20 ex MULGANNON | Mulgannon: T42 | Wexford |  | 52.3058 | -6.4596
MV/LV Substation WE***992X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =389kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40176 | 0 |  | --> | C15 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8496 | -8.2929
MV/LV Substation WE***994X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.04142 | 0 |  | --> | E14 ex DALTON | Dalton: T421∥T422 | Dalton |  | 53.8373 | -8.9568
MV/LV Substation WE***997Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.135 | 1.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.03325 | 0.17514 | 0 |  | --> | C19 ex TRABEG | Trabeg: T102 | Trabeg |  | 51.8638 | -8.4406
MV/LV Substation WF***306Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 1.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.2kW. | --> | C25 ex ROSBERCON | Rosbercon: T42 | Waterford |  | 52.4006 | -6.948
MV/LV Substation WH***001 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.276 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0304 | 0.38736 | 0 |  | --> | C17 ex GREYSTONES | Greystones: T41 | Fassaroe |  | 53.1417 | -6.0647
MV/LV Substation WH***005 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.428 | 1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C11 ex TRIMMS LANE | Trimms Lane: T41 | Salthill |  | 53.2671 | -9.0676
MV/LV Substation WH***007X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.287 | 9.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0247 | 0.39168 | 0 |  | --> | C20 ex ARTANE | Artane: T102 | Finglas |  | 53.3835 | -6.2219
MV/LV Substation WH***010 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.459 | 1.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex HEADFORD ROAD | Headford Road: T42 | Galway 110kv |  | 53.2725 | -9.0508
MV/LV Substation WH***010 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.136 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.0209 | 0.18798 | 0 |  | --> | C20 ex ATHY | Athy: T102 | Athy |  | 52.9984 | -6.985
MV/LV Substation WH***015X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | C20 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1692 | -6.8948
MV/LV Substation WH***021 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 6.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.8kW. | --> | E17 ex SPRINGS | Springs: T421∥T422 | Dungarvan |  | 52.11 | -7.5969
MV/LV Substation WH***025Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 1.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10095 | 0 |  | --> | C20 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.2998 | -6.5759
MV/LV Substation WH***026 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =485kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0266 | 0.5 | 0 |  | --> | C20 ex BALLYMUN | Ballymun: T42 | Finglas |  | 53.3899 | -6.2502
MV/LV Substation WH***027 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.128 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2112 | 0 |  | --> | C19 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.7248 | -6.3626
MV/LV Substation WH***029 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =106kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0323 | 0.18049 | 0 |  | --> | C19 ex CLONMINCH | Clonminch: T41 | Thornsberry |  | 53.2768 | -7.4821
MV/LV Substation WH***030X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex BREWERY ROAD | Brewery Road: T42 | Carrickmines |  | 53.2865 | -6.2089
MV/LV Substation WH***038 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 8.3 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown: T102 | Carrickmines |  | 53.2796 | -6.3747
MV/LV Substation WH***039 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.348 | 8.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40824 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown: T102 | Carrickmines |  | 53.2788 | -6.3754
MV/LV Substation WH***039X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.13015 | 0.5 | 0 |  | --> | C13 ex MULGANNON | Mulgannon: T41 | Wexford |  | 52.3154 | -6.4728
MV/LV Substation WH***040Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =80kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10315 | 0 |  | --> | C13 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1611 | -6.9176
MV/LV Substation WH***043X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.306 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =414.8kW. | --> | C15 ex BUNDORAN | Bundoran: T41∥T42 | Cathaleens Fall |  | 54.4734 | -8.2786
MV/LV Substation WH***047 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.373 | 8.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4043 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown: T102 | Carrickmines |  | 53.2779 | -6.377
MV/LV Substation WH***062 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.338 | 11.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4098 | 0 |  | --> | C26 ex SALTHILL | Salthill: T102 | Salthill |  | 53.268 | -9.1062
MV/LV Substation WH***066 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =128kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2112 | 0 |  | --> | C11 ex ROSEHILL | Rosehill: T41 | Kilkenny |  | 52.6457 | -7.2647
MV/LV Substation WH***067 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =292kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41692 | 0 |  | --> | C22 ex POPPINTREE | Poppintree: T102 | Finglas |  | 53.3974 | -6.2928
MV/LV Substation WH***072 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.438 | 9.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0228 | 0.5 | 0 |  | --> | C20 ex ARTANE | Artane: T102 | Finglas |  | 53.3821 | -6.2183
MV/LV Substation WH***074 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.263 | 2.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.03895 | 0.5 | 0 |  | --> | C13 ex WHITEHALL | Whitehall: T41 | Finglas |  | 53.375 | -6.2503
MV/LV Substation WH***075 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.305 | 2.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.05225 | 0.5 | 0 |  | --> | C12 ex CARRIGLAWN | Carriglawn: T41∥T42 | Wexford |  | 52.3399 | -6.4632
MV/LV Substation WH***080 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.188 | 7.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.06935 | 0.35954 | 0 |  | --> | C11 ex MILLTOWN (DR) | Milltown (dr): T101 | Poolbeg |  | 53.3118 | -6.245
MV/LV Substation WH***085X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C12 ex KILSARAN | Kilsaran: T42 | Drybridge |  | 53.8993 | -6.3867
MV/LV Substation WH***086Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex SEMPERIT | Semperit: T42 | Grange Castle |  | 53.3319 | -6.3642
MV/LV Substation WH***088X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.291 | 1.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =417.1kW. | --> | E17 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.0697 | -7.2722
MV/LV Substation WH***090Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.047345 | 0 |  | --> | C21 ex BIRR | Birr: T41 | Dallow |  | 53.0826 | -7.8936
MV/LV Substation WH***093 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.216 | 5.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0.4154 | 0 |  | --> | C14 ex DEANSGRANGE | Deansgrange: T42 | Carrickmines |  | 53.2786 | -6.1862
MV/LV Substation WH***095 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.333 | 3.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex CENTRE PARK ROAD | Marina: T106 | Marina |  | 51.8936 | -8.47
MV/LV Substation WH***101X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =53.2kW. | --> | E17 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.0553 | -7.3288
MV/LV Substation WH***102Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =31kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05295 | 0 |  | --> | C31 ex KILBARRY | Kilbarry: T101 | Kilbarry |  | 51.9364 | -8.4537
MV/LV Substation WH***107Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | C22 ex PORTLAOISE | Portlaoise: T42 | Portlaoise |  | 53.0583 | -7.2291
MV/LV Substation WH***110X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 53.0074 | -6.6431
MV/LV Substation WH***118 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.311 | 5.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.02755 | 0.385 | 0 |  | --> | C12 ex TRIMMS LANE | Trimms Lane: T42 | Salthill |  | 53.2651 | -9.0637
MV/LV Substation WH***118Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C13 ex OLDCASTLE | Oldcastle: T41 | Mullingar |  | 53.7685 | -7.1548
MV/LV Substation WH***118Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex POPPINTREE | Poppintree: T102 | Finglas |  | 53.392 | -6.255
MV/LV Substation WH***119X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.334 | 1.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0 | 0 | Constrained,otherwise capacity available =406.4kW. | --> | E17 ex BUNCRANA | Buncrana: T421∥T422 | Trillick |  | 55.0711 | -7.2674
MV/LV Substation WH***121 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =345kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.3947 | 0 |  | --> | C11 ex WOODFORD | Woodford: T41∥T42 | Knockearagh |  | 52.0586 | -9.4774
MV/LV Substation WH***127 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 8.3 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown: T102 | Carrickmines |  | 53.2792 | -6.3782
MV/LV Substation WH***128 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 8.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown: T102 | Carrickmines |  | 53.2804 | -6.3764
MV/LV Substation WH***129X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.099 | 3.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21553 | 0 |  | --> | C18 ex SHERCOCK | Shercock: T41∥T42 | Meath Hill |  | 54.0129 | -6.8873
MV/LV Substation WH***130Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =70kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10469 | 0 |  | --> | C31 ex KILBARRY | Kilbarry: T101 | Kilbarry |  | 51.9387 | -8.4521
MV/LV Substation WH***140X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.125 | 0.1 | Constrained,otherwise capacity available =300kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02755 | 0.38668 | 0 |  | --> | C20 ex MULGANNON | Mulgannon: T42 | Wexford |  | 52.3198 | -6.4796
MV/LV Substation WH***142 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.058 | 4.3 |  | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.1015 | 0 |  | --> | C16 ex LAWLESSTOWN | Lawlesstown: T42 | Doon |  | 52.3578 | -7.7315
MV/LV Substation WH***142Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 1.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10392 | 0 |  | --> | C26 ex KELLS | Kells: T41∥T42 | Navan |  | 53.6864 | -6.8531
MV/LV Substation WH***145 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy: T422 | Athlone |  | 53.6632 | -8.6357
MV/LV Substation WH***145X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.169 | 3.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.0076 | 0.1969 | 0 |  | --> | C20 ex OAKFIELD | Oakfield: T42 | Sligo |  | 54.2739 | -8.5122
MV/LV Substation WH***150Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =26kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00855 | 0.044697 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.5205 | -6.1108
MV/LV Substation WH***152 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.289 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0209 | 0.39538 | 0 |  | --> | C18 ex PALMERSTOWN | Palmerstown: T42 | Finglas |  | 53.3489 | -6.369
MV/LV Substation WH***152Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.025 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.049845 | 0 |  | --> | C16 ex JOHNSTOWN | Johnstown: T42 | Kilteel |  | 53.2502 | -6.5906
MV/LV Substation WH***164Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052037 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 53.0047 | -6.6568
MV/LV Substation WH***172Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.247 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0665 | 0.35376 | 0 |  | --> | C12 ex MORNINGTON ROAD | Mornington Road: T42 | Drybridge |  | 53.7104 | -6.3273
MV/LV Substation WH***178 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.25 | 4.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.4173 | 0 |  | --> | C11 ex BALLYRAINE | Ballyraine: T41∥T42 | Letterkenny |  | 54.9589 | -7.7224
MV/LV Substation WH***179 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 9.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C19 ex MIDLETON | Midleton: T101 | Midleton |  | 51.9463 | -8.2526
MV/LV Substation WH***181X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 5.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | E11 ex ARDNAREE | Ardnaree: T421 | Moy |  | 54.1072 | -9.0681
MV/LV Substation WH***182X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00665 | 0.043795 | 0 |  | --> | C17 ex TYMON | Tymon: T41 | Cookstown |  | 53.3059 | -6.3755
MV/LV Substation WH***204Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =144kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20876 | 0 |  | --> | C21 ex KILBARRY | Kilbarry: T101 | Kilbarry |  | 51.9122 | -8.474
MV/LV Substation WH***209Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.05 | 0.1 | Constrained,otherwise capacity available =161kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20614 | 0 |  | --> | C18 ex COOLMINE | Coolmine: T42 | Finglas |  | 53.3946 | -6.3979
MV/LV Substation WH***214 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0703 | 0.5 | 0 |  | --> | C18 ex GARVILLE AVENUE | Garville Avenue: T42 | Milltown (dr) |  | 53.3122 | -6.2822
MV/LV Substation WH***214X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.083 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.43564 | 0 |  | --> | C11 ex LIFFEY VALLEY | Liffey Valley: T41 | Inchicore 110kv |  | 53.3426 | -6.3914
MV/LV Substation WH***215 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 2.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.046885 | 0 |  | --> | E13 ex AGHADA | Aghada: T721 | N/A |  | 51.8227 | -8.2356
MV/LV Substation WH***235 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.054 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1071 | 0 |  | --> | C12 ex SCARIFF | Scariff: T42 | Ennis |  | 52.949 | -8.3751
MV/LV Substation WH***240Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C14 ex DRYBRIDGE | Drybridge: T42 | Drybridge |  | 53.7938 | -6.4217
MV/LV Substation WH***241Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.133 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.01615 | 0.19344 | 0 |  | --> | C12 ex MORNINGTON ROAD | Mornington Road: T42 | Drybridge |  | 53.709 | -6.3232
MV/LV Substation WH***243 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C12 ex SCARIFF | Scariff: T42 | Ennis |  | 52.9437 | -8.4046
MV/LV Substation WH***245 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C18 ex WOODFORD | Woodford: T41∥T42 | Knockearagh |  | 52.0537 | -9.4704
MV/LV Substation WH***249Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 2.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10377 | 0 |  | --> | E13 ex AGHADA | Aghada: T721 | N/A |  | 51.8123 | -8.186
MV/LV Substation WH***253Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 5.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown: T41 | Cookstown |  | 53.2784 | -6.3803
MV/LV Substation WH***255Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =196kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20064 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9955 | -6.6481
MV/LV Substation WH***261 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.19 | 1.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.02185 | 0.40924 | 0 |  | --> | C22 ex KIMMAGE | Kimmage: T42 | Inchicore 110kv |  | 53.3059 | -6.3205
MV/LV Substation WH***263Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7291 | -6.3424
MV/LV Substation WH***269X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.365 | 5.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40556 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown: T41 | Cookstown |  | 53.2803 | -6.3838
MV/LV Substation WH***271Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C30 ex KINSALE | Kinsale: T41∥T42 | Bandon |  | 51.6451 | -8.574
MV/LV Substation WH***274Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.16 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.2033 | 0 |  | --> | E20 ex LONGFORD | Longford: T422 | Richmond |  | 53.7406 | -7.7984
MV/LV Substation WH***284 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.31 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.39814 | 0 |  | --> | C13 ex PALMERSTOWN | Palmerstown: T41 | Finglas |  | 53.3499 | -6.3746
MV/LV Substation WH***293 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =319kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01615 | 0.39576 | 0 |  | --> | C18 ex CAHERDAVIN | Caherdavin: T42 | Ardnacrusha |  | 52.6765 | -8.6663
MV/LV Substation WH***317 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.05 | 0.1 | Constrained,otherwise capacity available =286kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41284 | 0 |  | --> | C18 ex COOLMINE | Coolmine: T42 | Finglas |  | 53.3898 | -6.4034
MV/LV Substation WH***320 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 1.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10064 | 0 |  | --> | E16 ex BALLYDEHOB | Ballydehob: T421 | Dunmanway |  | 51.4644 | -9.7537
MV/LV Substation WH***320Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C18 ex ROSCOMMON | Roscommon: T42 | Lanesboro |  | 53.5497 | -8.0693
MV/LV Substation WH***329Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =95kVA. | --> | 0.19 | 0 | 0 | 0 | 0.08265 | 0.12912 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.7011 | -6.2675
MV/LV Substation WH***330Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =69kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.20891 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.7026 | -6.2656
MV/LV Substation WH***331 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.068 | 2.2 |  | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.09999 | 0 |  | --> | C15 ex RANDALSTOWN | Randalstown: T41 | Navan |  | 53.6748 | -6.7588
MV/LV Substation WH***331Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =73kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0323 | 0.18533 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.7035 | -6.2652
MV/LV Substation WH***364 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =473kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.44613 | 0 | Constrained,otherwise capacity available =500kW. | --> | C24 ex BALLYCOOLIN | Ballycoolin: T42 | Finglas |  | 53.3992 | -6.399
MV/LV Substation WH***366 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 5.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10237 | 0 |  | --> | C18 ex ABBEYLAND | Abbeyland: T42 | Navan |  | 53.6594 | -6.7133
MV/LV Substation WH***371 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.3kW. | --> | C15 ex KILCLOHER | Kilcloher: T42 | Dungarvan |  | 52.1102 | -7.7682
MV/LV Substation WH***374 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =278kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.41506 | 0 |  | --> | C24 ex BALLYCOOLIN | Ballycoolin: T42 | Finglas |  | 53.3974 | -6.3949
MV/LV Substation WH***374Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 5.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E16 ex WHITECHURCH | Whitechurch: T422 | Kilbarry |  | 51.9782 | -8.5044
MV/LV Substation WH***378 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0057 | 0.44613 | 0 | Constrained,otherwise capacity available =500kW. | --> | C24 ex BALLYCOOLIN | Ballycoolin: T42 | Finglas |  | 53.3969 | -6.3979
MV/LV Substation WH***399Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.266 | 4.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.41488 | 0 |  | --> | C15 ex CASTLEKNOCK | Castleknock: T41∥T42 | Finglas |  | 53.368 | -6.3633
MV/LV Substation WH***4006 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =137kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20483 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.151 | -6.7792
MV/LV Substation WH***4008 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.4kW. | --> | C15 ex MILLTOWN MALBAY | Milltown Malbay: T42 | Tullabrack |  | 52.8034 | -9.4793
MV/LV Substation WH***400Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.489 | 4.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0133 | 0.44613 | 0 | Constrained,otherwise capacity available =500kW. | --> | C15 ex CASTLEKNOCK | Castleknock: T41∥T42 | Finglas |  | 53.3678 | -6.361
MV/LV Substation WH***402 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =140kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20438 | 0 |  | --> | C24 ex BALLYCOOLIN | Ballycoolin: T42 | Finglas |  | 53.3957 | -6.3987
MV/LV Substation WH***4024 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C16 ex STICKILLEN | Stickillen: T41∥T42 | Drybridge |  | 53.7985 | -6.4805
MV/LV Substation WH***4028 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.198 | 5.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20032 | 0 |  | --> | E18 ex WHITECHURCH | Whitechurch: T422 | Kilbarry |  | 51.984 | -8.5335
MV/LV Substation WH***4054 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =339kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40964 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.5138 | -6.127
MV/LV Substation WH***4079 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex BALLYBODEN | Ballyboden: T42 | Cookstown |  | 53.275 | -6.3152
MV/LV Substation WH***4094 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BALLYBODEN | Ballyboden: T41 | Cookstown |  | 53.2724 | -6.3157
MV/LV Substation WH***4095 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BALLYBODEN | Ballyboden: T41 | Cookstown |  | 53.2717 | -6.3117
MV/LV Substation WH***4127 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BALLYBODEN | Ballyboden: T41 | Cookstown |  | 53.2731 | -6.3163
MV/LV Substation WH***4174 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C20 ex CAHIR | Cahir: T42 | Cahir |  | 52.36 | -7.9863
MV/LV Substation WH***4197 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =305kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41492 | 0 |  | --> | C15 ex MORRISTOWN | Morristown: T41∥T42 | Newbridge |  | 53.1892 | -6.8112
MV/LV Substation WH***4209 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =370kVA. | --> | 0.38 | 0 | 0 | 0 | 0.04275 | 0.35978 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.7011 | -6.2698
MV/LV Substation WH***4235 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C20 ex KNOCKMULLEN | Knockmullen: T42 | Great Island |  | 52.3242 | -6.9789
MV/LV Substation WH***425 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.369 | 11.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.39894 | 0 |  | --> | C26 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2685 | -9.1046
MV/LV Substation WH***425Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00285 | 0.048265 | 0 |  | --> | C20 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.2988 | -6.6034
MV/LV Substation WH***4287 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C11 ex PORTARLINGTON | Portarlington: T41∥T42 | Portlaoise |  | 53.2164 | -7.1363
MV/LV Substation WH***4296 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.01425 | 0.5 | 0 |  | --> | C17 ex NAAS | Naas: T41 | Newbridge |  | 53.2096 | -6.6753
MV/LV Substation WH***4297 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =477kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.01615 | 0.5 | 0 |  | --> | C17 ex NAAS | Naas: T41 | Newbridge |  | 53.2096 | -6.6735
MV/LV Substation WH***4309 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 10.8 |  | --> | 0.95 | 0 | 0 | 0 | 0.0076 | 0.5 | 0 |  | --> | C23 ex PELLETSTOWN | Pelletstown: T101 | Finglas |  | 53.3713 | -6.3822
MV/LV Substation WH***4310 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 10.8 |  | --> | 0.95 | 0 | 0 | 0 | 0.01235 | 0.5 | 0 |  | --> | C23 ex PELLETSTOWN | Pelletstown: T101 | Finglas |  | 53.3713 | -6.3822
MV/LV Substation WH***4371 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.191 | 2.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =201.4kW. | --> | C19 ex NEWCASTLEWEST | Newcastlewest: T41∥T42 | Rathkeale |  | 52.3469 | -9.0064
MV/LV Substation WH***440X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 5.3 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex WOLFE TONE STREET | Wolfe Tone Street: T101 | Finglas |  | 53.3465 | -6.2692
MV/LV Substation WH***451Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E16 ex WHITECHURCH | Whitechurch: T422 | Kilbarry |  | 51.983 | -8.5101
MV/LV Substation WH***463X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.5186 | -6.1196
MV/LV Substation WH***471X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.18 | 5.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20318 | 0 |  | --> | C18 ex ABBEYLAND | Abbeyland: T42 | Navan |  | 53.6601 | -6.7234
MV/LV Substation WH***472Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.131 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.02185 | 0.18774 | 0 |  | --> | C15 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3265 | -6.4718
MV/LV Substation WH***490X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.163 | 4.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.01045 | 0.19483 | 0 |  | --> | E18 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.2772 | -6.3949
MV/LV Substation WH***506 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.318 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0361 | 0.3749 | 0 |  | --> | C18 ex BALLYBODEN | Ballyboden: T42 | Cookstown |  | 53.2845 | -6.2885
MV/LV Substation WH***509Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =172kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01425 | 0.18943 | 0 |  | --> | C23 ex GORESBRIDGE | Goresbridge: T41∥T42 | Kilkenny |  | 52.6803 | -7.0283
MV/LV Substation WH***517 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.258 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0722 | 0.3461 | 0 |  | --> | C18 ex BALLYBODEN | Ballyboden: T42 | Cookstown |  | 53.2824 | -6.2884
MV/LV Substation WH***540Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.324 | 4.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.01615 | 0.39498 | 0 |  | --> | C15 ex CASTLEKNOCK | Castleknock: T41∥T42 | Finglas |  | 53.3678 | -6.3578
MV/LV Substation WH***541Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.178 | 4.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0228 | 0.17949 | 0 |  | --> | C15 ex CASTLEKNOCK | Castleknock: T41∥T42 | Finglas |  | 53.3664 | -6.3533
MV/LV Substation WH***576X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.285 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.40798 | 0 |  | --> | C17 ex PALMERSTOWN | Palmerstown: T41 | Finglas |  | 53.3447 | -6.3824
MV/LV Substation WH***577X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.111 | 2.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20975 | 0 |  | --> | C17 ex PALMERSTOWN | Palmerstown: T41 | Finglas |  | 53.344 | -6.3813
MV/LV Substation WH***582Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.121 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.019 | 0.19225 | 0 |  | --> | C12 ex MORNINGTON ROAD | Mornington Road: T42 | Drybridge |  | 53.7087 | -6.3193
MV/LV Substation WH***599Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =87kVA. | --> | 0.095 | 0 | 0 | 0 | 0.00285 | 0.09906 | 0 |  | --> | E16 ex BEALISTOWN | Bealistown: | N/A |  | 52.2517 | -6.9632
MV/LV Substation WH***600 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10284 | 0 |  | --> | C15 ex TRIM | Trim: T41∥T42 | Navan |  | 53.562 | -6.7948
MV/LV Substation WH***610Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.327 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41152 | 0 |  | --> | C12 ex MORNINGTON ROAD | Mornington Road: T42 | Drybridge |  | 53.7094 | -6.3292
MV/LV Substation WH***612X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10064 | 0 |  | --> | E16 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.6641 | -6.2726
MV/LV Substation WH***633 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 1.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052647 | 0 |  | --> | E18 ex GARRANACANTY | Garranacanty: T422 | Tipperary |  | 52.5097 | -8.1757
MV/LV Substation WH***654 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.0531 | 0 |  | --> | C12 ex SCARIFF | Scariff: T42 | Ennis |  | 52.9458 | -8.3725
MV/LV Substation WH***654X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =97kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10048 | 0 |  | --> | C24 ex MACETOWN | Macetown: T102 | Macetown |  | 53.4702 | -6.4148
MV/LV Substation WH***654X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.133 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21044 | 0 |  | --> | C12 ex CASHEL | Cashel: T42 | Cahir |  | 52.5068 | -7.8921
MV/LV Substation WH***660Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =112kVA. | --> | 0.19 | 0 | 0 | 0 | 0.02375 | 0.1886 | 0 |  | --> | C15 ex BLAKE | Blake: T41∥T42 | Blake |  | 53.2847 | -6.8615
MV/LV Substation WH***665 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C12 ex SCARIFF | Scariff: T42 | Ennis |  | 52.9507 | -8.3738
MV/LV Substation WH***665Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =177kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =193.6kW. | --> | C17 ex ROSCREA | Roscrea: T41 | Ikerrin |  | 52.9464 | -7.7863
MV/LV Substation WH***676X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 9.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10222 | 0 |  | --> | C21 ex ENNIS | Ennis: T101 | Ennis |  | 52.8976 | -8.9385
MV/LV Substation WH***687 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E18 ex BUNCLODY | Bunclody: T421∥T422 | Crane |  | 52.5713 | -6.7194
MV/LV Substation WH***691Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0475 | 0.35002 | 0 |  | --> | C19 ex CLONARD | Clonard: T41∥T42 | Wexford |  | 52.3243 | -6.5007
MV/LV Substation WH***691Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =280kVA. | --> | 0.38 | 0 | 0 | 0 | 0.1045 | 0.30876 | 0 |  | --> | E21 ex BALTRASNA | Baltrasna: T121 | Baltrasna |  | 53.5074 | -6.3856
MV/LV Substation WH***692Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =454kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.01235 | 0.5 | 0 |  | --> | C21 ex PORTARLINGTON | Portarlington: T43 | Blake |  | 53.1509 | -7.1864
MV/LV Substation WH***698X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.045265 | 0 |  | --> | C20 ex MULGANNON | Mulgannon: T42 | Wexford |  | 52.3183 | -6.479
MV/LV Substation WH***707 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.023 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.04414 | 0 |  | --> | C13 ex SANDYFORD | Sandyford: T41 | Carrickmines |  | 53.261 | -6.2943
MV/LV Substation WH***707Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =123kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21195 | 0 |  | --> | E13 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9338 | -6.6963
MV/LV Substation WH***708X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 2.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20176 | 0 |  | --> | E18 ex NEWPORT | Newport: T421 | Carrowbeg |  | 53.8869 | -9.5501
MV/LV Substation WH***717 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex KIMMAGE | Kimmage: T41 | Inchicore 110kv |  | 53.3092 | -6.3123
MV/LV Substation WH***727X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C18 ex DEERPARK | Deerpark: T41∥T42 | Ballydine |  | 52.3732 | -7.3805
MV/LV Substation WH***734X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.322 | 3.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =412.3kW. | --> | C13 ex TURLOUGH ROAD | Turlough Road: T41∥T42 | Castlebar |  | 53.8675 | -9.2832
MV/LV Substation WH***737 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.395 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4008 | 0 |  | --> | C11 ex WHITEHALL | Whitehall: T41 | Finglas |  | 53.3769 | -6.2511
MV/LV Substation WH***739 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.047107 | 0 |  | --> | E20 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.5185 | -6.1282
MV/LV Substation WH***742Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =285kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0285 | 0.38798 | 0 |  | --> | C21 ex KILMONEY | Kilmoney: T41∥T42 | Trabeg |  | 51.8033 | -8.4054
MV/LV Substation WH***750Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =145kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20861 | 0 |  | --> | C14 ex GORESBRIDGE | Goresbridge: T41∥T42 | Kilkenny |  | 52.6045 | -6.9228
MV/LV Substation WH***763X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =29kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05325 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 53.0121 | -6.662
MV/LV Substation WH***765X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =287kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00095 | 0.41668 | 0 |  | --> | C16 ex TOGHER | Togher: T42 | Trabeg |  | 51.8745 | -8.5066
MV/LV Substation WH***768Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00665 | 0.043637 | 0 |  | --> | E14 ex BLESSINGTON | Blessington: T422 | Kilteel |  | 53.1124 | -6.6196
MV/LV Substation WH***784 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.1kW. | --> | C15 ex KILCLOHER | Kilcloher: T42 | Dungarvan |  | 52.1109 | -7.7531
MV/LV Substation WH***786 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C15 ex KILCLOHER | Kilcloher: T42 | Dungarvan |  | 52.1084 | -7.7459
MV/LV Substation WH***788 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.285 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0304 | 0.38598 | 0 |  | --> | C19 ex BRAY | Bray: T41 | Fassaroe |  | 53.1901 | -6.114
MV/LV Substation WH***791X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 5.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10174 | 0 |  | --> | C18 ex ABBEYLAND | Abbeyland: T42 | Navan |  | 53.6595 | -6.7205
MV/LV Substation WH***794Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =123kVA. | --> | 0.19 | 0 | 0 | 0 | 0.019 | 0.19195 | 0 |  | --> | C21 ex PORTARLINGTON | Portarlington: T43 | Blake |  | 53.1526 | -7.1867
MV/LV Substation WH***805Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 2.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | C19 ex NEWCASTLEWEST | Newcastlewest: T41∥T42 | Rathkeale |  | 52.3372 | -9.0096
MV/LV Substation WH***812 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.277 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.0456 | 0.3712 | 0 |  | --> | C18 ex DUNDRUM | Dundrum: T42 | Blackrock |  | 53.3031 | -6.2348
MV/LV Substation WH***820Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1788 | -6.7981
MV/LV Substation WH***821Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1788 | -6.7982
MV/LV Substation WH***854X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 5.3 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex WOLFE TONE STREET | Wolfe Tone Street: T101 | Finglas |  | 53.3466 | -6.2692
MV/LV Substation WH***855Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.125 | 0.1 | Constrained,otherwise capacity available =295kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0323 | 0.38246 | 0 |  | --> | C20 ex MULGANNON | Mulgannon: T42 | Wexford |  | 52.3215 | -6.4796
MV/LV Substation WH***864Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.04032 | 0 |  | --> | E15 ex JENKINSTOWN | Jenkinstown: T421∥T422 | Dundalk |  | 54.0397 | -6.3946
MV/LV Substation WH***872 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 3.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10299 | 0 |  | --> | C18 ex TRAMORE | Tramore: T42 | Butlerstown |  | 52.2329 | -7.2158
MV/LV Substation WH***873 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 9.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole: T41∥T42 | Fassaroe |  | 53.1102 | -6.0642
MV/LV Substation WH***875X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C23 ex KILKEE | Kilkee: T41 | Tullabrack |  | 52.6477 | -9.6727
MV/LV Substation WH***883 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =75kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0.09792 | 0 |  | --> | C28 ex CLAREGALWAY | Claregalway: T42 | Galway 110kv |  | 53.3255 | -8.9674
MV/LV Substation WH***892 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.145 | 10.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.20561 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown: T101 | Carrickmines |  | 53.2847 | -6.3914
MV/LV Substation WH***901 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C16 ex STICKILLEN | Stickillen: T41∥T42 | Drybridge |  | 53.8108 | -6.461
MV/LV Substation WH***909Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.162 | 7.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20199 | 0 |  | --> | C23 ex ATHY | Athy: T101 | Athy |  | 52.9459 | -7.0364
MV/LV Substation WH***931X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.157 | 0.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =206.8kW. | --> | C16 ex GARRYSPILLANE | Garryspillane: T41 | Tipperary |  | 52.3296 | -8.4728
MV/LV Substation WH***931X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.366 | 4.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4054 | 0 |  | --> | C12 ex TYMON | Tymon: T42 | Cookstown |  | 53.3082 | -6.3546
MV/LV Substation WH***932X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.148 | 0.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20815 | 0 |  | --> | C17 ex KYLEERAGH | Kyleeragh: T41 | Nenagh |  | 52.9932 | -8.1236
MV/LV Substation WH***955Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =98kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10032 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9947 | -6.6472
MV/LV Substation WH***957 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C16 ex STICKILLEN | Stickillen: T41∥T42 | Drybridge |  | 53.8064 | -6.4627
MV/LV Substation WH***985 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =92kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0 | 0 | Constrained,otherwise capacity available =95.3kW. | --> | C11 ex TEMPLEMORE | Templemore: T41 | Ikerrin |  | 52.7761 | -7.8399
MV/LV Substation WI***002 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.267 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42072 | 0 |  | --> | C11 ex SMEARLA | Smearla: T41 | Trien |  | 52.4475 | -9.4865
MV/LV Substation WI***002 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C17 ex CRANMORE | Cranmore: T41∥T42 | Sligo |  | 54.2719 | -8.478
MV/LV Substation WI***003Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.357 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40682 | 0 |  | --> | C16 ex MANOR STREET | Manor Street: T42 | Waterford |  | 52.2591 | -7.1045
MV/LV Substation WI***004Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.2015 | -6.7537
MV/LV Substation WI***007 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.274 | 7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.41166 | 0 |  | --> | C12 ex ARDGEEHA | Ardgeeha: T41∥T42 | Doon |  | 52.3664 | -7.6979
MV/LV Substation WI***010 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.13 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2109 | 0 |  | --> | C24 ex BAILIEBORO | Bailieboro: T41∥T42 | Meath Hill |  | 53.9155 | -6.9737
MV/LV Substation WI***013 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 7.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0.02375 | 0.5 | 0 |  | --> | C17 ex BALLYMUN | Ballymun: T41 | Finglas |  | 53.3903 | -6.2695
MV/LV Substation WI***019Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.112 | 2 |  | --> | 0.19 | 0 | 0 | 0 | 0.02375 | 0.1886 | 0 |  | --> | C17 ex GRANGE (SR) | Grange (sr): T41∥T42 | Butlerstown |  | 52.242 | -7.0967
MV/LV Substation WI***030 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.404 | 1.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0.01425 | 0.5 | 0 |  | --> | C19 ex DUNDRUM | Dundrum: T41 | Blackrock |  | 53.3012 | -6.2451
MV/LV Substation WI***034 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.067 | 4.2 |  | --> | 0.095 | 0 | 0 | 0 | 0.0114 | 0 | 0 | Constrained,otherwise capacity available =93.1kW. | --> | C16 ex BUNDORAN | Bundoran: T41∥T42 | Cathaleens Fall |  | 54.4974 | -8.2091
MV/LV Substation WI***034 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.197 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20048 | 0 |  | --> | E19 ex TULLOW | Tullow: T421 | Carlow |  | 52.8007 | -6.6837
MV/LV Substation WI***035 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.395 | 0.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4008 | 0 |  | --> | C18 ex KNOCKMULLEN | Knockmullen: T42 | Great Island |  | 52.3904 | -6.9432
MV/LV Substation WI***040X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | C11 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6504 | -8.1407
MV/LV Substation WI***041 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0209 | 0.5 | 0 |  | --> | C12 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8557 | -8.2828
MV/LV Substation WI***041 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.473 | 0.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C18 ex STICKILLEN | Stickillen: T41∥T42 | Drybridge |  | 53.8527 | -6.5366
MV/LV Substation WI***044 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.021 | 5.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.22068 | 0 |  | --> | C13 ex MCDONAGH | Mcdonagh: T41 | Kilkenny |  | 52.655 | -7.2402
MV/LV Substation WI***058 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0456 | 0.5 | 0 |  | --> | C19 ex DUNDALK | Dundalk: T41 | Dundalk |  | 53.9985 | -6.4259
MV/LV Substation WI***065X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 26.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | E12 ex WEXFORD | Wexford: T121∥T122 | Wexford |  | 52.3738 | -6.6533
MV/LV Substation WI***074 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =215kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02565 | 0.40154 | 0 |  | --> | C22 ex POPPINTREE | Poppintree: T102 | Finglas |  | 53.3922 | -6.2787
MV/LV Substation WI***077Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.193 | 1.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.19812 | 0 |  | --> | E12 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.2354 | -7.0747
MV/LV Substation WI***081 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.245 | 11.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0304 | 0.39206 | 0 |  | --> | C20 ex BALLYBEG | Ballybeg: T102 | Carrickmines |  | 52.9751 | -6.0474
MV/LV Substation WI***085 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.056 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1068 | 0 |  | --> | C11 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.7188 | -6.3647
MV/LV Substation WI***086X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00285 | 0.049495 | 0 |  | --> | E15 ex MOHILL | Mohill: T421∥T422 | Carrick On Shannon |  | 54.0521 | -7.7952
MV/LV Substation WI***088 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =129kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20705 | 0 |  | --> | C11 ex GARDEN CITY | Garden City: T41∥T42 | Arklow |  | 52.6822 | -6.2968
MV/LV Substation WI***097X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C12 ex CHARLESTOWN | Charlestown: T41 | Tonroe |  | 53.9557 | -8.7936
MV/LV Substation WI***109Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.381 | 3.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40304 | 0 |  | --> | C18 ex CASHEL | Cashel: T42 | Cahir |  | 52.5117 | -7.8015
MV/LV Substation WI***122 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.344 | 11.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0171 | 0.39086 | 0 |  | --> | C20 ex BALLYBEG | Ballybeg: T102 | Carrickmines |  | 52.9745 | -6.0447
MV/LV Substation WI***126Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin: T41 | Inchicore 110kv |  | 53.3253 | -6.3623
MV/LV Substation WI***134 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.299 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41584 | 0 |  | --> | C11 ex TRABEG | Trabeg: T102 | Trabeg |  | 51.8911 | -8.4682
MV/LV Substation WI***136X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =142kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20407 | 0 |  | --> | C20 ex DENNEHYS CROSS | Dennehys Cross: T42 | Trabeg |  | 51.8792 | -8.5049
MV/LV Substation WI***139Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.355 | 2.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =402.1kW. | --> | C15 ex NEWCASTLEWEST | Newcastlewest: T41∥T42 | Rathkeale |  | 52.4467 | -9.0447
MV/LV Substation WI***140Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.327 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0209 | 0.38952 | 0 |  | --> | C12 ex MONEYCOOLEY | Moneycooley: T42 | Griffinrath |  | 53.346 | -6.5487
MV/LV Substation WI***149X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 2.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex SHERIFF STREET | Sheriff Street: T41 | Francis Street |  | 53.3455 | -6.2445
MV/LV Substation WI***153Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =143kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0152 | 0.19292 | 0 |  | --> | C22 ex MIDLETON | Midleton: T102 | Midleton |  | 51.9251 | -8.1834
MV/LV Substation WI***154 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.034 | 0.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =110kW. | --> | C18 ex ATHBOY | Athboy: T42 | Navan |  | 53.619 | -6.9253
MV/LV Substation WI***157X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.9 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex SHERIFF STREET | Sheriff Street: T41 | Francis Street |  | 53.3446 | -6.2431
MV/LV Substation WI***163X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.185 | 4.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.19739 | 0 |  | --> | C13 ex DUNDALK | Dundalk: T42 | Dundalk |  | 53.9978 | -6.4222
MV/LV Substation WI***166Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.275 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.02945 | 0.38852 | 0 |  | --> | E21 ex CURRALEIGH | Curraleigh: T421∥T422 | Kilbarry |  | 51.9287 | -8.5907
MV/LV Substation WI***168 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =134kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.42638 | 0 |  | --> | C13 ex TOGHER | Togher: T41 | Trabeg |  | 51.8829 | -8.5066
MV/LV Substation WI***169 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.209 | 0.2 | Constrained,otherwise capacity available =309kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01995 | 0.3933 | 0 |  | --> | C21 ex BISHOPSTOWN | Bishopstown: T41 | Kilbarry |  | 51.8849 | -8.5098
MV/LV Substation WI***169 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =128kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.44126 | 0 |  | --> | C12 ex ROCHES STREET | Roches Street: T42 | Limerick |  | 52.6617 | -8.6232
MV/LV Substation WI***170 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.167 | 0.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20521 | 0 |  | --> | C21 ex BISHOPSTOWN | Bishopstown: T41 | Kilbarry |  | 51.8832 | -8.5139
MV/LV Substation WI***170Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.149 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.208 | 0 |  | --> | C12 ex CASHEL | Cashel: T42 | Cahir |  | 52.5058 | -7.8956
MV/LV Substation WI***171 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.141 | 2.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.0152 | 0.19322 | 0 |  | --> | C20 ex DUNDRUM | Dundrum: T42 | Blackrock |  | 53.2844 | -6.2396
MV/LV Substation WI***175Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =329kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4112 | 0 |  | --> | C17 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4143 | -6.412
MV/LV Substation WI***186Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.334 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.40542 | 0 |  | --> | C11 ex MULGANNON | Mulgannon: T41 | Wexford |  | 52.3372 | -6.4765
MV/LV Substation WI***189 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.324 | 11.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.39598 | 0 |  | --> | C26 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2662 | -9.1092
MV/LV Substation WI***189 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.256 | 5.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.03895 | 0.3814 | 0 |  | --> | C20 ex UNIDARE | Unidare: T42 | Finglas |  | 53.3939 | -6.2825
MV/LV Substation WI***193 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 8.1 |  | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0.09416 | 0 |  | --> | C25 ex MULLINGAR | Mullingar: T101 | Mullingar |  | 53.5897 | -7.5306
MV/LV Substation WI***193Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.303 | 5.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.02565 | 0.38822 | 0 |  | --> | C22 ex BALLINCOLLIG | Ballincollig: T42 | Kilbarry |  | 51.883 | -8.6124
MV/LV Substation WI***194 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.321 | 1.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.01425 | 0.5 | 0 |  | --> | C16 ex KIMMAGE | Kimmage: T42 | Inchicore 110kv |  | 53.3249 | -6.3098
MV/LV Substation WI***197X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex MILLTOWN (DR) | Milltown (dr): T102 | Inchicore 110kv |  | 53.3013 | -6.2454
MV/LV Substation WI***200Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =138kVA. | --> | 0.19 | 0 | 0 | 0 | 0.019 | 0.18968 | 0 |  | --> | C22 ex MIDLETON | Midleton: T102 | Midleton |  | 51.9266 | -8.1853
MV/LV Substation WI***201Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 0.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10484 | 0 |  | --> | C17 ex MONEYCOOLEY | Moneycooley: T41 | Griffinrath |  | 53.4362 | -6.5331
MV/LV Substation WI***207X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.358 | 4.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.38766 | 0 |  | --> | E15 ex MOHILL | Mohill: T421∥T422 | Carrick On Shannon |  | 54.0504 | -7.7919
MV/LV Substation WI***209X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.017 | 5.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.050012 | 0 |  | --> | E12 ex CLARA | Clara: T422 | Thornsberry |  | 53.369 | -7.48
MV/LV Substation WI***209Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =336kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.39812 | 0 |  | --> | C20 ex GARRYOWEN | Garryowen: T42 | Limerick |  | 52.6455 | -8.5907
MV/LV Substation WI***211Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =263kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.40634 | 0 |  | --> | C23 ex POLLERTON | Pollerton: T41 | Carlow |  | 52.8268 | -6.9067
MV/LV Substation WI***216X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.147 | 1.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.1983 | 0 |  | --> | E12 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.2377 | -7.0957
MV/LV Substation WI***217Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.37 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.39478 | 0 |  | --> | C13 ex SMEARLA | Smearla: T41 | Trien |  | 52.4496 | -9.4802
MV/LV Substation WI***221X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.318 | 8.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.4069 | 0 |  | --> | C14 ex GORTLEE | Gortlee: T41∥T42 | Letterkenny |  | 54.9666 | -7.7582
MV/LV Substation WI***223 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.347 | 2.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0.06555 | 0.5 | 0 |  | --> | C16 ex DODDER ROAD | Dodder Road: T42 | Milltown (dr) |  | 53.2966 | -6.2608
MV/LV Substation WI***225Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.327 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41152 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.3336 | -6.5275
MV/LV Substation WI***226Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.299 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0209 | 0.39384 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.3354 | -6.5295
MV/LV Substation WI***228Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.279 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.4089 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.3352 | -6.5262
MV/LV Substation WI***230 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.269 | 3.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C14 ex CRUMLIN | Crumlin: T42 | Inchicore 110kv |  | 53.3199 | -6.3149
MV/LV Substation WI***233Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.275 | 0.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41452 | 0 |  | --> | C15 ex RIVERSTOWN | Riverstown: T41∥T42 | Kilbarry |  | 51.9325 | -8.3796
MV/LV Substation WI***238X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =276kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.40036 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin: T41 | Inchicore 110kv |  | 53.3124 | -6.4012
MV/LV Substation WI***247Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 8.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C25 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9864 | -6.0531
MV/LV Substation WI***256Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.357 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40682 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.3363 | -6.5299
MV/LV Substation WI***261 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =121kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0076 | 0.20425 | 0 |  | --> | E13 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9084 | -6.8454
MV/LV Substation WI***261X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.242 | 13.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.4045 | 0 |  | --> | C36 ex CASTLEVIEW | Castleview: T102 | Castleview |  | 51.9008 | -8.346
MV/LV Substation WI***267 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 150 kVA :Pole Substation | 0.15 | --> | 0.15 | 0.142 | 2.7 |  | --> | 0.1425 | 0 | 0 | 0 | 0.00475 | 0.14628 | 0 |  | --> | C20 ex SUTTON | Sutton: T42 | Grange (dr) |  | 53.3689 | -6.0669
MV/LV Substation WI***274Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E12 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.2365 | -7.0837
MV/LV Substation WI***280 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.364 | 5.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40572 | 0 |  | --> | C26 ex GALWAY 110KV | Galway 110kv: T102 | Galway 110kv |  | 53.2903 | -9.011
MV/LV Substation WI***280Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 0.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | E14 ex RANDALSTOWN | Randalstown: T422 | Navan |  | 53.7324 | -6.7105
MV/LV Substation WI***281Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.068 | 0.5 |  | --> | 0.095 | 0 | 0 | 0 | 0.01045 | 0.09399 | 0 |  | --> | E14 ex RANDALSTOWN | Randalstown: T422 | Navan |  | 53.7338 | -6.712
MV/LV Substation WI***283 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.29 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.03705 | 0.37822 | 0 |  | --> | C19 ex SWORDS | Swords: T41 | Glasmore |  | 53.4598 | -6.2305
MV/LV Substation WI***287Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.179 | 1.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20333 | 0 |  | --> | E11 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.2601 | -7.0257
MV/LV Substation WI***289X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.153 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20738 | 0 |  | --> | E18 ex EDGEWORTHSTOWN | Edgeworthstown: T421∥T422 | Richmond |  | 53.6584 | -7.5215
MV/LV Substation WI***292X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0057 | 0.5 | 0 |  | --> | C19 ex KILMORE | Kilmore: T101 | Finglas |  | 53.4066 | -6.2222
MV/LV Substation WI***319 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 2.7 |  | --> | 0.095 | 0 | 0 | 0 | 0.019 | 0.08253 | 0 |  | --> | C20 ex SUTTON | Sutton: T42 | Grange (dr) |  | 53.3691 | -6.068
MV/LV Substation WI***320Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.363 | 7.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40588 | 0 |  | --> | C12 ex GARRYCASTLE | Garrycastle: T42 | Athlone |  | 53.4119 | -7.8964
MV/LV Substation WI***322Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =386kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40224 | 0 |  | --> | E20 ex COLLOONEY | Collooney: T422 | Sligo |  | 54.2077 | -8.5103
MV/LV Substation WI***337Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0.01045 | 0.04759 | 0 |  | --> | E14 ex RANDALSTOWN | Randalstown: T422 | Navan |  | 53.74 | -6.715
MV/LV Substation WI***339Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =281kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4186 | 0 |  | --> | C20 ex BALLINACURRA | Ballinacurra: T42 | Limerick |  | 52.6597 | -8.635
MV/LV Substation WI***342X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C11 ex KILSARAN | Kilsaran: T42 | Drybridge |  | 53.8755 | -6.407
MV/LV Substation WI***358 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.414 | 5.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0095 | 0.5 | 0 |  | --> | C12 ex MILLTOWN (DR) | Milltown (dr): T102 | Inchicore 110kv |  | 53.3173 | -6.2551
MV/LV Substation WI***363Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =149kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.203 | 0 |  | --> | C22 ex MACETOWN | Macetown: T102 | Macetown |  | 53.395 | -6.4429
MV/LV Substation WI***364Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =333kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.40458 | 0 |  | --> | C22 ex MACETOWN | Macetown: T102 | Macetown |  | 53.3943 | -6.4428
MV/LV Substation WI***373Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C12 ex AGHAMORE | Aghamore: T42 | Lanesboro |  | 53.7659 | -8.0513
MV/LV Substation WI***376 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =241kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42466 | 0 |  | --> | C14 ex BELFIELD | Belfield: T42 | Blackrock |  | 53.3062 | -6.1976
MV/LV Substation WI***382Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.178 | 8.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E20 ex BALTRASNA | Baltrasna: T122 | Baltrasna |  | 53.5227 | -6.4131
MV/LV Substation WI***383 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.209 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0589 | 0.36744 | 0 |  | --> | C14 ex TEMPLEOGUE | Templeogue: T42 | Milltown (dr) |  | 53.3017 | -6.3265
MV/LV Substation WI***387Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.2 | 8.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C21 ex KILLOTERAN | Killoteran: T101 | Killoteran |  | 52.252 | -7.159
MV/LV Substation WI***389Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 10.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C24 ex MULLINGAR | Mullingar: T102 | Mullingar |  | 53.6124 | -7.42
MV/LV Substation WI***391X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.31 | 5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41414 | 0 |  | --> | C17 ex KILMORE | Kilmore: T101 | Finglas |  | 53.3978 | -6.1949
MV/LV Substation WI***396Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0133 | 0.0391 | 0 |  | --> | E11 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.2302 | -7.0697
MV/LV Substation WI***400 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =455kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C22 ex POPPINTREE | Poppintree: T102 | Finglas |  | 53.3942 | -6.2794
MV/LV Substation WI***4021 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =34kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052495 | 0 |  | --> | E18 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.5304 | -6.2362
MV/LV Substation WI***4032 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 3.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05295 | 0 |  | --> | C18 ex BOYLE | Boyle: T41∥T42 | Carrick On Shannon |  | 53.8479 | -8.2059
MV/LV Substation WI***4047 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C21 ex CASTLEREA | Castlerea: T41∥T42 | Carrick On Shannon |  | 53.7287 | -8.4696
MV/LV Substation WI***4049 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.05035 | 0.5 | 0 |  | --> | C20 ex GREENHILLS | Greenhills: T42 | Inchicore 110kv |  | 53.3068 | -6.3309
MV/LV Substation WI***4056 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 2.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | C25 ex TYCOR | Tycor: T41∥T42 | Waterford |  | 52.2498 | -7.1748
MV/LV Substation WI***4060 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy: T422 | Athlone |  | 53.6787 | -8.5461
MV/LV Substation WI***4063 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.02185 | 0.5 | 0 |  | --> | C12 ex SAGGART | Saggart: T41∥T42 | Grange Castle |  | 53.2802 | -6.4777
MV/LV Substation WI***4064 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C26 ex ATHY | Athy: T102 | Athy |  | 53.0174 | -6.9899
MV/LV Substation WI***4065 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.08265 | 0.5 | 0 |  | --> | C13 ex GREENHILLS | Greenhills: T42 | Inchicore 110kv |  | 53.3093 | -6.3308
MV/LV Substation WI***4074 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.156 | 9.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20692 | 0 |  | --> | C11 ex KILCOOLE | Kilcoole: T41∥T42 | Fassaroe |  | 53.0714 | -6.1105
MV/LV Substation WI***4077 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.06365 | 0.5 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines: T41 | Carrickmines |  | 53.2448 | -6.1881
MV/LV Substation WI***4094 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C11 ex DONEGAL | Donegal: T41∥T42 | Cathaleens Fall |  | 54.6504 | -8.2213
MV/LV Substation WI***4099 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.157 | 3.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20676 | 0 |  | --> | C22 ex CASTLEREA | Castlerea: T41∥T42 | Carrick On Shannon |  | 53.8347 | -8.3207
MV/LV Substation WI***4101 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C11 ex RATHDRUM | Rathdrum: T42 | Arklow |  | 52.9492 | -6.2057
MV/LV Substation WI***410Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =167kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.20221 | 0 |  | --> | C22 ex MACETOWN | Macetown: T102 | Macetown |  | 53.3951 | -6.4408
MV/LV Substation WI***4121 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.154 | 2.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20723 | 0 |  | --> | C15 ex CASTLECOMER | Castlecomer: T41∥T42 | Ballyragget |  | 52.8452 | -7.0838
MV/LV Substation WI***4132 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.302 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.04845 | 0.36438 | 0 |  | --> | C11 ex SALLINS | Sallins: T41 | Griffinrath |  | 53.2503 | -6.657
MV/LV Substation WI***4167 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.152 | 1.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20754 | 0 |  | --> | C20 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.2978 | -6.5708
MV/LV Substation WI***417 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 7.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.9kW. | --> | E14 ex ARIGNA | Arigna: T121 | Arigna |  | 54.0549 | -8.0185
MV/LV Substation WI***4174 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.296 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.4023 | 0 |  | --> | C11 ex LLOYD | Lloyd: T41∥T42 | Navan |  | 53.735 | -6.8846
MV/LV Substation WI***417X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 0.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052037 | 0 |  | --> | E15 ex KILMAGIG | Kilmagig: T42 | Arklow |  | 52.8396 | -6.3124
MV/LV Substation WI***4189 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines: T41 | Carrickmines |  | 53.2405 | -6.1984
MV/LV Substation WI***4191 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 8.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C17 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9336 | -6.0311
MV/LV Substation WI***4199 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 4.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E21 ex CLARA | Clara: T421 | Thornsberry |  | 53.35 | -7.6236
MV/LV Substation WI***420Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E17 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.6115 | -6.6923
MV/LV Substation WI***4217 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4006 | -6.4457
MV/LV Substation WI***4223 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E14 ex KILCOCK | Kilcock: T422 | Griffinrath |  | 53.5148 | -6.7111
MV/LV Substation WI***4250 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.15 | 0.2 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.44613 | 0 | Constrained,otherwise capacity available =500kW. | --> | C11 ex COOLMINE | Coolmine: T41 | Finglas |  | 53.3796 | -6.4004
MV/LV Substation WI***4251 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.15 | 0.2 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.44613 | 0 | Constrained,otherwise capacity available =500kW. | --> | C11 ex COOLMINE | Coolmine: T41 | Finglas |  | 53.38 | -6.4012
MV/LV Substation WI***4291 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.1349 | 0.49279 | 0 |  | --> | C39 ex COLLEGE PARK | College Park: T103 | College Park |  | 53.4254 | -6.3757
MV/LV Substation WI***4363 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 0.7 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex LEESON STREET | Leeson Street: T42 | Milltown (dr) |  | 53.3328 | -6.2515
MV/LV Substation WI***437X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =68kVA. | --> | 0.095 | 0 | 0 | 0 | 0.019 | 0.08499 | 0 |  | --> | C16 ex KILLACLOYNE | Killacloyne: T41∥T42 | Midleton |  | 51.9199 | -8.3134
MV/LV Substation WI***4444 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex LEESON STREET | Leeson Street: T42 | Milltown (dr) |  | 53.3342 | -6.2502
MV/LV Substation WI***446Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =150kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20784 | 0 |  | --> | C20 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1688 | -6.9089
MV/LV Substation WI***449Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0152 | 0.5 | 0 |  | --> | E12 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.2397 | -7.0886
MV/LV Substation WI***451X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.137 | 0.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.20083 | 0 |  | --> | C14 ex KNOCKMULLEN | Knockmullen: T42 | Great Island |  | 52.4078 | -6.9363
MV/LV Substation WI***468Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =337kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40996 | 0 |  | --> | C22 ex MACETOWN | Macetown: T102 | Macetown |  | 53.3943 | -6.4404
MV/LV Substation WI***469Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 12.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex MONREAD | Monread: T101 | Monread |  | 53.2533 | -6.6676
MV/LV Substation WI***472Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.15 | 0.2 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C11 ex COOLMINE | Coolmine: T41 | Finglas |  | 53.3786 | -6.3978
MV/LV Substation WI***489 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C16 ex BRAY | Bray: T42 | Fassaroe |  | 53.1814 | -6.1429
MV/LV Substation WI***489Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.15 | 0.2 | Constrained,otherwise capacity available =289kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41738 | 0 |  | --> | C11 ex COOLMINE | Coolmine: T41 | Finglas |  | 53.3804 | -6.3993
MV/LV Substation WI***491X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 0.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 51.9354 | -10.2402
MV/LV Substation WI***492 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C11 ex KILSARAN | Kilsaran: T42 | Drybridge |  | 53.8831 | -6.4094
MV/LV Substation WI***492Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.297 | 8.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.40014 | 0 |  | --> | C21 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9872 | -6.0797
MV/LV Substation WI***496X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 8.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex GORTLEE | Gortlee: T41∥T42 | Letterkenny |  | 54.9668 | -7.7327
MV/LV Substation WI***504 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.311 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.02945 | 0.383 | 0 |  | --> | C18 ex BALLYBODEN | Ballyboden: T42 | Cookstown |  | 53.2868 | -6.2888
MV/LV Substation WI***508 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.283 | 0.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.4123 | 0 |  | --> | C19 ex PEMBROKE | Pembroke: T42 | Ringsend |  | 53.3265 | -6.2158
MV/LV Substation WI***520Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | E13 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.474 | -6.2324
MV/LV Substation WI***521Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =351kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.38876 | 0 |  | --> | E11 ex GLASMORE | Glasmore: T421 | Glasmore |  | 53.4926 | -6.138
MV/LV Substation WI***542 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =124kVA. | --> | 0.95 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C17 ex GARVILLE AVENUE | Garville Avenue: T42 | Milltown (dr) |  | 53.3254 | -6.2656
MV/LV Substation WI***546 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.17 | 2.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20474 | 0 |  | --> | C14 ex TEMPLEOGUE | Templeogue: T42 | Milltown (dr) |  | 53.2975 | -6.3268
MV/LV Substation WI***548X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 3.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | C26 ex ATHY | Athy: T102 | Athy |  | 53.0219 | -6.994
MV/LV Substation WI***550X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.173 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0.20227 | 0 |  | --> | C15 ex SCARTEEN | Scarteen: T41∥T42 | Mallow |  | 52.1299 | -8.6643
MV/LV Substation WI***553X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.194 | 2.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.01425 | 0.18596 | 0 |  | --> | C18 ex TULLYNAMALRA | Tullynamalra: T41∥T42 | Meath Hill |  | 54.0816 | -6.8252
MV/LV Substation WI***561 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.15 | 0.2 | Constrained,otherwise capacity available =247kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01995 | 0.40276 | 0 |  | --> | C15 ex COOLMINE | Coolmine: T41 | Finglas |  | 53.3905 | -6.4197
MV/LV Substation WI***567Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =173kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20427 | 0 |  | --> | C20 ex DENNEHYS CROSS | Dennehys Cross: T42 | Trabeg |  | 51.8769 | -8.5078
MV/LV Substation WI***570 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =86kVA. | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0.096215 | 0 |  | --> | E13 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.3851 | -7.0017
MV/LV Substation WI***575Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.137 | 3.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0228 | 0.18583 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge: T41 | Griffinrath |  | 53.3469 | -6.547
MV/LV Substation WI***580X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.102 | 1.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.0209 | 0.19309 | 0 |  | --> | C13 ex LIFFEY VALLEY | Liffey Valley: T41 | Inchicore 110kv |  | 53.3555 | -6.4231
MV/LV Substation WI***586 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.144 | 0.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.20576 | 0 |  | --> | C19 ex PEMBROKE | Pembroke: T42 | Ringsend |  | 53.3266 | -6.217
MV/LV Substation WI***588X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.273 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.03705 | 0.38082 | 0 |  | --> | C13 ex LIFFEY VALLEY | Liffey Valley: T41 | Inchicore 110kv |  | 53.3554 | -6.4267
MV/LV Substation WI***594 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =106kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21449 | 0 |  | --> | C13 ex LOUGHLINSTOWN | Loughlinstown: T41 | Carrickmines |  | 53.2552 | -6.1361
MV/LV Substation WI***599X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.16 | 0.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.0304 | 0.1743 | 0 |  | --> | C20 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.836 | -9.0003
MV/LV Substation WI***612 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.037 | 4.4 |  | --> | 0.095 | 0 | 0 | 0 | 0.0114 | 0.09759 | 0 |  | --> | C16 ex BRAY | Bray: T42 | Fassaroe |  | 53.1777 | -6.1457
MV/LV Substation WI***612Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 8.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9876 | -6.0767
MV/LV Substation WI***612Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.157 | 1.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.0076 | 0.19876 | 0 |  | --> | C11 ex DERRYCRAMPH | Derrycramph: T41∥T42 | Shankill |  | 53.9737 | -7.348
MV/LV Substation WI***615 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.496 | 3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex MERRION SQUARE | Merrion Square: T42 | Ringsend |  | 53.3344 | -6.2471
MV/LV Substation WI***624 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.021 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.044432 | 0 |  | --> | C18 ex BALLYHALE | Ballyhale: T42 | Kilkenny |  | 52.4608 | -7.3986
MV/LV Substation WI***625 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0.0114 | 0.09084 | 0 |  | --> | C18 ex BALLYHALE | Ballyhale: T42 | Kilkenny |  | 52.461 | -7.3947
MV/LV Substation WI***642Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.13 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0.2089 | 0 |  | --> | C11 ex MULGANNON | Mulgannon: T41 | Wexford |  | 52.3363 | -6.476
MV/LV Substation WI***652Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C15 ex MONEYCOOLEY | Moneycooley: T41 | Griffinrath |  | 53.34 | -6.6029
MV/LV Substation WI***654 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =149kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.203 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy: T422 | Athlone |  | 53.6774 | -8.5811
MV/LV Substation WI***655 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =9kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.056147 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy: T422 | Athlone |  | 53.6777 | -8.5777
MV/LV Substation WI***658 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 5.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | E16 ex BUSH | Bush: T421∥T422 | Dundalk |  | 53.9915 | -6.1431
MV/LV Substation WI***665X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.044795 | 0 |  | --> | C22 ex BUSHFIELD | Bushfield: T42 | Athlone |  | 53.4379 | -7.8999
MV/LV Substation WI***668Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C26 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8978 | -8.5335
MV/LV Substation WI***682 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C11 ex KILSARAN | Kilsaran: T42 | Drybridge |  | 53.8753 | -6.3985
MV/LV Substation WI***684 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =34kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0076 | 0.044495 | 0 |  | --> | E16 ex ACADEMY STREET | Academy Street: T421∥T422 | Navan |  | 53.6127 | -6.6754
MV/LV Substation WI***694Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy: T422 | Athlone |  | 53.6747 | -8.5842
MV/LV Substation WI***701X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex DENNEHYS CROSS | Dennehys Cross: T42 | Trabeg |  | 51.881 | -8.5076
MV/LV Substation WI***712Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy: T422 | Athlone |  | 53.6763 | -8.5911
MV/LV Substation WI***720Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.159 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.0133 | 0.19245 | 0 |  | --> | C15 ex COES ROAD | Coes Road: T41∥T42 | Dundalk |  | 54.0045 | -6.3566
MV/LV Substation WI***724X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =99kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10016 | 0 |  | --> | C17 ex DOUGLAS | Douglas: T42 | Trabeg |  | 51.8577 | -8.4503
MV/LV Substation WI***749 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =162kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0437 | 0.15999 | 0 |  | --> | C16 ex KILLACLOYNE | Killacloyne: T41∥T42 | Midleton |  | 51.9201 | -8.3191
MV/LV Substation WI***749 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex BALLYRICKARD | Ballyrickard: T41∥T42 | Tralee |  | 52.2851 | -9.7079
MV/LV Substation WI***753X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 2.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.047885 | 0 |  | --> | C17 ex RANDALSTOWN | Randalstown: T41 | Navan |  | 53.6703 | -6.7039
MV/LV Substation WI***770 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.012 | 0 | Constrained,otherwise capacity available =32kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00855 | 0.0438 | 0 |  | --> | C15 ex MOATE | Moate: T42 | Athlone |  | 53.3971 | -7.738
MV/LV Substation WI***773X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MALLOW | Mallow: T42 | Mallow |  | 52.1371 | -8.643
MV/LV Substation WI***806X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 26.8 |  | --> | 0.095 | 0 | 0 | 0 | 0.01425 | 0.08737 | 0 |  | --> | E21 ex WEXFORD | Wexford: T121∥T122 | Wexford |  | 52.3887 | -6.3661
MV/LV Substation WI***828X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 5.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.046265 | 0 |  | --> | C11 ex BALLINCOLLIG | Ballincollig: T41 | Kilbarry |  | 51.8453 | -8.6104
MV/LV Substation WI***836 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =11kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.055867 | 0 |  | --> | C22 ex GREYSTONES | Greystones: T42 | Fassaroe |  | 53.1223 | -6.109
MV/LV Substation WI***838 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C22 ex GREYSTONES | Greystones: T42 | Fassaroe |  | 53.1239 | -6.1066
MV/LV Substation WI***840X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.263 | 8.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41634 | 0 |  | --> | C25 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9821 | -6.0495
MV/LV Substation WI***862Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.34 | 7.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40948 | 0 |  | --> | C11 ex GARRYCASTLE | Garrycastle: T41 | Athlone |  | 53.4161 | -7.907
MV/LV Substation WI***876Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =152kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0 | 0 | Constrained,otherwise capacity available =205.5kW. | --> | C16 ex MOUNTMELLICK | Mountmellick: T41∥T42 | Portlaoise |  | 53.1135 | -7.3158
MV/LV Substation WI***882 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C11 ex ATHENRY | Athenry: T41∥T42 | Galway 110kv |  | 53.2714 | -8.7745
MV/LV Substation WI***882Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =71kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10454 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy: T422 | Athlone |  | 53.6755 | -8.5793
MV/LV Substation WI***887Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.095 | 5.5 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.21312 | 0 |  | --> | C12 ex ABBEYLAND | Abbeyland: T42 | Navan |  | 53.6667 | -6.699
MV/LV Substation WI***888Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.343 | 5.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40902 | 0 |  | --> | C12 ex ABBEYLAND | Abbeyland: T42 | Navan |  | 53.6686 | -6.6956
MV/LV Substation WI***934 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.346 | 9.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40854 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole: T41∥T42 | Fassaroe |  | 53.1052 | -6.0638
MV/LV Substation WI***950Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =117kVA. | --> | 0.19 | 0 | 0 | 0 | 0.02185 | 0.18985 | 0 |  | --> | C16 ex DOUGLAS | Douglas: T41 | Trabeg |  | 51.8924 | -8.4217
MV/LV Substation WI***974 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 0.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10016 | 0 |  | --> | E14 ex RANDALSTOWN | Randalstown: T422 | Navan |  | 53.7387 | -6.7183
MV/LV Substation WI***989 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.134 | 1.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.02755 | 0.18129 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North: T41∥T42 | Ennis |  | 52.8531 | -8.9932
MV/LV Substation WK***760Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.169 | 5.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.038 | 0.1649 | 0 |  | --> | C18 ex PURCELLS INCH | Purcells Inch: T42 | Kilkenny |  | 52.6462 | -7.2133
MV/LV Substation WO***001 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.402 | 3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C21 ex SWINFORD | Swinford: T41∥T42 | Castlebar |  | 53.9826 | -9.1134
MV/LV Substation WO***001 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.184 | 9.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20255 | 0 |  | --> | C17 ex CONVOY | Convoy: T41∥T42 | Letterkenny |  | 54.8585 | -7.659
MV/LV Substation WO***001Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =334kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41042 | 0 |  | --> | C22 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8513 | -8.3154
MV/LV Substation WO***002Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex KILMORE | Kilmore: T101 | Finglas |  | 53.4095 | -6.2361
MV/LV Substation WO***005 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =27kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0057 | 0.04755 | 0 |  | --> | C16 ex LOUGHREA | Loughrea: T41∥T42 | Somerset |  | 53.1929 | -8.5646
MV/LV Substation WO***007 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | E15 ex PATRICKSWELL | Patrickswell: T421∥T422 | Limerick |  | 52.5626 | -8.7662
MV/LV Substation WO***007X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E16 ex BALLYCROSSAUN | Ballycrossaun: T421∥T422 | Somerset |  | 53.1008 | -8.2846
MV/LV Substation WO***008 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =356kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40698 | 0 |  | --> | C22 ex MIDLETON | Midleton: T102 | Midleton |  | 51.9014 | -8.1709
MV/LV Substation WO***008 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =98kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10032 | 0 |  | --> | E12 ex BIRDHILL | Birdhill: T422 | Ardnacrusha |  | 52.8089 | -8.4818
MV/LV Substation WO***008Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.359 | 4.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4065 | 0 |  | --> | C12 ex DUNDALK | Dundalk: T42 | Dundalk |  | 54.0139 | -6.4136
MV/LV Substation WO***012X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.179 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20333 | 0 |  | --> | C11 ex BALLYARD | Ballyard: T41∥T42 | Tralee |  | 52.262 | -9.7032
MV/LV Substation WO***013 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 1.3 |  | --> | 0.095 | 0 | 0 | 0 | 0.01045 | 0.09338 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North: T41∥T42 | Ennis |  | 52.8523 | -9.0137
MV/LV Substation WO***013X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.308 | 3.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0228 | 0 | 0 | Constrained,otherwise capacity available =390.5kW. | --> | E20 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 51.9393 | -7.9924
MV/LV Substation WO***014 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.3 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North: T41∥T42 | Ennis |  | 52.8539 | -9.0095
MV/LV Substation WO***016 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =275kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.40952 | 0 |  | --> | C17 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.1625 | -6.903
MV/LV Substation WO***016Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.128 | 3.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.2082 | 0 |  | --> | C12 ex MARSHES | Marshes: T42 | Dundalk |  | 53.9909 | -6.3914
MV/LV Substation WO***022Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 3.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10377 | 0 |  | --> | C18 ex MARSHES | Marshes: T42 | Dundalk |  | 53.9816 | -6.3842
MV/LV Substation WO***024Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =326kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.40866 | 0 |  | --> | C11 ex GARDEN CITY | Garden City: T41∥T42 | Arklow |  | 52.6849 | -6.2921
MV/LV Substation WO***025Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex GARDEN CITY | Garden City: T41∥T42 | Arklow |  | 52.684 | -6.291
MV/LV Substation WO***028 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.05 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.22262 | 0 |  | --> | E19 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.7079 | -6.4972
MV/LV Substation WO***030 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.245 | 3.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.40406 | 0 |  | --> | C18 ex MONEENAGEISHA | Moneenageisha: T42 | Galway 110kv |  | 53.2808 | -9.0253
MV/LV Substation WO***030 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.457 | 1.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0152 | 0.5 | 0 |  | --> | E19 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.7101 | -6.5016
MV/LV Substation WO***030 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 2.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10284 | 0 |  | --> | C12 ex PORTLAW | Portlaw: T41∥T42 | Butlerstown |  | 52.2943 | -7.3103
MV/LV Substation WO***030X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.291 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41206 | 0 |  | --> | C17 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5598 | -6.7745
MV/LV Substation WO***030Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =78kVA. | --> | 0.095 | 0 | 0 | 0 | 0.01045 | 0.069851 | 0 | Constrained,otherwise capacity available =92.5kW. | --> | C17 ex BIRR | Birr: T41 | Dallow |  | 53.0869 | -7.9002
MV/LV Substation WO***032 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =34kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052495 | 0 |  | --> | E15 ex WHITECHURCH | Whitechurch: T421 | Kilbarry |  | 51.9381 | -8.5603
MV/LV Substation WO***033Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =352kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4076 | 0 |  | --> | C20 ex TOGHER | Togher: T42 | Trabeg |  | 51.8772 | -8.4901
MV/LV Substation WO***034 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =298kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.416 | 0 |  | --> | C17 ex BALLYBEGGAN | Ballybeggan: T43∥T44 | Tralee |  | 52.2859 | -9.6914
MV/LV Substation WO***034Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.2 | 4.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C17 ex SWORDS | Swords: T41 | Glasmore |  | 53.4619 | -6.2115
MV/LV Substation WO***039 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.139 | 7.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.0133 | 0.19553 | 0 |  | --> | E24 ex BANOGE | Banoge: T122 | Banoge |  | 52.6447 | -6.2345
MV/LV Substation WO***040 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =162kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01235 | 0.19299 | 0 |  | --> | E17 ex CREAGH | Creagh: T421∥T422 | Athlone |  | 53.3295 | -8.1933
MV/LV Substation WO***040 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 2.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.048992 | 0 |  | --> | C14 ex BALLYBODEN | Ballyboden: T42 | Cookstown |  | 53.2692 | -6.3139
MV/LV Substation WO***042 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.337 | 1.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40996 | 0 |  | --> | C20 ex CAHIR | Cahir: T42 | Cahir |  | 52.3813 | -7.9318
MV/LV Substation WO***042X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.306 | 3.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41476 | 0 |  | --> | C19 ex BOGHALL ROAD | Boghall Road: T41 | Fassaroe |  | 53.1798 | -6.1287
MV/LV Substation WO***043Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.054 | 0.1 | Constrained,otherwise capacity available =245kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00665 | 0.41706 | 0 |  | --> | C16 ex SANTRY | Santry: T42 | Finglas |  | 53.399 | -6.2309
MV/LV Substation WO***044Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.054 | 0.1 | Constrained,otherwise capacity available =244kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.4192 | 0 |  | --> | C16 ex SANTRY | Santry: T42 | Finglas |  | 53.4011 | -6.2308
MV/LV Substation WO***045 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.326 | 4.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.39666 | 0 |  | --> | C11 ex OAKFIELD | Oakfield: T41 | Sligo |  | 54.2552 | -8.4668
MV/LV Substation WO***046 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =88kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1019 | 0 |  | --> | C19 ex MILFORD (NR) | Milford (nr): T41∥T42 | Letterkenny |  | 55.072 | -7.6787
MV/LV Substation WO***046 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.128 | 2.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =211.2kW. | --> | C15 ex KILRUSH | Kilrush: T41∥T42 | Tullabrack |  | 52.64 | -9.4731
MV/LV Substation WO***048 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0209 | 0.5 | 0 |  | --> | C18 ex WOODFORD | Woodford: T41∥T42 | Knockearagh |  | 52.05 | -9.503
MV/LV Substation WO***050 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =107.7kW. | --> | E12 ex PORTLAOISE | Portlaoise: T423∥T424 | Portlaoise |  | 53.0127 | -7.1478
MV/LV Substation WO***055 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.152 | 9.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20754 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.7966 | -9.5413
MV/LV Substation WO***056X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =89kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10174 | 0 |  | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9953 | -8.0658
MV/LV Substation WO***056Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =127kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21135 | 0 |  | --> | C21 ex DOUGLAS | Douglas: T42 | Trabeg |  | 51.8757 | -8.3913
MV/LV Substation WO***059 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =264kVA. | --> | 0.38 | 0 | 0 | 0 | 0.1159 | 0.29918 | 0 |  | --> | C17 ex LUCAN EAST | Lucan East: T41∥T42 | Grange Castle |  | 53.3609 | -6.4453
MV/LV Substation WO***059Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.175 | 7.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20396 | 0 |  | --> | C19 ex ATHY | Athy: T101 | Athy |  | 52.9925 | -7.0013
MV/LV Substation WO***062 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 0.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10206 | 0 |  | --> | C12 ex KILMAGIG | Kilmagig: T42 | Arklow |  | 52.8303 | -6.2346
MV/LV Substation WO***062Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.24 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0266 | 0.3968 | 0 |  | --> | C12 ex MONEYCOOLEY | Moneycooley: T42 | Griffinrath |  | 53.3424 | -6.5529
MV/LV Substation WO***063Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.258 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.03135 | 0.3891 | 0 |  | --> | C12 ex MONEYCOOLEY | Moneycooley: T42 | Griffinrath |  | 53.3425 | -6.5508
MV/LV Substation WO***067 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =289kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0247 | 0.39138 | 0 |  | --> | C12 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.9349 | -7.7353
MV/LV Substation WO***067X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =146kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0171 | 0.19046 | 0 |  | --> | E47 ex CLAREGALWAY | Claregalway: T421 | Galway 110kv |  | 53.3669 | -8.8892
MV/LV Substation WO***068 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | E12 ex KILCOCK | Kilcock: T422 | Griffinrath |  | 53.4745 | -6.5696
MV/LV Substation WO***070Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =131kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0475 | 0.16074 | 0 |  | --> | C14 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.2371 | -7.0115
MV/LV Substation WO***071 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.321 | 8.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.40944 | 0 |  | --> | C12 ex MONREAD | Monread: T102 | Monread |  | 53.2258 | -6.6592
MV/LV Substation WO***074Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.475 | 5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex KILMORE | Kilmore: T101 | Finglas |  | 53.4085 | -6.2363
MV/LV Substation WO***078X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | E17 ex BALLYMACARRY | Ballymacarry: T421 | Trillick |  | 55.0768 | -7.4506
MV/LV Substation WO***081 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.298 | 4.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.397 | 0 |  | --> | C11 ex BALLYRICKARD | Ballyrickard: T41∥T42 | Tralee |  | 52.2781 | -9.7022
MV/LV Substation WO***081Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =80kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10315 | 0 |  | --> | C21 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4464 | -6.4829
MV/LV Substation WO***082Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C21 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4442 | -6.4839
MV/LV Substation WO***085 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =295kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.06555 | 0.5 | 0 |  | --> | C14 ex BELFIELD | Belfield: T42 | Blackrock |  | 53.3089 | -6.209
MV/LV Substation WO***085 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray: T41 | Fassaroe |  | 53.2167 | -6.1135
MV/LV Substation WO***089X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 1.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =105.7kW. | --> | C11 ex FOYNES | Foynes: T41 | Rathkeale |  | 52.61 | -9.1073
MV/LV Substation WO***090 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.169 | 0.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2049 | 0 |  | --> | C12 ex KILMAGIG | Kilmagig: T42 | Arklow |  | 52.8327 | -6.2322
MV/LV Substation WO***091 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.006 | 4.6 |  | --> | 0.095 | 0 | 0 | 0 | 0.00285 | 0.11096 | 0 |  | --> | E16 ex BALLYRAGGET | Ballyragget: T421∥T422 | Ballyragget |  | 52.8434 | -7.3936
MV/LV Substation WO***094 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.428 | 5.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0114 | 0.5 | 0 |  | --> | C17 ex POTTERY ROAD | Pottery Road: T101 | Carrickmines |  | 53.2761 | -6.143
MV/LV Substation WO***096 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.328 | 7.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41136 | 0 |  | --> | E41 ex KINSALE | Kinsale: T423 | Bandon |  | 51.6985 | -8.5194
MV/LV Substation WO***096 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =53.7kW. | --> | C16 ex RATHDRUM | Rathdrum: T42 | Arklow |  | 52.934 | -6.2424
MV/LV Substation WO***096 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 25.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | C13 ex ARKLOW | Arklow: T101∥T102 | Arklow |  | 52.8136 | -6.1579
MV/LV Substation WO***097 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | E11 ex BEALNABLATH | Bealnablath: T421 | Bandon |  | 51.8237 | -8.7616
MV/LV Substation WO***098Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.29 | 7 |  | --> | 0.38 | 0 | 0 | 0 | 0.02375 | 0.39222 | 0 |  | --> | C17 ex BUSHFIELD | Bushfield: T41 | Athlone |  | 53.4332 | -7.8987
MV/LV Substation WO***100Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.173 | 2.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20427 | 0 |  | --> | C11 ex COOLOCK | Coolock: T41 | Finglas |  | 53.3956 | -6.1911
MV/LV Substation WO***102X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 2.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10299 | 0 |  | --> | C16 ex ROSSGEIR | Rossgeir: T41∥T42 | Letterkenny |  | 54.876 | -7.5785
MV/LV Substation WO***104X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.327 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41152 | 0 |  | --> | C18 ex MOUNT MERRION | Mount Merrion: T42 | Carrickmines |  | 53.3003 | -6.1884
MV/LV Substation WO***106Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.345 | 1.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4087 | 0 |  | --> | E15 ex BALLYCONNELL | Ballyconnell: T421∥T422 | Gortawee |  | 54.1134 | -7.5839
MV/LV Substation WO***106Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.103 | 8.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0209 | 0.19294 | 0 |  | --> | E18 ex BALTRASNA | Baltrasna: T122 | Baltrasna |  | 53.5078 | -6.4719
MV/LV Substation WO***107Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =192kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.19728 | 0 |  | --> | E20 ex COLLOONEY | Collooney: T422 | Sligo |  | 54.2131 | -8.5159
MV/LV Substation WO***112X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | E24 ex BIRR | Birr: T422 | Dallow |  | 53.1081 | -7.8964
MV/LV Substation WO***112Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.143 | 2.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =208.9kW. | --> | C15 ex NEWCASTLEWEST | Newcastlewest: T41∥T42 | Rathkeale |  | 52.4441 | -9.0486
MV/LV Substation WO***116 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E11 ex CARRIGALLEN | Carrigallen: T421 | Carrick On Shannon |  | 54.0557 | -7.6929
MV/LV Substation WO***116 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.259 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0.40894 | 0 |  | --> | C15 ex TYMON | Tymon: T41 | Cookstown |  | 53.2834 | -6.3378
MV/LV Substation WO***117 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.238 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0266 | 0.3971 | 0 |  | --> | C15 ex TYMON | Tymon: T41 | Cookstown |  | 53.2812 | -6.3345
MV/LV Substation WO***118X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex INCHICORE NORTH | Inchicore North: T41 | Inchicore 110kv |  | 53.3288 | -6.3543
MV/LV Substation WO***121 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.107 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.02565 | 0.18735 | 0 |  | --> | C28 ex ACADEMY STREET | Academy Street: T44 | Navan |  | 53.6473 | -6.6842
MV/LV Substation WO***122X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.364 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40572 | 0 |  | --> | C18 ex DUN LAOGHAIRE | Dun Laoghaire: T42 | Blackrock |  | 53.294 | -6.1412
MV/LV Substation WO***132 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.314 | 3.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0171 | 0.39552 | 0 |  | --> | C16 ex BOGHALL ROAD | Boghall Road: T42 | Fassaroe |  | 53.1894 | -6.1119
MV/LV Substation WO***136 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.316 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.39822 | 0 |  | --> | C19 ex SANDYFORD | Sandyford: T41 | Carrickmines |  | 53.2721 | -6.2493
MV/LV Substation WO***136 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.157 | 3.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.03515 | 0.16976 | 0 |  | --> | C12 ex MAYFIELD | Mayfield: T42 | Kilbarry |  | 51.9058 | -8.4341
MV/LV Substation WO***136X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C12 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.9301 | -7.7203
MV/LV Substation WO***138 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.478 | 1.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0209 | 0.5 | 0 |  | --> | C11 ex TRABEG | Trabeg: T102 | Trabeg |  | 51.8851 | -8.4504
MV/LV Substation WO***143X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.1kW. | --> | E12 ex CARNDONAGH | Carndonagh: T421∥T422 | Trillick |  | 55.2687 | -7.2686
MV/LV Substation WO***145X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.451 | 5.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex WOLFE TONE STREET | Wolfe Tone Street: T101 | Finglas |  | 53.3494 | -6.2675
MV/LV Substation WO***145Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.291 | 0.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.019 | 0.39706 | 0 |  | --> | C14 ex KNOCKMULLEN | Knockmullen: T42 | Great Island |  | 52.3868 | -6.9286
MV/LV Substation WO***147 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =458kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0171 | 0.5 | 0 |  | --> | C21 ex CENTRAL PARK | Central Park: T101 | Carrickmines |  | 53.2922 | -6.202
MV/LV Substation WO***148X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | C15 ex TOOMEVARA | Toomevara: T42 | Nenagh |  | 52.889 | -8.0515
MV/LV Substation WO***151X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.362 | 3 |  | --> | 0.38 | 0 | 0 | 0 | 0.03515 | 0 | 0 | Constrained,otherwise capacity available =369kW. | --> | C13 ex SWINFORD | Swinford: T41∥T42 | Castlebar |  | 53.9387 | -8.9441
MV/LV Substation WO***151Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 11.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex BALLYBEG | Ballybeg: T102 | Carrickmines |  | 52.994 | -6.0867
MV/LV Substation WO***152X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =136kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01235 | 0.19698 | 0 |  | --> | C12 ex LUCAN EAST | Lucan East: T41∥T42 | Grange Castle |  | 53.3541 | -6.4612
MV/LV Substation WO***155X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex CABRA | Cabra: T101 | Finglas |  | 53.3753 | -6.3052
MV/LV Substation WO***157X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.09 | 5.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21685 | 0 |  | --> | E14 ex MOY | Moy: T421∥T422 | Moy |  | 54.2103 | -9.2221
MV/LV Substation WO***158Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.152 | 0.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.0133 | 0.19354 | 0 |  | --> | C21 ex BISHOPSTOWN | Bishopstown: T41 | Kilbarry |  | 51.8861 | -8.5195
MV/LV Substation WO***161X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.099 | 3.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.21253 | 0 |  | --> | C22 ex CASTLEREA | Castlerea: T41∥T42 | Carrick On Shannon |  | 53.7694 | -8.5058
MV/LV Substation WO***162Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.05 | 0.1 | Constrained,otherwise capacity available =496kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.44613 | 0 | Constrained,otherwise capacity available =500kW. | --> | C12 ex COOLMINE | Coolmine: T42 | Finglas |  | 53.3881 | -6.3917
MV/LV Substation WO***166X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C18 ex DUNLEER | Dunleer: T41∥T42 | Drybridge |  | 53.8213 | -6.4026
MV/LV Substation WO***166Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =32kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0076 | 0 | 0 | Constrained,otherwise capacity available =44.8kW. | --> | C13 ex FERMOY NORTH | Fermoy North: T41∥T42 | Barrymore |  | 52.1453 | -8.2685
MV/LV Substation WO***169X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =172kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20443 | 0 |  | --> | E25 ex TALBOTS INCH | Talbots Inch: T41∥T42 | Kilkenny |  | 52.7306 | -7.4055
MV/LV Substation WO***180Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.3 | 25.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.40468 | 0 |  | --> | C22 ex ARKLOW | Arklow: T101∥T102 | Arklow |  | 52.7947 | -6.1778
MV/LV Substation WO***182 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.387 | 5.4 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0608 | 0.5 | 0 |  | --> | C18 ex TEMPLEOGUE | Templeogue: T41 | Milltown (dr) |  | 53.2904 | -6.3093
MV/LV Substation WO***184 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.067 | 8.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.21119 | 0 |  | --> | C21 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 52.9947 | -6.0796
MV/LV Substation WO***189 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E11 ex CARRIGALLEN | Carrigallen: T421 | Carrick On Shannon |  | 54.097 | -7.7835
MV/LV Substation WO***189X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =180kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20318 | 0 |  | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9913 | -8.0672
MV/LV Substation WO***195Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.1kW. | --> | C15 ex KILCLOHER | Kilcloher: T42 | Dungarvan |  | 52.0904 | -7.8523
MV/LV Substation WO***196X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.172 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20443 | 0 |  | --> | C16 ex DUNLEER | Dunleer: T41∥T42 | Drybridge |  | 53.8316 | -6.3896
MV/LV Substation WO***197Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.315 | 25.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.40738 | 0 |  | --> | C22 ex ARKLOW | Arklow: T101∥T102 | Arklow |  | 52.797 | -6.1768
MV/LV Substation WO***197Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C21 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4413 | -6.4784
MV/LV Substation WO***201X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C13 ex CARRICKMINES | Carrickmines: T41 | Carrickmines |  | 53.25 | -6.1873
MV/LV Substation WO***204X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.292 | 2.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41692 | 0 |  | --> | E19 ex KENMARE | Kenmare: T421 | Knockearagh |  | 51.8201 | -9.8765
MV/LV Substation WO***206 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =95kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | C11 ex WOODFORD | Woodford: T41∥T42 | Knockearagh |  | 52.0568 | -9.471
MV/LV Substation WO***208 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.313 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.40168 | 0 |  | --> | C13 ex DODDER ROAD | Dodder Road: T42 | Milltown (dr) |  | 53.2998 | -6.274
MV/LV Substation WO***212Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C13 ex OLDCASTLE | Oldcastle: T41 | Mullingar |  | 53.7683 | -7.1361
MV/LV Substation WO***213 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =204kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00665 | 0.42318 | 0 |  | --> | C13 ex MOYLISH | Moylish: T41∥T42 | Ardnacrusha |  | 52.6772 | -8.6532
MV/LV Substation WO***214Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05173 | 0 |  | --> | E18 ex DALTON | Dalton: T421∥T422 | Dalton |  | 53.6852 | -8.9339
MV/LV Substation WO***215 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =468kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0266 | 0.5 | 0 |  | --> | C13 ex GARRYOWEN | Garryowen: T41 | Limerick |  | 52.6539 | -8.6016
MV/LV Substation WO***218 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =275kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00665 | 0.41252 | 0 |  | --> | C13 ex CAHERDAVIN | Caherdavin: T41 | Ardnacrusha |  | 52.6753 | -8.6628
MV/LV Substation WO***221X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.151 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.02945 | 0.17669 | 0 |  | --> | C20 ex SUTTON | Sutton: T42 | Grange (dr) |  | 53.3792 | -6.0601
MV/LV Substation WO***228X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =172kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0095 | 0.19443 | 0 |  | --> | E47 ex CLAREGALWAY | Claregalway: T421 | Galway 110kv |  | 53.3665 | -8.8907
MV/LV Substation WO***231X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C17 ex KILCAR | Kilcar: T41 | Binbane |  | 54.6978 | -8.7701
MV/LV Substation WO***232 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.212 | 0.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0323 | 0.39498 | 0 |  | --> | C19 ex BREWERY ROAD | Brewery Road: T41 | Carrickmines |  | 53.2744 | -6.2003
MV/LV Substation WO***232 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 4.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10284 | 0 |  | --> | C21 ex BALLYRAINE | Ballyraine: T41∥T42 | Letterkenny |  | 54.9831 | -7.6955
MV/LV Substation WO***233 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0 | 0 | Constrained,otherwise capacity available =28kVA. | --> | 0.03135 | 0 | 0 | 0 | 0 | 0.03379 | 0 |  | --> | E18 ex BIRDHILL | Birdhill: T422 | Ardnacrusha |  | 52.7068 | -8.4837
MV/LV Substation WO***234 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E18 ex BIRDHILL | Birdhill: T422 | Ardnacrusha |  | 52.7077 | -8.4853
MV/LV Substation WO***234 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.1009 | 0.1 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.02945 | 0.5 | 0 |  | --> | C11 ex COOLCORCORAN | Coolcorcoran: T41∥T42 | Knockearagh |  | 52.0616 | -9.4827
MV/LV Substation WO***238 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =75kVA. | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.09892 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray: T41 | Fassaroe |  | 53.2185 | -6.1221
MV/LV Substation WO***238Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.11 | 25.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.0114 | 0.2019 | 0 |  | --> | C22 ex ARKLOW | Arklow: T101∥T102 | Arklow |  | 52.7982 | -6.1766
MV/LV Substation WO***240Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 0.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10454 | 0 |  | --> | C12 ex KILMAGIG | Kilmagig: T42 | Arklow |  | 52.8319 | -6.2389
MV/LV Substation WO***240Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.166 | 5.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0.19637 | 0 |  | --> | C11 ex BALLINCOLLIG | Ballincollig: T41 | Kilbarry |  | 51.8545 | -8.5641
MV/LV Substation WO***243Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 5.3 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10454 | 0 |  | --> | C14 ex SMEARLA | Smearla: T42 | Trien |  | 52.5754 | -9.3795
MV/LV Substation WO***246 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =291kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.41106 | 0 |  | --> | C14 ex MOYLISH | Moylish: T41∥T42 | Ardnacrusha |  | 52.6791 | -8.6509
MV/LV Substation WO***249X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =140kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20538 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin: T44 | Inchicore 110kv |  | 53.3212 | -6.3793
MV/LV Substation WO***250X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =229kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02185 | 0.40346 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin: T44 | Inchicore 110kv |  | 53.3213 | -6.3777
MV/LV Substation WO***250Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.347 | 10.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4084 | 0 |  | --> | C23 ex PELLETSTOWN | Pelletstown: T101 | Finglas |  | 53.3849 | -6.3705
MV/LV Substation WO***253X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex KILMORE | Kilmore: T101 | Finglas |  | 53.4117 | -6.2399
MV/LV Substation WO***257Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex OLDCASTLE | Oldcastle: T41 | Mullingar |  | 53.784 | -7.1372
MV/LV Substation WO***258X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.1259 | 0.1 | Constrained,otherwise capacity available =410kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex WOLFE TONE STREET | Wolfe Tone Street: T102 | Finglas |  | 53.3497 | -6.2679
MV/LV Substation WO***260Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =175kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20396 | 0 |  | --> | E20 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.3561 | -7.1967
MV/LV Substation WO***263Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C20 ex CELBRIDGE | Celbridge: T42 | Griffinrath |  | 53.2982 | -6.559
MV/LV Substation WO***264Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0494 | 0.5 | 0 |  | --> | C19 ex JOHNSTOWN | Johnstown: T41 | Kilteel |  | 53.2221 | -6.6516
MV/LV Substation WO***267X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex OAKFIELD | Oakfield: T42 | Sligo |  | 54.25 | -8.469
MV/LV Substation WO***268 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.319 | 13.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.39676 | 0 |  | --> | C20 ex POTTERY ROAD | Pottery Road: T102 | Carrickmines |  | 53.2657 | -6.1452
MV/LV Substation WO***269X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.148 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.01995 | 0.18715 | 0 |  | --> | C18 ex DUNLEER | Dunleer: T41∥T42 | Drybridge |  | 53.8258 | -6.3993
MV/LV Substation WO***269X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen: T41∥T42 | Tonroe |  | 53.8221 | -8.5654
MV/LV Substation WO***270X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20176 | 0 |  | --> | C18 ex DUNLEER | Dunleer: T41∥T42 | Drybridge |  | 53.8265 | -6.3967
MV/LV Substation WO***272X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.329 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.4052 | 0 |  | --> | C11 ex RAMPARTS | Ramparts: T41 | Dundalk |  | 53.9934 | -6.393
MV/LV Substation WO***272X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 2.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10284 | 0 |  | --> | E17 ex LONGFORD | Longford: T421 | Richmond |  | 53.7448 | -7.7178
MV/LV Substation WO***275 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10032 | 0 |  | --> | E19 ex LAWLESSTOWN | Lawlesstown: T421 | Doon |  | 52.5232 | -7.7552
MV/LV Substation WO***276Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.002 | 10.9 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ENNIS | Ennis: T102 | Ennis |  | 52.8445 | -8.9842
MV/LV Substation WO***284X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.488 | 2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex FAIRVIEW | Fairview: T41 | Mcdermott |  | 53.3711 | -6.2093
MV/LV Substation WO***284Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E18 ex GLASMORE | Glasmore: T422 | Glasmore |  | 53.5232 | -6.2115
MV/LV Substation WO***287Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.164 | 4 |  | --> | 0.19 | 0 | 0 | 0 | 0.0418 | 0.16168 | 0 |  | --> | E18 ex TULLOW | Tullow: T422 | Carlow |  | 52.8539 | -6.5631
MV/LV Substation WO***288Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.307 | 8.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.4056 | 0 |  | --> | E18 ex BALTRASNA | Baltrasna: T122 | Baltrasna |  | 53.507 | -6.4683
MV/LV Substation WO***292X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 1.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10299 | 0 |  | --> | E11 ex CARRIGALLEN | Carrigallen: T421 | Carrick On Shannon |  | 54.043 | -7.6789
MV/LV Substation WO***292Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.15 | 0.2 | Constrained,otherwise capacity available =339kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40964 | 0 |  | --> | C11 ex COOLMINE | Coolmine: T41 | Finglas |  | 53.3764 | -6.4034
MV/LV Substation WO***293Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =95kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | C24 ex MACETOWN | Macetown: T102 | Macetown |  | 53.4732 | -6.3756
MV/LV Substation WO***297X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.11 | 0.1 | Constrained,otherwise capacity available =329kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.4082 | 0 |  | --> | C15 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.5111 | -8.8693
MV/LV Substation WO***298 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.283 | 6.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4183 | 0 |  | --> | C20 ex PELLETSTOWN | Pelletstown: T102 | Finglas |  | 53.3817 | -6.3195
MV/LV Substation WO***298 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.302 | 2.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.00665 | 0.40838 | 0 |  | --> | C19 ex COOLOCK | Coolock: T41 | Finglas |  | 53.3877 | -6.1761
MV/LV Substation WO***299 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.268 | 3.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.41658 | 0 |  | --> | C22 ex COOLOCK | Coolock: T42 | Finglas |  | 53.3896 | -6.1742
MV/LV Substation WO***304 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex GRAIGUE | Graigue: T41 | Carlow |  | 52.8307 | -6.9272
MV/LV Substation WO***304Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =148kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0133 | 0.19415 | 0 |  | --> | C15 ex MALAHIDE | Malahide: T41 | Glasmore |  | 53.4295 | -6.1367
MV/LV Substation WO***307X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =285kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02375 | 0.39298 | 0 |  | --> | C15 ex LUCAN EAST | Lucan East: T41∥T42 | Grange Castle |  | 53.352 | -6.465
MV/LV Substation WO***310X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.024 | 2.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.0171 | 0.20827 | 0 |  | --> | C18 ex PALMERSTOWN | Palmerstown: T42 | Finglas |  | 53.352 | -6.3707
MV/LV Substation WO***312X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C11 ex CROSSMOLINA | Crossmolina: T41∥T42 | Moy |  | 54.0891 | -9.314
MV/LV Substation WO***315X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053697 | 0 |  | --> | E18 ex CURRALEIGH | Curraleigh: T421∥T422 | Kilbarry |  | 51.9141 | -8.5731
MV/LV Substation WO***317Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C19 ex NEWCASTLEWEST | Newcastlewest: T41∥T42 | Rathkeale |  | 52.4412 | -9.05
MV/LV Substation WO***321Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C15 ex BLAKE | Blake: T41∥T42 | Blake |  | 53.2961 | -6.8232
MV/LV Substation WO***323X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.227 | 2.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.03135 | 0.39376 | 0 |  | --> | C20 ex PALMERSTOWN | Palmerstown: T42 | Finglas |  | 53.3538 | -6.3781
MV/LV Substation WO***324X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.116 | 2.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.01615 | 0.196 | 0 |  | --> | C20 ex PALMERSTOWN | Palmerstown: T42 | Finglas |  | 53.3543 | -6.38
MV/LV Substation WO***325 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =136kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =210kW. | --> | C18 ex MOUNTRATH | Mountrath: T41∥T42 | Portlaoise |  | 52.9958 | -7.4656
MV/LV Substation WO***326 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =34kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =47.5kW. | --> | C14 ex FERMOY NORTH | Fermoy North: T41∥T42 | Barrymore |  | 52.1874 | -8.354
MV/LV Substation WO***334X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.187 | 2.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20207 | 0 |  | --> | C20 ex SUTTON | Sutton: T42 | Grange (dr) |  | 53.3775 | -6.0648
MV/LV Substation WO***334Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex KILMORE | Kilmore: T101 | Finglas |  | 53.4089 | -6.236
MV/LV Substation WO***335X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C12 ex ROSSGEIR | Rossgeir: T41∥T42 | Letterkenny |  | 54.8408 | -7.5824
MV/LV Substation WO***336 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E19 ex STRANORLAR | Stranorlar: T421 | Letterkenny |  | 54.864 | -8.0336
MV/LV Substation WO***339Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =135kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0.20814 | 0 |  | --> | C15 ex BLAKE | Blake: T41∥T42 | Blake |  | 53.2908 | -6.8167
MV/LV Substation WO***340 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex NAAS | Naas: T42 | Newbridge |  | 53.1977 | -6.7455
MV/LV Substation WO***341 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 7.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C06 ex AHANE | Ahane: T102 | Ahane |  | 52.6672 | -8.5207
MV/LV Substation WO***341X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.135 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21014 | 0 |  | --> | C11 ex KILSARAN | Kilsaran: T42 | Drybridge |  | 53.9016 | -6.4307
MV/LV Substation WO***347 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.7kW. | --> | E11 ex MACROOM | Macroom: T422 | Macroom |  | 51.9469 | -8.8241
MV/LV Substation WO***347Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.15 | 0.2 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C11 ex COOLMINE | Coolmine: T41 | Finglas |  | 53.3768 | -6.4027
MV/LV Substation WO***357 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.269 | 10.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0171 | 0.40242 | 0 |  | --> | C27 ex SALTHILL | Salthill: T101 | Salthill |  | 53.3402 | -9.179
MV/LV Substation WO***369Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C18 ex NEWBROOK | Newbrook: T42 | Mullingar |  | 53.5059 | -7.4521
MV/LV Substation WO***385Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.333 | 7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0209 | 0.38858 | 0 |  | --> | C17 ex BUSHFIELD | Bushfield: T41 | Athlone |  | 53.4341 | -7.8977
MV/LV Substation WO***387Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =134kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20529 | 0 |  | --> | C17 ex CARRIGSHANE | Carrigshane: T41 | Midleton |  | 51.8679 | -8.1631
MV/LV Substation WO***389Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.38 | 0 | 0 | 0 | 0.05415 | 0.3888 | 0 |  | --> | C15 ex BLAKE | Blake: T41∥T42 | Blake |  | 53.2844 | -6.8588
MV/LV Substation WO***391 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.12 | 4.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.2074 | 0 |  | --> | C11 ex BALLYRICKARD | Ballyrickard: T41∥T42 | Tralee |  | 52.2796 | -9.7012
MV/LV Substation WO***393 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.281 | 10.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.4066 | 0 |  | --> | C33 ex SALTHILL | Salthill: T101 | Salthill |  | 53.2612 | -9.1254
MV/LV Substation WO***395 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.366 | 5.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.4014 | 0 |  | --> | C24 ex GALWAY 110KV | Galway 110kv: T102 | Galway 110kv |  | 53.2776 | -9.0045
MV/LV Substation WO***398Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =176kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2038 | 0 |  | --> | C12 ex LUCAN EAST | Lucan East: T41∥T42 | Grange Castle |  | 53.3536 | -6.4604
MV/LV Substation WO***4002 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.117 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.01235 | 0.19985 | 0 |  | --> | C21 ex SCARTEEN | Scarteen: T41∥T42 | Mallow |  | 52.1403 | -8.6594
MV/LV Substation WO***4009 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E11 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.4738 | -6.3652
MV/LV Substation WO***4020 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C13 ex WOODFORD | Woodford: T41∥T42 | Knockearagh |  | 52.0441 | -9.4224
MV/LV Substation WO***403 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown: T41 | Tonroe |  | 53.9341 | -8.7881
MV/LV Substation WO***4039 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 11.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C36 ex SALTHILL | Salthill: T102 | Salthill |  | 53.309 | -9.1333
MV/LV Substation WO***4047 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 2.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | E12 ex KILCOCK | Kilcock: T422 | Griffinrath |  | 53.4706 | -6.5691
MV/LV Substation WO***4047 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E12 ex MILLTOWN (SR) | Milltown (sr): T422 | Oughtragh |  | 52.084 | -9.8175
MV/LV Substation WO***4052 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E11 ex CARRIGALLEN | Carrigallen: T421 | Carrick On Shannon |  | 54.0528 | -7.6872
MV/LV Substation WO***4054 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 4.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10253 | 0 |  | --> | E13 ex CLARA | Clara: T421 | Thornsberry |  | 53.4424 | -7.4843
MV/LV Substation WO***405Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 3.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.04825 | 0 |  | --> | E16 ex CRATLOE | Cratloe: T421∥T422 | Ardnacrusha |  | 52.6951 | -8.7324
MV/LV Substation WO***4064 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.352 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.3936 | 0 |  | --> | C16 ex LITTLE BRAY | Little Bray: T42 | Fassaroe |  | 53.2363 | -6.1269
MV/LV Substation WO***4070 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex SANDYFORD | Sandyford: T41 | Carrickmines |  | 53.2616 | -6.2255
MV/LV Substation WO***4072 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.188 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =201.9kW. | --> | C15 ex KILCLOHER | Kilcloher: T42 | Dungarvan |  | 52.0822 | -7.7718
MV/LV Substation WO***407X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1.2 |  | --> | 0.095 | 0 | 0 | 0 | 0.02185 | 0.07732 | 0 |  | --> | C26 ex KYLEERAGH | Kyleeragh: T42 | Nenagh |  | 52.9015 | -8.2399
MV/LV Substation WO***4086 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C12 ex CULLION | Cullion: T41∥T42 | Letterkenny |  | 54.9394 | -7.7375
MV/LV Substation WO***4096 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.025 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053845 | 0 |  | --> | E31 ex TRIM | Trim: T421 | Navan |  | 53.5505 | -6.8932
MV/LV Substation WO***4097 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.379 | 3.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40336 | 0 |  | --> | C22 ex COOLOCK | Coolock: T42 | Finglas |  | 53.3909 | -6.1754
MV/LV Substation WO***409X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =250kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0114 | 0.4113 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin: T44 | Inchicore 110kv |  | 53.325 | -6.3791
MV/LV Substation WO***4111 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.195 | 1.2 |  | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0 | 0 | Constrained,otherwise capacity available =195.8kW. | --> | C18 ex MILLTOWN MALBAY | Milltown Malbay: T42 | Tullabrack |  | 52.8475 | -9.4293
MV/LV Substation WO***411Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 0.5 |  | --> | 0.095 | 0 | 0 | 0 | 0.00285 | 0.10154 | 0 |  | --> | C14 ex KNOCKMULLEN | Knockmullen: T42 | Great Island |  | 52.3834 | -6.9419
MV/LV Substation WO***4120 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.6 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex SANDYFORD | Sandyford: T41 | Carrickmines |  | 53.2673 | -6.2069
MV/LV Substation WO***4156 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.134 | 8.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21029 | 0 |  | --> | C19 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 53.0195 | -6.1018
MV/LV Substation WO***4162 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | C16 ex RATHDRUM | Rathdrum: T42 | Arklow |  | 53.0091 | -6.3087
MV/LV Substation WO***4163 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C16 ex KILCLOHER | Kilcloher: T42 | Dungarvan |  | 52.1026 | -7.8099
MV/LV Substation WO***4163 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 10.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.0038 | 0.5 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown: T101 | Carrickmines |  | 53.2895 | -6.385
MV/LV Substation WO***4165 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.123 | 0.1 | Constrained,otherwise capacity available =312kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01235 | 0 | 0 | Constrained,otherwise capacity available =400.8kW. | --> | C16 ex RATHDRUM | Rathdrum: T42 | Arklow |  | 52.9365 | -6.2381
MV/LV Substation WO***4168 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C11 ex DEERPARK | Deerpark: T41∥T42 | Ballydine |  | 52.3297 | -7.4067
MV/LV Substation WO***416Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =328kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.40736 | 0 |  | --> | C22 ex KILMONEY | Kilmoney: T41∥T42 | Trabeg |  | 51.8089 | -8.3993
MV/LV Substation WO***4170 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray: T41 | Fassaroe |  | 53.2172 | -6.1179
MV/LV Substation WO***4171 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray: T41 | Fassaroe |  | 53.2179 | -6.1179
MV/LV Substation WO***4172 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray: T41 | Fassaroe |  | 53.2178 | -6.1156
MV/LV Substation WO***4173 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray: T41 | Fassaroe |  | 53.2181 | -6.1136
MV/LV Substation WO***4174 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C24 ex GORESBRIDGE | Goresbridge: T41∥T42 | Kilkenny |  | 52.6411 | -7.0581
MV/LV Substation WO***418 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =92kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10128 | 0 |  | --> | C15 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9425 | -8.1131
MV/LV Substation WO***4206 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =363kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.069851 | 0 | Constrained,otherwise capacity available =405.9kW. | --> | C19 ex BIRR | Birr: T41 | Dallow |  | 53.1036 | -7.9121
MV/LV Substation WO***421 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 0.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10016 | 0 |  | --> | C12 ex KILMAGIG | Kilmagig: T42 | Arklow |  | 52.8325 | -6.2349
MV/LV Substation WO***4211 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C18 ex FERMOY NORTH | Fermoy North: T41∥T42 | Barrymore |  | 52.1555 | -8.3452
MV/LV Substation WO***4211 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | E14 ex BLESSINGTON | Blessington: T422 | Kilteel |  | 53.1232 | -6.5563
MV/LV Substation WO***4245 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.3 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex WATLING STREET | Watling Street: T42 | Francis Street |  | 53.3478 | -6.2829
MV/LV Substation WO***424Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =340kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.40148 | 0 |  | --> | E14 ex COLLOONEY | Collooney: T422 | Sligo |  | 54.1672 | -8.6085
MV/LV Substation WO***4259 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.302 | 7.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.247 | 0.15538 | 0 |  | --> | C20 ex GARRYCASTLE | Garrycastle: T42 | Athlone |  | 53.4257 | -7.8942
MV/LV Substation WO***431X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.098 | 1.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.00285 | 0.21268 | 0 |  | --> | C14 ex CLONDALKIN | Clondalkin: T42 | Inchicore 110kv |  | 53.3374 | -6.404
MV/LV Substation WO***4404 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E14 ex CRANE | Crane: T122 | Crane |  | 52.5325 | -6.6319
MV/LV Substation WO***4404 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.359 | 2.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =406.5kW. | --> | C19 ex NEWCASTLEWEST | Newcastlewest: T41∥T42 | Rathkeale |  | 52.4423 | -9.0521
MV/LV Substation WO***443 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 7.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | C13 ex KILLYBEGS | Killybegs: T41 | Binbane |  | 54.6524 | -8.2674
MV/LV Substation WO***4446 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00285 | 0.5 | 0 |  | --> | C30 ex ACADEMY STREET | Academy Street: T44 | Navan |  | 53.6499 | -6.6531
MV/LV Substation WO***4457 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E13 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.9126 | -6.8586
MV/LV Substation WO***448 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =256kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.4034 | 0 |  | --> | C16 ex DOUGLAS | Douglas: T41 | Trabeg |  | 51.8893 | -8.4235
MV/LV Substation WO***449 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0095 | 0.04295 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North: T41∥T42 | Ennis |  | 52.8419 | -9.0277
MV/LV Substation WO***452 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0.01045 | 0.04119 | 0 |  | --> | C16 ex ROSSGEIR | Rossgeir: T41∥T42 | Letterkenny |  | 54.893 | -7.5436
MV/LV Substation WO***452X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =225kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00665 | 0.42006 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin: T44 | Inchicore 110kv |  | 53.3235 | -6.3829
MV/LV Substation WO***452Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C12 ex KILMAGIG | Kilmagig: T42 | Arklow |  | 52.8312 | -6.2316
MV/LV Substation WO***459Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.288 | 25.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41752 | 0 |  | --> | C22 ex ARKLOW | Arklow: T101∥T102 | Arklow |  | 52.7975 | -6.1787
MV/LV Substation WO***460 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.064 | 9.9 |  | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0.0996 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole: T41∥T42 | Fassaroe |  | 53.0952 | -6.0689
MV/LV Substation WO***461X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =297kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41614 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin: T44 | Inchicore 110kv |  | 53.3235 | -6.3799
MV/LV Substation WO***462 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C24 ex CAHIR | Cahir: T42 | Cahir |  | 52.3789 | -7.8204
MV/LV Substation WO***481Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20176 | 0 |  | --> | E12 ex TULLOW | Tullow: T422 | Carlow |  | 52.7892 | -6.729
MV/LV Substation WO***492Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.144 | 0.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20876 | 0 |  | --> | C14 ex KNOCKMULLEN | Knockmullen: T42 | Great Island |  | 52.3875 | -6.9298
MV/LV Substation WO***496Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex KYLEERAGH | Kyleeragh: T42 | Nenagh |  | 52.8623 | -8.2181
MV/LV Substation WO***498X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =73kVA. | --> | 0.095 | 0 | 0 | 0 | 0.01235 | 0.09123 | 0 |  | --> | E18 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.3372 | -7.0538
MV/LV Substation WO***499Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C17 ex CARRIGSHANE | Carrigshane: T41 | Midleton |  | 51.9037 | -8.1479
MV/LV Substation WO***504Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =290kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41222 | 0 |  | --> | E15 ex WHITECHURCH | Whitechurch: T421 | Kilbarry |  | 51.9415 | -8.5622
MV/LV Substation WO***508X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =252kVA. | --> | 0.38 | 0 | 0 | 0 | 0.03325 | 0.388 | 0 |  | --> | C18 ex LUCAN EAST | Lucan East: T41∥T42 | Grange Castle |  | 53.3577 | -6.428
MV/LV Substation WO***510Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =309kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.4003 | 0 |  | --> | C22 ex MIDLETON | Midleton: T102 | Midleton |  | 51.9024 | -8.1604
MV/LV Substation WO***513 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.11 | 0.1 | Constrained,otherwise capacity available =199kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.19516 | 0 |  | --> | C23 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.5755 | -9.0043
MV/LV Substation WO***517Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.014 | 0 | Constrained,otherwise capacity available =237kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02185 | 0.40226 | 0 |  | --> | C21 ex CASTLETROY | Castletroy: T41∥T42 | Ardnacrusha |  | 52.6645 | -8.5473
MV/LV Substation WO***520Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.339 | 26.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.00665 | 0.40264 | 0 |  | --> | E21 ex WEXFORD | Wexford: T121∥T122 | Wexford |  | 52.3896 | -6.4441
MV/LV Substation WO***522Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ROSEHILL | Rosehill: T42 | Kilkenny |  | 52.6342 | -7.2434
MV/LV Substation WO***523 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =279kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02945 | 0.3879 | 0 |  | --> | C21 ex CENTRAL PARK | Central Park: T101 | Carrickmines |  | 53.2864 | -6.1964
MV/LV Substation WO***524Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex BALLYBEG | Ballybeg: T102 | Carrickmines |  | 52.9937 | -6.087
MV/LV Substation WO***533X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C15 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9579 | -8.1689
MV/LV Substation WO***538X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.148 | 0.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.0076 | 0.20015 | 0 |  | --> | C16 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.8355 | -8.9953
MV/LV Substation WO***539Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =318kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0 | 0 | Constrained,otherwise capacity available =397.9kW. | --> | C15 ex PALLAS | Pallas: T41∥T42 | Portlaoise |  | 53.0437 | -7.3193
MV/LV Substation WO***540Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E11 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.1932 | -6.9872
MV/LV Substation WO***541 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 0.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10253 | 0 |  | --> | C23 ex GLENTIES | Glenties: T41 | Binbane |  | 54.7592 | -8.4041
MV/LV Substation WO***541X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.3kW. | --> | E16 ex KILMACTHOMAS | Kilmacthomas: T421∥T422 | Dungarvan |  | 52.1255 | -7.4801
MV/LV Substation WO***541Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050637 | 0 |  | --> | E11 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.1918 | -6.9879
MV/LV Substation WO***542 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | E12 ex CARNDONAGH | Carndonagh: T421∥T422 | Trillick |  | 55.2597 | -7.3159
MV/LV Substation WO***542X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.3kW. | --> | E16 ex KILMACTHOMAS | Kilmacthomas: T421∥T422 | Dungarvan |  | 52.126 | -7.474
MV/LV Substation WO***547Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.308 | 5.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.41146 | 0 |  | --> | E13 ex BLESSINGTON | Blessington: T421 | Kilteel |  | 53.1779 | -6.5302
MV/LV Substation WO***550 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.255 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0038 | 0.41854 | 0 |  | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham: T41∥T42 | Letterkenny |  | 54.9967 | -7.5059
MV/LV Substation WO***550Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | E14 ex EDENDERRY | Edenderry: T421∥T422 | Blake |  | 53.3397 | -6.9304
MV/LV Substation WO***552Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.329 | 13.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.3962 | 0 |  | --> | C18 ex CASTLEVIEW | Castleview: T102 | Castleview |  | 51.912 | -8.3922
MV/LV Substation WO***554Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.245 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0247 | 0.39806 | 0 |  | --> | C17 ex SALLINS | Sallins: T41 | Griffinrath |  | 53.294 | -6.6857
MV/LV Substation WO***557X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =312kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41384 | 0 |  | --> | C17 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.946 | -8.0812
MV/LV Substation WO***561Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.163 | 1.7 |  | --> | 0.19 | 0 | 0 | 0 | 0.0057 | 0.19983 | 0 |  | --> | C20 ex MONEYCOOLEY | Moneycooley: T42 | Griffinrath |  | 53.3758 | -6.6013
MV/LV Substation WO***562 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.073 | 1.8 |  | --> | 0.095 | 0 | 0 | 0 | 0.0076 | 0.09623 | 0 |  | --> | E18 ex CURRALEIGH | Curraleigh: T421∥T422 | Kilbarry |  | 51.9155 | -8.5777
MV/LV Substation WO***565Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | E12 ex BUNCLODY | Bunclody: T421∥T422 | Crane |  | 52.6595 | -6.6614
MV/LV Substation WO***565Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.366 | 8.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4054 | 0 |  | --> | E18 ex BALTRASNA | Baltrasna: T122 | Baltrasna |  | 53.5055 | -6.4688
MV/LV Substation WO***568Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.37 | 5.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =404.8kW. | --> | C14 ex BANDON | Bandon: T101 | Bandon |  | 51.7435 | -8.7336
MV/LV Substation WO***573Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | E11 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.1974 | -7.0089
MV/LV Substation WO***576Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =138kVA. | --> | 0.19 | 0 | 0 | 0 | 0.01235 | 0.19668 | 0 |  | --> | C12 ex LEIXLIP | Leixlip: T42 | Griffinrath |  | 53.3732 | -6.4997
MV/LV Substation WO***579X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.18 | 1.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20318 | 0 |  | --> | E18 ex CURRALEIGH | Curraleigh: T421∥T422 | Kilbarry |  | 51.912 | -8.5743
MV/LV Substation WO***580Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =199kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20016 | 0 |  | --> | C15 ex BLAKE | Blake: T41∥T42 | Blake |  | 53.2945 | -6.8203
MV/LV Substation WO***581X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 3.3 |  | --> | 0.095 | 0 | 0 | 0 | 0.0057 | 0.09464 | 0 |  | --> | E16 ex CRATLOE | Cratloe: T421∥T422 | Ardnacrusha |  | 52.703 | -8.7014
MV/LV Substation WO***583X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | C16 ex CURRA | Curra: T41 | Somerset |  | 53.0525 | -8.4053
MV/LV Substation WO***586Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.331 | 0.3 | Constrained,otherwise capacity available =353kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.39246 | 0 |  | --> | C21 ex CARRICKMACROSS | Carrickmacross: T41 | Meath Hill |  | 53.9708 | -6.7261
MV/LV Substation WO***589 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0.023 | 4.1 |  | --> | 0.03135 | 0 | 0 | 0 | 0.0057 | 0.028563 | 0 |  | --> | C21 ex BALLYRAINE | Ballyraine: T41∥T42 | Letterkenny |  | 54.9825 | -7.6987
MV/LV Substation WO***591 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 4.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | E11 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.223 | -6.5425
MV/LV Substation WO***595 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.197 | 4.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200.5kW. | --> | E14 ex MOVILLE | Moville: T421∥T422 | Trillick |  | 55.1905 | -7.0444
MV/LV Substation WO***609 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 6.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00285 | 0 | 0 | Constrained,otherwise capacity available =49.2kW. | --> | E18 ex RATHKEALE | Rathkeale: T421∥T422 | Rathkeale |  | 52.5286 | -8.9473
MV/LV Substation WO***615 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.067 | 1.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.03515 | 0.18319 | 0 |  | --> | C15 ex DUNDRUM | Dundrum: T41 | Blackrock |  | 53.2885 | -6.2207
MV/LV Substation WO***617X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.369 | 7.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.40194 | 0 |  | --> | E24 ex BANOGE | Banoge: T122 | Banoge |  | 52.6455 | -6.2389
MV/LV Substation WO***619Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 7.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E12 ex DUNFIRTH | Dunfirth: T122 | Dunfirth |  | 53.4137 | -6.8101
MV/LV Substation WO***624 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.265 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0209 | 0.39904 | 0 |  | --> | C12 ex BALLYBODEN | Ballyboden: T42 | Cookstown |  | 53.2778 | -6.3127
MV/LV Substation WO***626 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.9kW. | --> | C12 ex CLOONBANNIN | Cloonbannin: T42 | Glenlara |  | 52.1435 | -9.123
MV/LV Substation WO***626X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =80kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10315 | 0 |  | --> | C15 ex CARRICK ON SHANNON | Carrick On Shannon: T41∥T42 | Carrick On Shannon |  | 53.9432 | -8.1153
MV/LV Substation WO***628 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 6.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.3kW. | --> | E28 ex MILFORD (MWR) | Milford (mwr): T422 | Charleville |  | 52.3422 | -8.8656
MV/LV Substation WO***628 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E22 ex COLLOONEY | Collooney: T422 | Sligo |  | 54.183 | -8.4682
MV/LV Substation WO***636 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.055 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0.01045 | 0 | 0 | Constrained,otherwise capacity available =95.9kW. | --> | E23 ex ATHBOY | Athboy: T423 | Navan |  | 53.5338 | -6.9701
MV/LV Substation WO***637Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.358 | 4.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0.39866 | 0 |  | --> | E18 ex BAGENALSTOWN | Bagenalstown: T421∥T422 | Carlow |  | 52.7159 | -6.8485
MV/LV Substation WO***639X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.325 | 4.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.02185 | 0.38882 | 0 |  | --> | C17 ex CASTLEKNOCK | Castleknock: T41∥T42 | Finglas |  | 53.3748 | -6.3781
MV/LV Substation WO***644 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.314 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0133 | 0.39952 | 0 |  | --> | C12 ex BALLYBODEN | Ballyboden: T42 | Cookstown |  | 53.2777 | -6.3098
MV/LV Substation WO***645 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.344 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.39386 | 0 |  | --> | C12 ex BALLYBODEN | Ballyboden: T42 | Cookstown |  | 53.2763 | -6.309
MV/LV Substation WO***649X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =320kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4126 | 0 |  | --> | C18 ex LUCAN EAST | Lucan East: T41∥T42 | Grange Castle |  | 53.3587 | -6.4251
MV/LV Substation WO***654X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.295 | 0.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.40646 | 0 |  | --> | C20 ex CAHIRCALLA | Cahircalla: T41∥T42 | Ennis |  | 52.8322 | -8.9983
MV/LV Substation WO***654Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =32kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.11031 | 0 |  | --> | C14 ex GORESBRIDGE | Goresbridge: T41∥T42 | Kilkenny |  | 52.6041 | -6.9338
MV/LV Substation WO***655X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C15 ex CRANNY | Cranny: T41 | Ennis |  | 52.7159 | -9.3322
MV/LV Substation WO***661 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =24kVA. | --> | 0.0475 | 0 | 0 | 0 | 0.0038 | 0.049992 | 0 |  | --> | C19 ex MILFORD (NR) | Milford (nr): T41∥T42 | Letterkenny |  | 55.1059 | -7.5304
MV/LV Substation WO***661 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.305 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.03135 | 0.38192 | 0 |  | --> | C13 ex DODDER ROAD | Dodder Road: T42 | Milltown (dr) |  | 53.3014 | -6.275
MV/LV Substation WO***687 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.067 | 2.5 |  | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.10014 | 0 |  | --> | C16 ex CURRA | Curra: T41 | Somerset |  | 53.0533 | -8.4016
MV/LV Substation WO***687Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.271 | 5.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42012 | 0 |  | --> | C11 ex MCDONAGH | Mcdonagh: T41 | Kilkenny |  | 52.6555 | -7.2423
MV/LV Substation WO***690 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.159 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20645 | 0 |  | --> | C16 ex CURRA | Curra: T41 | Somerset |  | 53.0478 | -8.3988
MV/LV Substation WO***691X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | E14 ex EMYVALE | Emyvale: T422 | Lisdrum |  | 54.3348 | -6.9715
MV/LV Substation WO***697 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 1.6 |  | --> | 0.095 | 0 | 0 | 0 | 0.0114 | 0.090995 | 0 |  | --> | C13 ex SANDYFORD | Sandyford: T41 | Carrickmines |  | 53.2659 | -6.3131
MV/LV Substation WO***697X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =155kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0019 | 0.20507 | 0 |  | --> | E20 ex COLLOONEY | Collooney: T422 | Sligo |  | 54.2126 | -8.5145
MV/LV Substation WO***701X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.155 | 1.3 |  | --> | 0.19 | 0 | 0 | 0 | 0.01235 | 0.19407 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North: T41∥T42 | Ennis |  | 52.8414 | -9.0322
MV/LV Substation WO***703X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 1.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North: T41∥T42 | Ennis |  | 52.8407 | -9.0282
MV/LV Substation WO***711Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.483 | 1.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex TRABEG | Trabeg: T102 | Trabeg |  | 51.8799 | -8.4664
MV/LV Substation WO***713 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.039 | 1.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1093 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry: T42 | Tonroe |  | 54.1284 | -8.7371
MV/LV Substation WO***718X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.126 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2115 | 0 |  | --> | C16 ex CURRA | Curra: T41 | Somerset |  | 53.051 | -8.4009
MV/LV Substation WO***722X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C17 ex KILLESHANDRA | Killeshandra: T41∥T42 | Gortawee |  | 54.0547 | -7.6162
MV/LV Substation WO***722X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | C24 ex MACETOWN | Macetown: T102 | Macetown |  | 53.4782 | -6.3698
MV/LV Substation WO***723X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.057 | 0.1 | Constrained,otherwise capacity available =219kVA. | --> | 0.38 | 0 | 0 | 0 | 0.02565 | 0.40094 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn: T42 | Cookstown |  | 53.2755 | -6.3341
MV/LV Substation WO***732Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.306 | 2.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =404.8kW. | --> | C19 ex NEWCASTLEWEST | Newcastlewest: T41∥T42 | Rathkeale |  | 52.4418 | -9.0465
MV/LV Substation WO***735X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.185 | 1.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20239 | 0 |  | --> | E18 ex CONG | Cong: T421∥T422 | Cloon |  | 53.5441 | -9.3624
MV/LV Substation WO***736 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.027 | 4.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05355 | 0 |  | --> | E13 ex BALLYRAGGET | Ballyragget: T421∥T422 | Ballyragget |  | 52.7198 | -7.5108
MV/LV Substation WO***747 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.38 | 0.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =403.2kW. | --> | E16 ex KILMACTHOMAS | Kilmacthomas: T421∥T422 | Dungarvan |  | 52.125 | -7.4757
MV/LV Substation WO***749Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.186 | 4.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20223 | 0 |  | --> | E18 ex BAGENALSTOWN | Bagenalstown: T421∥T422 | Carlow |  | 52.7172 | -6.8496
MV/LV Substation WO***752 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 3.4 |  | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.095955 | 0 |  | --> | C20 ex GRAIGUE | Graigue: T42 | Carlow |  | 52.8327 | -6.9711
MV/LV Substation WO***753X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.246 | 8.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.2014 | 0.2119 | 0 |  | --> | C19 ex BALLYBEG | Ballybeg: T101 | Carrickmines |  | 53.0039 | -6.1079
MV/LV Substation WO***754Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052037 | 0 |  | --> | E11 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.4763 | -6.3651
MV/LV Substation WO***755X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.299 | 3.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0209 | 0 | 0 | Constrained,otherwise capacity available =393.8kW. | --> | C16 ex TURLOUGH ROAD | Turlough Road: T41∥T42 | Castlebar |  | 53.8573 | -9.3157
MV/LV Substation WO***765Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.055 | 4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10695 | 0 |  | --> | E12 ex TULLOW | Tullow: T422 | Carlow |  | 52.7971 | -6.7308
MV/LV Substation WO***767X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.057 | 0.1 | Constrained,otherwise capacity available =159kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00475 | 0.20145 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn: T42 | Cookstown |  | 53.2748 | -6.338
MV/LV Substation WO***769X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =95kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | C24 ex MACETOWN | Macetown: T102 | Macetown |  | 53.4739 | -6.3769
MV/LV Substation WO***772Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | C17 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.731 | -6.4738
MV/LV Substation WO***773X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =140kVA. | --> | 0.19 | 0 | 0 | 0 | 0.038 | 0.16938 | 0 |  | --> | C18 ex BUTTEVANT | Buttevant: T41∥T42 | Mallow |  | 52.2738 | -8.7334
MV/LV Substation WO***773Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E17 ex BALTINGLASS | Baltinglass: T421∥T422 | Stratford |  | 52.926 | -6.6594
MV/LV Substation WO***774 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.403 | 3.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.02945 | 0.5 | 0 |  | --> | C16 ex BOGHALL ROAD | Boghall Road: T42 | Fassaroe |  | 53.189 | -6.1097
MV/LV Substation WO***780 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =316kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01805 | 0.39422 | 0 |  | --> | C23 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4146 | -6.4711
MV/LV Substation WO***784 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =288kVA. | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0.40252 | 0 |  | --> | C22 ex GREYSTONES | Greystones: T42 | Fassaroe |  | 53.1363 | -6.058
MV/LV Substation WO***785X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex KELLS | Kells: T41∥T42 | Navan |  | 53.7306 | -6.8423
MV/LV Substation WO***786X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.184 | 1.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20255 | 0 |  | --> | C14 ex KELLS | Kells: T41∥T42 | Navan |  | 53.7329 | -6.8441
MV/LV Substation WO***790 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 11.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.2kW. | --> | E16 ex WESTPORT | Westport: T421∥T422 | Castlebar |  | 53.7673 | -9.5555
MV/LV Substation WO***790X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.35 | 1.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.40292 | 0 |  | --> | C32 ex ACADEMY STREET | Academy Street: T44 | Navan |  | 53.646 | -6.6831
MV/LV Substation WO***795 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =78kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =103.5kW. | --> | E22 ex ROSCREA | Roscrea: T42 | Ikerrin |  | 52.9743 | -7.8892
MV/LV Substation WO***797 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 6.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C14 ex AGHAGAD | Aghagad: T41∥T42 | Sligo |  | 54.3265 | -8.4682
MV/LV Substation WO***800X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.242 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.4085 | 0 |  | --> | C15 ex TYMON | Tymon: T41 | Cookstown |  | 53.2741 | -6.3264
MV/LV Substation WO***804 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.175 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20396 | 0 |  | --> | C18 ex BREWERY ROAD | Brewery Road: T42 | Carrickmines |  | 53.2865 | -6.2063
MV/LV Substation WO***808 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | C14 ex BALLYBODEN | Ballyboden: T42 | Cookstown |  | 53.2755 | -6.3181
MV/LV Substation WO***812Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E11 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.4747 | -6.3647
MV/LV Substation WO***819 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05016 | 0 |  | --> | C26 ex GLENTIES | Glenties: T41 | Binbane |  | 54.8035 | -8.2797
MV/LV Substation WO***820X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =147kVA. | --> | 0.19 | 0 | 0 | 0 | 0.00855 | 0 | 0 | Constrained,otherwise capacity available =199.3kW. | --> | C24 ex RAMSTOWN | Ramstown: T41∥T42 | Crane |  | 52.6764 | -6.3077
MV/LV Substation WO***821 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.0038 | 0.5 | 0 |  | --> | C11 ex WOODFORD | Woodford: T41∥T42 | Knockearagh |  | 52.057 | -9.4715
MV/LV Substation WO***824X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.257 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.41224 | 0 |  | --> | C15 ex TYMON | Tymon: T41 | Cookstown |  | 53.2739 | -6.3232
MV/LV Substation WO***825X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.209 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.01045 | 0.41844 | 0 |  | --> | C15 ex TYMON | Tymon: T41 | Cookstown |  | 53.2759 | -6.3298
MV/LV Substation WO***827X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.127 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0.01805 | 0.19235 | 0 |  | --> | C28 ex ACADEMY STREET | Academy Street: T44 | Navan |  | 53.6485 | -6.6813
MV/LV Substation WO***827Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.173 | 5.6 |  | --> | 0.19 | 0 | 0 | 0 | 0.0152 | 0 | 0 | Constrained,otherwise capacity available =188.3kW. | --> | C13 ex BANDON | Bandon: T101 | Bandon |  | 51.7326 | -8.7583
MV/LV Substation WO***834 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.19 | 1.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2016 | 0 |  | --> | E11 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.1999 | -6.9864
MV/LV Substation WO***848 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =398kVA. | --> | 0.38 | 0 | 0 | 0 | 0.038 | 0.36032 | 0 |  | --> | E18 ex BALLINDERRY | Ballinderry: T422 | Mullingar |  | 53.5021 | -7.2298
MV/LV Substation WO***853X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.14 | 1.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0.20538 | 0 |  | --> | C15 ex TYMON | Tymon: T41 | Cookstown |  | 53.2739 | -6.3217
MV/LV Substation WO***854 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.359 | 13.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.4015 | 0 |  | --> | C18 ex POTTERY ROAD | Pottery Road: T102 | Carrickmines |  | 53.2779 | -6.1153
MV/LV Substation WO***857 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C44 ex BEDFORD ROW | Bedford Row: T41 | Francis Street |  | 53.3439 | -6.2703
MV/LV Substation WO***865 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | E18 ex CREESLOUGH | Creeslough: T421 | Ardnagappary |  | 55.1228 | -7.8801
MV/LV Substation WO***865 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 7.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0.00475 | 0.047037 | 0 |  | --> | C13 ex KILLYBEGS | Killybegs: T41 | Binbane |  | 54.6538 | -8.4267
MV/LV Substation WO***865 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.227 | 0.2 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C15 ex DUNGLOE | Dungloe: T42 | Ardnagappary |  | 54.8763 | -8.3103
MV/LV Substation WO***867X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 1.3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | E12 ex KILCARRAGH | Kilcarragh: T421∥T422 | Butlerstown |  | 52.2394 | -7.0641
MV/LV Substation WO***868X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.308 | 6.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.40446 | 0 |  | --> | C17 ex CAHIR | Cahir: T41 | Cahir |  | 52.3829 | -7.9131
MV/LV Substation WO***876X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.28 | 1.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.02185 | 0.39576 | 0 |  | --> | C15 ex TYMON | Tymon: T41 | Cookstown |  | 53.2756 | -6.3254
MV/LV Substation WO***898Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | C12 ex TIMOLEAGUE | Timoleague: T41 | Bandon |  | 51.722 | -8.7902
MV/LV Substation WO***901 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E16 ex MOHILL | Mohill: T421∥T422 | Carrick On Shannon |  | 53.8813 | -7.8994
MV/LV Substation WO***908X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 7.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0.0133 | 0.0388 | 0 |  | --> | C06 ex AHANE | Ahane: T102 | Ahane |  | 52.6703 | -8.5184
MV/LV Substation WO***909X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.172 | 1.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.01425 | 0.18943 | 0 |  | --> | E18 ex CURRALEIGH | Curraleigh: T421∥T422 | Kilbarry |  | 51.9142 | -8.5754
MV/LV Substation WO***910 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | E17 ex BELMULLET | Belmullet: T421 | Bellacorick |  | 54.229 | -10.0083
MV/LV Substation WO***914X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =160kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.2063 | 0 |  | --> | C11 ex GARDEN CITY | Garden City: T41∥T42 | Arklow |  | 52.6838 | -6.293
MV/LV Substation WO***930 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 2.3 |  | --> | 0.095 | 0 | 0 | 0 | 0.0095 | 0.09048 | 0 |  | --> | E16 ex CLONROCHE | Clonroche: T421∥T422 | Wexford |  | 52.548 | -6.736
MV/LV Substation WO***932Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.381 | 7.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.39704 | 0 |  | --> | C19 ex ATHY | Athy: T101 | Athy |  | 52.9929 | -6.999
MV/LV Substation WO***933X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.065 | 1.8 |  | --> | 0.19 | 0 | 0 | 0 | 0.0304 | 0.18848 | 0 |  | --> | C15 ex TYMON | Tymon: T41 | Cookstown |  | 53.2737 | -6.3297
MV/LV Substation WO***936 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 4.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | E21 ex CLARA | Clara: T421 | Thornsberry |  | 53.3666 | -7.6274
MV/LV Substation WO***937Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.6 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex BALLYJAMESDUFF | Ballyjamesduff: T42 | Shankill |  | 53.8634 | -7.1953
MV/LV Substation WO***944Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.11 | 0.1 | Constrained,otherwise capacity available =360kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.39736 | 0 |  | --> | C15 ex TUAM NORTH | Tuam North: T41∥T42 | Cloon |  | 53.5115 | -8.8729
MV/LV Substation WO***956 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 3.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05295 | 0 |  | --> | C20 ex OAKFIELD | Oakfield: T42 | Sligo |  | 54.2716 | -8.5173
MV/LV Substation WO***957 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.057 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0.01805 | 0 | 0 | Constrained,otherwise capacity available =202.6kW. | --> | E23 ex ATHBOY | Athboy: T423 | Navan |  | 53.5333 | -6.9606
MV/LV Substation WO***963X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =361kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.4032 | 0 |  | --> | C16 ex TOGHER | Togher: T42 | Trabeg |  | 51.8755 | -8.5179
MV/LV Substation WO***970Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =316kVA. | --> | 0.38 | 0 | 0 | 0 | 0.00285 | 0.41022 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown: T421∥T422 | Drybridge |  | 53.6964 | -6.2602
MV/LV Substation WO***971 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.361 | 3.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4062 | 0 |  | --> | C20 ex BOGHALL ROAD | Boghall Road: T42 | Fassaroe |  | 53.1865 | -6.1004
MV/LV Substation WO***978Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.374 | 4 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.38814 | 0 |  | --> | E12 ex TULLOW | Tullow: T422 | Carlow |  | 52.7953 | -6.7294
MV/LV Substation WO***981 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E17 ex MANORHAMILTON | Manorhamilton: T422 | Sligo |  | 54.2754 | -8.2002
MV/LV Substation WO***982 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051107 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton: T422 | Sligo |  | 54.2832 | -7.9771
MV/LV Substation WO***989Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.302 | 4.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41538 | 0 |  | --> | E11 ex KNOCKMULLEN | Knockmullen: T421 | Great Island |  | 52.3978 | -6.9264
MV/LV Substation WO***992 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 3.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1019 | 0 |  | --> | E16 ex BALLYCROSSAUN | Ballycrossaun: T421∥T422 | Somerset |  | 53.1055 | -8.2368
MV/LV Substation WO***992Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.163 | 4 |  | --> | 0.19 | 0 | 0 | 0 | 0.01235 | 0.19283 | 0 |  | --> | E12 ex TULLOW | Tullow: T422 | Carlow |  | 52.7927 | -6.7264
MV/LV Substation WO***993X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | E16 ex WINDSOR | Windsor: T421∥T422 | Castlebar |  | 53.8495 | -9.2766
MV/LV Substation WO***997X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.022 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0.01615 | 0.037287 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North: T41∥T42 | Ennis |  | 52.8436 | -9.0256
MV/LV Substation WO***999X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =163kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20583 | 0 |  | --> | C22 ex COBH | Cobh: T41∥T42 | Cow Cross |  | 51.8513 | -8.3147
MV/LV Substation WP***4009 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 3.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | C12 ex TELAYDON | Telaydon: T42 | Lisdrum |  | 54.2528 | -6.9567
MV/LV Substation WP***4281 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 9.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg: T41∥T42 | Carrowbeg |  | 53.8091 | -9.5454
MV/LV Substation WR***018 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.298 | 2.5 |  | --> | 0.38 | 0 | 0 | 0 | 0.01995 | 0.395 | 0 |  | --> | E15 ex TULLOW | Tullow: T421 | Carlow |  | 52.7981 | -6.7446
MV/LV Substation WR***052 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.265 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.42104 | 0 |  | --> | C23 ex RAMPARTS | Ramparts: T41 | Dundalk |  | 54.0071 | -6.4011
MV/LV Substation WR***064 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.284 | 4.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0285 | 0.38814 | 0 |  | --> | C13 ex OAKFIELD | Oakfield: T41 | Sligo |  | 54.2672 | -8.5014
MV/LV Substation WR***086Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.493 | 2.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex SUTTON | Sutton: T41 | Grange (dr) |  | 53.3896 | -6.0746
MV/LV Substation WR***188Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =121kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0152 | 0.19625 | 0 |  | --> | C22 ex KILMONEY | Kilmoney: T41∥T42 | Trabeg |  | 51.8056 | -8.4069
MV/LV Substation WR***578 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.194 | 1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20096 | 0 |  | --> | C17 ex TRIM | Trim: T41∥T42 | Navan |  | 53.5422 | -6.7141
MV/LV Substation WR***896X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 10.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C18 ex WATERFORD IND EST | Waterford Ind Est: T42∥T44 | Butlerstown |  | 52.2458 | -7.1436
MV/LV Substation WR***968 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.333 | 2.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.41058 | 0 |  | --> | C13 ex GRANBY ROW | Granby Row: T41 | Mcdermott |  | 53.3548 | -6.2644
MV/LV Substation WU***4293 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =376kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0171 | 0.38582 | 0 |  | --> | C15 ex LITTLE MILLS | Little Mills: T41 | Dundalk |  | 53.9696 | -6.4145
MV/LV Substation WU***4294 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =393kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40112 | 0 |  | --> | C15 ex LITTLE MILLS | Little Mills: T41 | Dundalk |  | 53.9659 | -6.4144
MV/LV Substation WV***4066 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 0.8 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10284 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane: T421∥T422 | Oughtragh |  | 51.8282 | -10.1661
MV/LV Substation WW***4085 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.188 | 2.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20191 | 0 |  | --> | C16 ex ROSSGEIR | Rossgeir: T41∥T42 | Letterkenny |  | 54.9317 | -7.4589
MV/LV Substation WW***4166 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C32 ex SALTHILL | Salthill: T102 | Salthill |  | 53.2896 | -9.0752
MV/LV Substation WW***4174 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 5.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400kW. | --> | C14 ex BANDON | Bandon: T101 | Bandon |  | 51.7518 | -8.7184
MV/LV Substation WW***929X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =188kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =201.9kW. | --> | C17 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.0835 | -7.7025
MV/LV Substation WY***048 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.23 | 1.4 |  | --> | 0.38 | 0 | 0 | 0 | 0.05225 | 0.3713 | 0 |  | --> | C25 ex DUNDRUM | Dundrum: T41 | Blackrock |  | 53.2839 | -6.251
MV/LV Substation WY***060 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.487 | 2.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00475 | 0.5 | 0 |  | --> | C15 ex CARRIGLAWN | Carriglawn: T41∥T42 | Wexford |  | 52.3393 | -6.4737
MV/LV Substation WY***072Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 1.9 |  | --> | 0.095 | 0 | 0 | 0 | 0.0038 | 0.098685 | 0 |  | --> | C12 ex BISHOPSTOWN | Bishopstown: T42 | Kilbarry |  | 51.8885 | -8.5311
MV/LV Substation WY***093 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =26kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.053697 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.5431 | -6.3491
MV/LV Substation WY***120Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =19kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.054725 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.5284 | -6.3127
MV/LV Substation WY***131X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.392 | 3.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40128 | 0 |  | --> | C14 ex SANDYFORD | Sandyford: T42 | Carrickmines |  | 53.2803 | -6.2448
MV/LV Substation WY***159 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.273 | 3.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.02565 | 0.39282 | 0 |  | --> | C19 ex DEANSGRANGE | Deansgrange: T41 | Carrickmines |  | 53.2894 | -6.1637
MV/LV Substation WY***161X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.383 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0057 | 0.39672 | 0 |  | --> | C15 ex CARRIGLAWN | Carriglawn: T41∥T42 | Wexford |  | 52.3398 | -6.472
MV/LV Substation WY***173X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C30 ex TANEY | Taney: T102 | Carrickmines |  | 53.2814 | -6.2421
MV/LV Substation WY***217 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =165kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20552 | 0 |  | --> | C21 ex CLONMINCH | Clonminch: T41 | Thornsberry |  | 53.2205 | -7.4746
MV/LV Substation WY***320X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex TANEY | Taney: T102 | Carrickmines |  | 53.2857 | -6.2392
MV/LV Substation WY***323 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.241 | 4.2 |  | --> | 0.38 | 0 | 0 | 0 | 0.0342 | 0.38866 | 0 |  | --> | C12 ex LOUGHLINSTOWN | Loughlinstown: T42 | Carrickmines |  | 53.2505 | -6.1361
MV/LV Substation WY***335X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.317 | 1.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0076 | 0 | 0 | Constrained,otherwise capacity available =405.1kW. | --> | C18 ex BALLYBAY | Ballybay: T41∥T42 | Lisdrum |  | 54.1318 | -6.8959
MV/LV Substation WY***363X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex TANEY | Taney: T102 | Carrickmines |  | 53.2857 | -6.2391
MV/LV Substation WY***4169 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex GARVILLE AVENUE | Garville Avenue: T42 | Milltown (dr) |  | 53.322 | -6.267
MV/LV Substation WY***4193 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C15 ex CARRIGLAWN | Carriglawn: T41∥T42 | Wexford |  | 52.3397 | -6.4706
MV/LV Substation WY***499 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051265 | 0 |  | --> | C12 ex BALLYTIVNAN | Ballytivnan: T42 | Sligo |  | 54.3062 | -8.4611
MV/LV Substation WY***524X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =75kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =103.9kW. | --> | C13 ex TIMOLEAGUE | Timoleague: T41 | Bandon |  | 51.6763 | -8.6833
MV/LV Substation WY***531 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =420kVA. | --> | 0.5985 | 0 | 0 | 0 | 0.01615 | 0.5 | 0 |  | --> | C17 ex GARVILLE AVENUE | Garville Avenue: T42 | Milltown (dr) |  | 53.3222 | -6.2671
MV/LV Substation WY***548 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05142 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.5396 | -6.3433
MV/LV Substation WY***571 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.3 | 4.8 |  | --> | 0.38 | 0 | 0 | 0 | 0.0152 | 0.39968 | 0 |  | --> | C15 ex BALLINCLEA | Ballinclea: T41 | Cherrywood |  | 53.2685 | -6.1153
MV/LV Substation WY***819Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.44613 | 0 | Constrained,otherwise capacity available =500kW. | --> | E21 ex ASHBOURNE | Ashbourne: T421 | Finglas |  | 53.5395 | -6.3553
MV/LV Substation WY***830Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.052037 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan: T44 | Newbridge |  | 53.1906 | -6.7747
MV/LV Substation WY***844X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.327 | 5.6 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.40252 | 0 |  | --> | C12 ex BALLINCOLLIG | Ballincollig: T42 | Kilbarry |  | 51.8861 | -8.62
MV/LV Substation WY***908Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.182 | 3.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20286 | 0 |  | --> | C20 ex ATHY | Athy: T102 | Athy |  | 52.9988 | -6.9885
MV/LV Substation WY***969X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.183 | 6.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =202.7kW. | --> | E11 ex RATHKEALE | Rathkeale: T421∥T422 | Rathkeale |  | 52.5947 | -8.9765
MV/LV Substation YA***056X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.321 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.40244 | 0 |  | --> | C19 ex BELFIELD | Belfield: T41 | Blackrock |  | 53.3008 | -6.2285
MV/LV Substation YA***311X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 2.2 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C11 ex SUTTON | Sutton: T41 | Grange (dr) |  | 53.3885 | -6.0677
MV/LV Substation YA***816 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 25.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051575 | 0 |  | --> | C22 ex ARKLOW | Arklow: T101∥T102 | Arklow |  | 52.7998 | -6.1712
MV/LV Substation YE***019 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 1.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10575 | 0 |  | --> | C15 ex BALLYTIVNAN | Ballytivnan: T41 | Sligo |  | 54.2814 | -8.4499
MV/LV Substation YE***021Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | E23 ex BALTRASNA | Baltrasna: T121 | Baltrasna |  | 53.5693 | -6.4556
MV/LV Substation YE***065 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.337 | 0.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0.00285 | 0.5 | 0 |  | --> | C11 ex DRYBRIDGE | Drybridge: T41 | Drybridge |  | 53.7218 | -6.3445
MV/LV Substation YE***068 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.257 | 0.3 |  | --> | 0.38 | 0 | 0 | 0 | 0.00855 | 0.41324 | 0 |  | --> | C21 ex NENAGH | Nenagh: T41 | Nenagh |  | 52.8618 | -8.205
MV/LV Substation YE***068Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =264kVA. | --> | 0.38 | 0 | 0 | 0 | 0.03705 | 0.38218 | 0 |  | --> | C23 ex MACETOWN | Macetown: T101 | Macetown |  | 53.4207 | -6.4765
MV/LV Substation YE***097 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =52kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0304 | 0.19034 | 0 |  | --> | C21 ex MALAHIDE | Malahide: T41 | Glasmore |  | 53.4491 | -6.1638
MV/LV Substation YE***108 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.178 | 1.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20349 | 0 |  | --> | C21 ex WATERFORD IND EST | Waterford Ind Est: T41 | Butlerstown |  | 52.2447 | -7.1299
MV/LV Substation YE***148X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.346 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40854 | 0 |  | --> | C15 ex BALLYTIVNAN | Ballytivnan: T41 | Sligo |  | 54.2801 | -8.4524
MV/LV Substation YE***149X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.345 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.4087 | 0 |  | --> | C15 ex BALLYTIVNAN | Ballytivnan: T41 | Sligo |  | 54.2788 | -8.4531
MV/LV Substation YE***189X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =280kVA. | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0.40876 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin: T44 | Inchicore 110kv |  | 53.3264 | -6.3813
MV/LV Substation YE***206 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | E14 ex BIRDHILL | Birdhill: T422 | Ardnacrusha |  | 52.809 | -8.3273
MV/LV Substation YE***233X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.9 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex BALLYTIVNAN | Ballytivnan: T41 | Sligo |  | 54.281 | -8.4527
MV/LV Substation YE***251X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 1.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | E19 ex SHILLELAGH | Shillelagh: T421∥T422 | Carlow |  | 52.7292 | -6.5584
MV/LV Substation YE***253 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.298 | 2.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.04655 | 0.367 | 0 |  | --> | C17 ex MOUNTGORRY | Mountgorry: T41 | Grange (dr) |  | 53.4511 | -6.1698
MV/LV Substation YE***258Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.138 | 2.4 |  | --> | 0.19 | 0 | 0 | 0 | 0.00665 | 0.20268 | 0 |  | --> | C17 ex VIRGINIA | Virginia: T41∥T42 | Meath Hill |  | 53.8331 | -7.0694
MV/LV Substation YE***278 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 6.4 |  | --> | 0.095 | 0 | 0 | 0 | 0.00475 | 0.09706 | 0 |  | --> | C14 ex AGHAGAD | Aghagad: T41∥T42 | Sligo |  | 54.3292 | -8.5024
MV/LV Substation YE***4278 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =381kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40304 | 0 |  | --> | C28 ex CLONDALKIN | Clondalkin: T44 | Inchicore 110kv |  | 53.3303 | -6.3859
MV/LV Substation YE***459 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 12.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050795 | 0 |  | --> | C23 ex MONREAD | Monread: T101 | Monread |  | 53.2254 | -6.7359
MV/LV Substation YE***580X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | E21 ex CURRALEIGH | Curraleigh: T421∥T422 | Kilbarry |  | 51.9412 | -8.6693
MV/LV Substation YE***678X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =154kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20723 | 0 |  | --> | C14 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.2254 | -7.0039
MV/LV Substation YE***881X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 12.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050477 | 0 |  | --> | C23 ex MONREAD | Monread: T101 | Monread |  | 53.2352 | -6.733
MV/LV Substation YE***911 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.267 | 1.9 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41572 | 0 |  | --> | C17 ex BALLYTIVNAN | Ballytivnan: T41 | Sligo |  | 54.3064 | -8.5643
MV/LV Substation YE***930Z | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =165kVA. | --> | 0.19 | 0 | 0 | 0 | 0.019 | 0.18552 | 0 |  | --> | C14 ex KILDARE | Kildare: T41∥T42 | Newbridge |  | 53.2253 | -6.9993
MV/LV Substation YE***931Y | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.127 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.21135 | 0 |  | --> | C32 ex ACADEMY STREET | Academy Street: T44 | Navan |  | 53.6456 | -6.699
MV/LV Substation YE***999 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.051885 | 0 |  | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road: T41∥T42 | Drybridge |  | 53.7353 | -6.3473
MV/LV Substation YO***007Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C15 ex CLOONLOUGH | Cloonlough: T41∥T42 | Barrymore |  | 52.2461 | -8.3645
MV/LV Substation YO***052X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.391 | 3.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =401.4kW. | --> | E17 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 51.953 | -7.8698
MV/LV Substation YO***073Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05032 | 0 |  | --> | E19 ex LONGFORD | Longford: T421 | Richmond |  | 53.6935 | -7.8199
MV/LV Substation YO***109X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.383 | 3.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.01425 | 0 | 0 | Constrained,otherwise capacity available =387.7kW. | --> | E17 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 51.9511 | -7.8734
MV/LV Substation YO***124X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 0.7 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex CAMDEN ROW | Camden Row: T41 | Francis Street |  | 53.3393 | -6.2641
MV/LV Substation YO***224X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.341 | 3.7 |  | --> | 0.38 | 0 | 0 | 0 | 0.0095 | 0 | 0 | Constrained,otherwise capacity available =399.3kW. | --> | E17 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 51.936 | -7.859
MV/LV Substation YO***286X | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.183 | 3.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =202.7kW. | --> | E17 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 51.97 | -7.8622
MV/LV Substation YO***353 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 3.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52kW. | --> | E14 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 51.9711 | -7.8592
MV/LV Substation YO***354 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.05095 | 0 |  | --> | C21 ex NENAGH | Nenagh: T41 | Nenagh |  | 52.8934 | -8.2961
MV/LV Substation YO***4063 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =91kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101.4kW. | --> | C20 ex ROSCREA | Roscrea: T42 | Ikerrin |  | 52.9494 | -7.8088
MV/LV Substation YO***4262 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | E13 ex BAGENALSTOWN | Bagenalstown: T421∥T422 | Carlow |  | 52.693 | -6.936
MV/LV Substation YO***430 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =101kVA. | --> | 0.19 | 0 | 0 | 0 | 0.0038 | 0 | 0 | Constrained,otherwise capacity available =211.2kW. | --> | C20 ex COLLIGAN | Colligan: T41 | Dungarvan |  | 52.0847 | -7.6304
MV/LV Substation YO***545Z | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 8 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CENTRE PARK ROAD | Marina: T105 | Marina |  | 51.9018 | -8.4667
MV/LV Substation YO***571 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 3.7 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =53.1kW. | --> | E13 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 51.9507 | -7.7281
MV/LV Substation YO***648 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.039 | 3.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =109.3kW. | --> | E19 ex FOXHOLE | Foxhole: T421∥T422 | Dungarvan |  | 52.0063 | -7.9069
MV/LV Substation YO***670 | 20 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 4.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10284 | 0 |  | --> | E13 ex KILLINICK | Killinick: T421∥T422 | Wexford |  | 52.2046 | -6.4077
MV/LV Substation YO***887 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.288 | 8.1 |  | --> | 0.38 | 0 | 0 | 0 | 0.00475 | 0.41252 | 0 |  | --> | C22 ex RINGSEND | Ringsend: T102 | Poolbeg |  | 53.3446 | -6.2269
MV/LV Substation YO***911 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | 0.050002 | 0 |  | --> | C18 ex KINGSCOURT | Kingscourt: T42 | Meath Hill |  | 53.9083 | -6.8037
MV/LV Substation ZA***060 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40002 | 0 |  | --> | C25 ex SRAH | Srah: T43 | Thornsberry |  | 53.2835 | -7.5069
MV/LV Substation ZA***876 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =388kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | 0.40192 | 0 |  | --> | C22 ex GREYSTONES | Greystones: T42 | Fassaroe |  | 53.128 | -6.0622
MV/LV Substation ZE***462 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 3.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.1008 | 0 |  | --> | C19 ex RECESS | Recess: T41 | Galway 110kv |  | 53.416 | -9.7948
MV/LV Substation ZE***539X | 10 kV | 400V(3ph) & 230V(single ph) | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 8.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex GORTLEE | Gortlee: T41∥T42 | Letterkenny |  | 54.9604 | -7.7137
MV/LV Substation ZE***662Y | 20 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 0.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20001 | 0 |  | --> | C20 ex KNOCKMULLEN | Knockmullen: T42 | Great Island |  | 52.365 | -6.9665
MV/LV Substation ZI***330 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.193 | 2.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | 0.20112 | 0 |  | --> | C11 ex DODDER ROAD | Dodder Road: T42 | Milltown (dr) |  | 53.3054 | -6.2727
MV/LV Substation ZI***4230 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.8 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex LIBERTY STREET | Liberty Street: T102 | Liberty Street |  | 51.8958 | -8.4868
MV/LV Substation ZO***130 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.2 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex CABRA | Cabra: T101 | Finglas |  | 53.3536 | -6.3024
MV/LV Substation ZU***019 | 10 kV | 400V(3ph) & 230V(single ph) | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 7.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | 0.10268 | 0 |  | --> | E24 ex BANOGE | Banoge: T122 | Banoge |  | 52.6726 | -6.2176

## Disclaimer
Disclaimer
This capacity heatmap provides an indication of the available transformer capacity at substations. The map indicates transformer capacity only. It does not guarantee the same capacity is available in the upstream networks. The heatmap is a snapshot, representing a moment in time, of a continually changing network system. It cannot be relied upon in isolation to assess the viability of a connection to a premises. Whilst we use reasonable endeavours to ensure that the capacity map and related information is accurate, we do not warrant, and do not accept any responsibility or liability for, the accuracy or completeness of the content or for any consequence or loss which may arise from reliance on the capacity heatmap or related information. The data provided must be considered in conjunction with explanations in ‘Important details about the Heatmap’ section. The available capacity figures will be periodically updated, and you should check the webpage routinely for the latest version. The legal disclaimer terms and conditions for use of our website apply to the capacity heatmap and related information.
The legal disclaimer terms and conditions for use of our website apply to the capacity heatmap and related information.

## Notes & FAQs
What is the Available Capacity Heatmap?
At ESB Networks we are committed to improving the experience of our customers. As part of this commitment, we have developed our interactive Capacity Heatmap. It contains capacity information on all our 3-phase LV, MV and HV DSO substations. It provides an interface that enables the easy identification of potential transformer capacity in the vicinity of your site. An excel file is available to download from the download section on this page.
We envisage that the map will be used to inform initial discussion between ourselves and our customers. Although we have taken steps to ensure the accuracy of the map, it cannot replicate the level of accuracy provided by the detailed assessment carried out as part of the formal application process. Please read the accompanying notes and important details section to understand what the map does and does not provide.
If the Available Capacity Heatmap indicates that there is insufficient capacity to accommodate your development, please contact us to discuss the next steps. We will always work with customers to find solutions.
Generation customer queries should be directed to DSOgenerators@esb.ie.
Demand customer queries should be directed to innovationfeedback@esbnetworks.ie.
Map Preparation Date: 30 June 2024
What can I learn from the map?
The Capacity Heatmap provides an indication of available transformer capacity, at substation level and at all voltage levels, for new demand and generation customers. It is a user-friendly and interactive map that shows how much demand or generation could be added into a substation without reinforcement. It empowers potential customers and helps them have a better understanding as to where connection is possible.
In the map HV substations are classified into three categories corresponding to the connection voltage i.e., 110kV, 38kV or Medium Voltage (MV).
The map also gives the location and available demand capacity for all 3 phase Medium Voltage to Low Voltage (MV/LV) substations.The LV data capacity is in the range of customers looking to connect demand less than 500kVA. This scale would be of most interest to small businesses, farming, and small community projects. If the indicated capacity meets your needs, then you can be reasonably assured no new substation development is required. However, site specific detail such as proximity and physical access could still be an overarching limiting factor.
Available capacity for LV generation is not specified because of additional considerations that are mainly site specific, see point No 5 below.
The pins on the map are colour coded by ranges of available capacity which can be separately filtered. Filtering can also be independently applied by voltage level.
How do I know which substation to review for my site?
We recommend using the Location Finder tool by clicking on the icon to the right of the map. Look for this symbol
Here you can type your place name, or Eircode and it will show the stations closest to the location. Please ensure you have selected the relevant connection voltages and available ranges in the filters section on the left or it may not return results.
For LV substations, use the map to locate your own site and then find the nearest LV substation to it. Typically, a substation must be within 300m or less to be suitable for connecting at LV otherwise a new substation must be provided nearer to you. The pop-up box also shows the parent HV substation that supplies the LV substation. Also check this for available capacity.
For MV connection (greater than or equal to 500kVA) locate the nearest LV station as in the previous paragraph and the parent capacity will also be shown.
Does the Capacity Available value mean I can connect the amount shown?
Not necessarily. There are many site-specific issues and detailed technical checks that must be completed to give that assurance and they can only be completed as part of an application. Below are some of the factors that influence the answer:
Am I the first to apply? All connection offers are provided on a first come first served basis so other customers may have applied ahead and used a proportion of the available capacity.
Proximity to the substation: typically for LV, you must be a maximum of 300m from the substation and much closer for the higher level of LV capacity. For 38kV and MV circuits, capacity is not assured, and new lines may need to be constructed or existing one upgraded.
HV substations are sometimes a parent supply to other downstream substations. In cases where the parent substation has limited capacity then all child substations will be curtailed by that limit. Furthermore, if just one child substation absorbs all the available capacity then that will result in no spare capacity for the other child stations. This form of interaction requires continual re-assessment to ensure no system overload occur.
A similar interaction can occur on circuits where apparently available capacity cannot be contracted because of customer increases on other circuits which share a common source with a capacity limit.
Generation, at all voltages, is particularly onerous due to the limited latitude to accommodate the associated voltage rise. This has an acute effect on the necessary proximity to a substation.
For ECP generation connections, the capacity available may differ depending on customers accepting or withdrawing their connection study offers during each batch of studies.
Capacity available is also influenced by disturbing load such as flicker and harmonic emissions.
The stated available capacity may exceed the maximum rating for an individual network component for example standard circuit connection capacity. In such cases, aconnection will be constrained by the network component and therefore will not be able to avail of the full value indicated.
How has the data been produced?
The data has been produced by an analysis of the available transformer capacity, existing loads, and contractual commitments to new customers. Detailed assessment aspects, necessary for connection offers, such as upstream circuit capacity and service contingency requirement are not included.
What are the available capacity figures based on?
Station capacity, as of Winter 2023.
Base load information comes from Special Load Readings, 2023/2024 which include 2023 Summer Valley load used in the Generation capacity preparation.
Demand calculation incorporates demand contracts and offers up to 21st June2024
Generation calculations incorporates generation contracts and offers up to 21st June 2024.
How often is the Network Capacity Map updated?
As part of ESB Networks strategy, the objective is to update the map quarterly.
Are the substation locations accurate?
HV substation locations are only indicative. The exact locations of MV/LV substations are provided.
How long does a connection take?
In general, where HV substation capacity is adequate, MV connections up to a maximum of 10MVA will entail construction of overhead line or new underground cable network, associated civil works and minor station works only and typically do not require planning permission. These would not be expected to take longer than 6-9 months. However, any instances requiring significant station work such as the installation of a new transformer or MV switchgear will require increased time, and possibly planning permission or necessary permits and would typically be expected to take approximately 2-3 years.
LV connections alone are usually completed within 6 months of application.
Generation connection information: Enduring Connection Policy (ECP) (esbnetworks.ie)
What other important points should be kept in mind about the data in the map?
The map does not replace a full formal application in determining network capacity.
The map does not provide capacity figures for the final connection from HV substation to customer premises. Such connections will need to tap into the existing MV (10kV or 20kV) network. Capacity availability is subject to many variables and an assessment is necessary.
In some cases, the available capacity shown in the Demand Map may already be contracted to individual customers but is not currently being fully utilised.
The information provided in the Generation and Demand Maps does not guarantee the same capacity is available in the upstream DSO networks.
Any increased load on the Distribution System will impact on the upstream Transmission System and reinforcements may be required on the Transmission System in order to cater for these loads. This will be separately assessed by the TSO.
An individual connection cannot be greater than the capacity of an individual transformer. In the case of 38kV and MV, the available capacity shown is the total of all transformers in the substation at the respective voltage. Therefore, full capacity utilisation may, sometimes, only be possible with more than one connection. (Note, a single premises cannot have more than one connection).